## Sheet1
Job Display ID | CAD_ID | Job Region | Job Area (DISTRICT) | Job Substation | Job Feeder | Feeder ID | Job OFF Time | Job ON Time | Job Duration Mins | Custs Affected | Call Qty | CMI | Cause ID | Cause Desc | Equip ID | Equip Desc | Job City | Device Address | CMI Category | Exclude CMI? | Job QA? | Event Exclusion? | Total System Premises | Total Region Premises | Total Area Premises | Total Subst Premises | Total Feeder Premises | Job SAIDI | Job SAIFI | Job CAIDI | Job ASAI | Call Code | Extent | STRCTUR_NO/Job Device ID | Device Type | Dev Subtype | Lead Crew | Lead Crew Phone | Region SAIDI | Area SAIDI | Subst SAIDI | Feeder SAIDI | AM Notes | OGE Causes | Major Storm Event Y (Yes) or N (No) | Distribution, Substation, Transmission | Transmission Voltage (69kV, 138kV, 161kv) feeding distribution substation | Month/Day/Year | Year | Equipment Desc that should be excluded from reported indices | Ark Grid Mod or OK Grid Enhancement Circuits
J2001.000006 | PD-01012020-00063 | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1722 | 861722 | 2020-01-01 00:22 | 2020-01-01 09:22 | 540.5 | 2 | 3 | 819.7333 | 3 | DAMAGED BY PUBLIC | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 4522 SUNNYVIEW DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859659 | 114164 | 71085 | 6883 | 1786 | 0.00095356 | 2.3265e-06 | 409.8667 | 1 | 310 | Secondary | 52740 | Load | Tran1phPad | DERICK WINSETT | 405-650-6102 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | #N/A
J2001.000021 | PD-01012020-00363 | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_631 | 460631 | 2020-01-01 03:00 | 2020-01-01 04:23 | 82.5 | 138 | 59 | 10803.1 | 4 | DETERIORATION | 17 | JUMPER | WOODWARD | SE CR-SUNDOWN ADDITION | CMI_NORMAL | NO | NO | NO | 859659 | 53470 | 10409 | 5676 | 1170 | 0.012567 | 0.00016053 | 78.2833 | 1 | 310 | Mainline | 3298 | Fuse | FuseOH | HAYDEN BIERIG | 580-748-0538 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | #N/A
J2001.000041 |  | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-01-01 08:40 | 2020-01-01 09:56 | 76.58 | 1 | 0 | 71.6 | 4 | DETERIORATION | 2 | TRANSFORMER OH | 0 | .5N RIVER 81 HWY WS | CMI_PLANNED | YES | NO | NO | 859723 | 128525 | 12721 | 6931 | 1822 | 8.3283e-05 | 1.1632e-06 | 71.6 | 1 | 0 | Load | 47926 | Load | Tran3phWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | #N/A
J2001.000045 | PD-01012020-00859 | SOUTHERN | SULPHUR | 5712:JOLLYVILLE | JOLLYVILLE_1264 | 571264 | 2020-01-01 08:48 | 2020-01-01 13:39 | 290.7 | 1 | 1 | 283.8667 | 13 | PREMATURE FAILURE | 2 | TRANSFORMER OH | HENNEPIN | W OF DAVIS | CMI_NORMAL | NO | NO | NO | 859723 | 77490 | 6805 | 371 | 261 | 0.00033018 | 1.1632e-06 | 283.8667 | 1 | 310 | Load | 6629 | Load | Tran1phOH | MICHAEL D DICKINSON | 580-229-5532 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | #N/A
J2001.000046 | PD-01012020-00858 | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_622 | 460622 | 2020-01-01 08:50 | 2020-01-01 11:00 | 129.58 | 1 | 1 | 120.9167 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | WOODWARD | 900 LAKEVIEW RD | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859723 | 53470 | 10409 | 5676 | 764 | 0.00014065 | 1.1632e-06 | 120.9167 | 1 | 310 | Load | 193223 | Load | Tran1phOH | C-TSENID1 TOM SEEDORF | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | #N/A
J2001.000047 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-01 09:01 | 2020-01-01 10:08 | 66.95 | 5 | 3 | 276 | 4 | DETERIORATION | 2 | TRANSFORMER OH | HARTMAN | 261 Burlison St | CMI_PLANNED | YES | NO | NO | 859723 | 82074 | 7527 | 1501 | 1198 | 0.00032103 | 5.8158e-06 | 55.2 | 1 | 308 | Load | 8135 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-01 | 2020 |  | Ark - Series 2
J2001.000048 | PD-01012020-00860 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4864 | 824864 | 2020-01-01 09:06 | 2020-01-01 10:23 | 76.83 | 1 | 1 | 72.2833 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 2435 SW.20 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859723 | 167925 | 148141 | 4181 | 2020 | 8.4077e-05 | 1.1632e-06 | 72.2833 | 1 | 310 | Customer | 48247 | Load | Tran1phOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | OK - 2021
J2001.000052 | PD-01012020-00862 | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_629 | 730629 | 2020-01-01 09:12 | 2020-01-01 10:25 | 73.12 | 4 | 5 | 265.8667 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | SEMINOLE | 2220 GROUNDS | CMI_NORMAL | NO | NO | NO | 859723 | 114164 | 13574 | 4055 | 567 | 0.00030925 | 4.6527e-06 | 66.4667 | 1 | 310 | Load | 5941 | Load | Tran1phOH | DELBERT HISAW | 405-683-1721 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | OK - 2021
J2001.000049 | PD-01012020-00861 | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3421 | 843421 | 2020-01-01 09:14 | 2020-01-01 11:23 | 129.13 | 1 | 2 | 121.8667 | 3 | DAMAGED BY PUBLIC | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 1804 NE.56 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167925 | 148141 | 1224 | 498 | 0.00014175 | 1.1632e-06 | 121.8667 | 1 | 320 | Customer | 18697 | Load | Tran1phOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | #N/A
J2001.000053 |  | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_622 | 410622 | 2020-01-01 09:27 | 2020-01-01 09:27 | 0 | 1501 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ENID | 1600 N 4TH | CMI_MOMENTARY | YES | NO | NO | 859723 | 53470 | 37546 | 6007 | 1501 | 0 | 0.0017459 | 0 | 1 | 0 | Feeder | HEMLOCK_622 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-01 | 2020 |  | #N/A
J2001.000056 | PD-01012020-00863 | METRO WEST | WEST | 8323:RICHARDS | RICHARDS_2324 | 832324 | 2020-01-01 09:39 | 2020-01-01 12:10 | 151.3 | 1 | 1 | 136.6167 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 8517 NW 129th St | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859723 | 128525 | 115804 | 4997 | 1586 | 0.00015891 | 1.1632e-06 | 136.6167 | 1 | 320 | Customer | 380735 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | #N/A
J2001.000057 | PD-01012020-00864 | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_622 | 410622 | 2020-01-01 09:54 | 2020-01-01 10:43 | 49.13 | 1 | 1 | 47.2833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ENID | 2807 N.JEFFERSON | CMI_NORMAL | NO | NO | NO | 859723 | 53470 | 37546 | 6007 | 1501 | 5.4998e-05 | 1.1632e-06 | 47.2833 | 1 | 310 | Customer | 95 | Load | Tran1phOH | WILLIAM R PETHICK | 580-278-8129 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | #N/A
J2001.000061 | PD-01012020-00867 | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_424 | 580424 | 2020-01-01 10:16 | 2020-01-01 11:58 | 101.98 | 1 | 1 | 87.9667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ADA | PASS Y ON FITTS HWY | CMI_NORMAL | NO | NO | NO | 859723 | 77490 | 11493 | 3410 | 435 | 0.00010232 | 1.1632e-06 | 87.9667 | 1 | 310 | Customer | 8907 | Load | Tran1phOH | CAMERON BRADY | 580-307-7052 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | OK - 2021
J2001.000062 | PD-01012020-00868 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2123 | 822123 | 2020-01-01 10:17 | 2020-01-01 13:01 | 164.27 | 1 | 1 | 8.3969 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1213 N.META AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167925 | 148141 | 9234 | 1487 | 9.7669e-06 | 1.1632e-06 | 8.3969 | 1 | 310 | Customer | 13349 | Load | Tran1phOH | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | OK - 2020
J2001.000064 | PD-01012020-00869 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7424 | 847424 | 2020-01-01 10:36 | 2020-01-01 11:43 | 67.35 | 1 | 1 | 67.35 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1324 STATON DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167925 | 148141 | 6147 | 2197 | 7.8339e-05 | 1.1632e-06 | 67.35 | 1 | 310 | Customer | 4509 | Load | Tran1phOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | OK - 2020
J2001.000074 | PD-01012020-00871 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3731 | 833731 | 2020-01-01 11:31 | 2020-01-01 12:27 | 56.47 | 7 | 8 | 383.8333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1207 NW.86 | CMI_NORMAL | NO | NO | NO | 859723 | 167925 | 148141 | 5755 | 1902 | 0.00044646 | 8.1422e-06 | 54.8333 | 1 | 310 | Load | 6905 | Load | TranOHDeltaSplitBank | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | OK - 2020
J2001.000077 | PD-01012020-00874 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_866 | 830866 | 2020-01-01 11:50 | 2020-01-01 13:10 | 80.37 | 1 | 1 | 4.3667 | 22 | WIND | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | N May and Quail Springs Pkwy | CMI_NORMAL | NO | NO | NO | 859723 | 167925 | 148141 | 19332 | 4301 | 5.0792e-06 | 1.1632e-06 | 4.3667 | 1 | 320 | Customer | 256970 | Load | Tran3phPadWye | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | #N/A
J2001.000081 | PD-01012020-00875 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4029 | 834029 | 2020-01-01 12:10 | 2020-01-01 12:27 | 17.5 | 1 | 1 | 6.8816 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | OKC | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 128525 | 115804 | 10838 | 1146 | 8.0044e-06 | 1.1632e-06 | 6.8816 | 1 | 320 | Customer | 87497 | Load | Tran1phPad | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | #N/A
J2001.000083 | PD-01012020-00878 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2024 | 862024 | 2020-01-01 12:19 | 2020-01-01 13:57 | 97.73 | 1 | 1 | 31.8439 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3616 S. Robinson, in alley | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 158924 | 102033 | 4737 | 770 | 3.704e-05 | 1.1632e-06 | 31.8439 | 1 | 310 | Customer | 20508 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | #N/A
J2001.000084 |  | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5029 | 865029 | 2020-01-01 12:21 | 2020-01-01 12:21 | 0 | 1735 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MIDWEST CITY | 8346 SE 15TH | CMI_MOMENTARY | YES | NO | NO | 859723 | 114164 | 71085 | 8624 | 1735 | 0 | 0.0020181 | 0 | 1 | 0 | Feeder | GLENDALE_5029 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-01 | 2020 |  | #N/A
J2001.000096 | PD-01012020-00883 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4122 | 814122 | 2020-01-01 12:45 | 2020-01-01 15:22 | 156.88 | 1 | 1 | 110.25 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 4901 S.BROADWAY PL | CMI_NORMAL | NO | NO | NO | 859723 | 158924 | 102033 | 5797 | 1269 | 0.00012824 | 1.1632e-06 | 110.25 | 1 | 310 | Customer | 36920 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | #N/A
J2001.000095 |  | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2923 | 812923 | 2020-01-01 12:46 | 2020-01-01 12:50 | 3.72 | 1 | 1 | 3.7167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2809 SW.53 | CMI_MOMENTARY | YES | NO | NO | 859723 | 158924 | 102033 | 6369 | 1632 | 4.3231e-06 | 1.1632e-06 | 3.7167 | 1 | 310 | Customer | 25803 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | #N/A
J2001.000100 | PD-01012020-00886 | NORTHEAST | SAPULPA | 3213:BOWDEN | BOWDEN_1329 | 321329 | 2020-01-01 12:53 | 2020-01-01 13:55 | 62.38 | 1 | 2 | 60.0833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | SAPULPA | 1 1/2W HY97 ON 81,1/4N,1/4E | CMI_NORMAL | NO | NO | NO | 859723 | 73883 | 40681 | 3366 | 1516 | 6.9887e-05 | 1.1632e-06 | 60.0833 | 1 | 310 | Load | 19234 | Load | Tran1phOH | JOSHUA N MCKINNEY | 918-863-6313 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | OK - 2020
J2001.000101 | PD-01012020-00889 | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_450 | 710450 | 2020-01-01 13:01 | 2020-01-01 21:55 | 534.32 | 1 | 1 | 530.3667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | SPARKS | 9MS CHANDLER | CMI_NORMAL | NO | NO | NO | 859723 | 114164 | 7447 | 2817 | 401 | 0.0006169 | 1.1632e-06 | 530.3667 | 1 | 310 | Load | 5713 | Load | Tran1phOH | AUSTIN WELLIVER | 405-221-0200 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | OK - 2021
J2001.000105 | PD-01012020-00891 | NORTHEAST | SAPULPA | 7605:DRUMRIGHT | DRUMRIGHT_544 | 760544 | 2020-01-01 13:05 | 2020-01-01 14:43 | 97.68 | 1 | 2 | 93.4667 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | OILTON | SW COR 5TH + CMPBLL | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859723 | 73883 | 40681 | 1691 | 1112 | 0.00010872 | 1.1632e-06 | 93.4667 | 1 | 310 | Customer | 14519 | Load | Tran1phOH | NICHOLAS MANION | 918-290-1327 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | #N/A
J2001.000107 | PD-01012020-00892 | METRO WEST | WEST | 8335:BETHANY | BETHANY_3528 | 833528 | 2020-01-01 13:09 | 2020-01-01 14:55 | 106.23 | 19 | 3 | 1976 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | MAC ARTHUR / NW 29TH | CMI_NORMAL | NO | NO | NO | 859723 | 128525 | 115804 | 7861 | 2124 | 0.0022984 | 2.21e-05 | 104 | 1 | 310 | Mainline | 7163 | Fuse | FuseOH | MARK A PALMORE | 405-512-1933 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | OK - 2022
J2001.000104 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5121 | 815121 | 2020-01-01 13:17 | 2020-01-01 13:23 | 6.48 | 1 | 1 | 6.4833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | SW.89 + MAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 158924 | 102033 | 13932 | 1998 | 7.5412e-06 | 1.1632e-06 | 6.4833 | 1 | 310 | Customer | 71420 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | #N/A
J2001.000118 | PD-01012020-00896 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2231 | 852231 | 2020-01-01 13:47 | 2020-01-01 17:03 | 195.67 | 3 | 3 | 577.35 | 4 | DETERIORATION | 27 | CUTOUT | OKLAHOMA CITY | 15912 SE 44TH | CMI_NORMAL | NO | NO | NO | 859723 | 114164 | 71085 | 11611 | 1436 | 0.00067155 | 3.4895e-06 | 192.45 | 1 | 310 | Load | 66333 | Load | Tran1phOH | JACOB SHANDY | 918-623-6369 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | OK - 2021
J2001.000114 |  | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-01-01 13:49 | 2020-01-01 14:40 | 51.12 | 1 | 1 | 49.8667 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | EL RENO | 4503 N HIGHWAY 81 | CMI_PLANNED | YES | NO | NO | 859723 | 128525 | 12721 | 6931 | 1822 | 5.8003e-05 | 1.1632e-06 | 49.8667 | 1 | 308 | Load | 251775 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | #N/A
J2001.000120 | PD-01012020-00897 | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-01 14:06 | 2020-01-01 15:33 | 87.48 | 1 | 1 | 87.4833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | HARTMAN | 1MS Hwy 64 & Main | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 82074 | 7527 | 1501 | 1198 | 0.00010176 | 1.1632e-06 | 87.4833 | 1 | 320 | Load | 320858 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-01 | 2020 |  | Ark - Series 2
J2001.000122 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-01 14:13 | 2020-01-01 14:59 | 46.17 | 1 | 0 | 39.7 | 4 | DETERIORATION | 2 | TRANSFORMER OH | HARTMAN | HARTMAN-E.HWY 64 ON HARRIS | CMI_PLANNED | YES | NO | NO | 859723 | 82074 | 7527 | 1501 | 1198 | 4.6178e-05 | 1.1632e-06 | 39.7 | 1 | 0 | Load | 1715 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-01 | 2020 |  | Ark - Series 2
J2001.000127 |  | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4122 | 814122 | 2020-01-01 14:17 | 2020-01-01 15:28 | 71.3 | 4 | 5 | 75.4667 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 4901 S.BROADWAY PL | CMI_NORMAL | NO | NO | NO | 859723 | 158924 | 102033 | 5797 | 1269 | 8.778e-05 | 4.6527e-06 | 18.8667 | 1 | 310 | Load | 36920 | Load | Tran1phOH | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | #N/A
J2001.000125 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4035 | 834035 | 2020-01-01 14:26 | 2020-01-01 14:31 | 5.35 | 1 | 1 | 5.35 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 12000 N. MacArthur | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 128525 | 115804 | 10838 | 1422 | 6.2229e-06 | 1.1632e-06 | 5.35 | 1 | 310 | Load | 373509 | Load | Tran3phPadWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | #N/A
J2001.000132 | PD-01012020-00901 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3731 | 833731 | 2020-01-01 14:41 | 2020-01-01 15:51 | 69.93 | 1 | 1 | 69.9333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | THE VILLAGE | 1512 CASADY LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167925 | 148141 | 5755 | 1902 | 8.1344e-05 | 1.1632e-06 | 69.9333 | 1 | 310 | Customer | 13998 | Load | Tran1phOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | OK - 2020
J2001.000137 | PD-01012020-00905 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1524 | 811524 | 2020-01-01 14:43 | 2020-01-01 16:39 | 116.48 | 1 | 2 | 99.3167 | 27 | TREE:NON PREVENTABLE | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 2115 SW.34 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859723 | 158924 | 102033 | 6051 | 2070 | 0.00011552 | 1.1632e-06 | 99.3167 | 1 | 311 | Customer | 54798 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | OK - 2022
J2001.000134 | PD-01012020-00903 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6522 | 836522 | 2020-01-01 14:44 | 2020-01-01 17:23 | 159.18 | 1 | 1 | 147.7333 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 5812 NW.82 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859723 | 128525 | 115804 | 7416 | 1859 | 0.00017184 | 1.1632e-06 | 147.7333 | 1 | 310 | Customer | 28963 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | OK - 2021
J2001.000140 | PD-01012020-00906 | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2824 | 312824 | 2020-01-01 15:09 | 2020-01-01 16:18 | 69.43 | 1 | 1 | 69.4333 | 12 | POOR CONNECTION | 50 | CONNECTOR | MUSKOGEE | 1606 S.ABERDEEN | CMI_NORMAL | NO | NO | NO | 859723 | 73883 | 33202 | 5270 | 1608 | 8.0762e-05 | 1.1632e-06 | 69.4333 | 1 | 310 | Customer | 5199 | Load | Tran1phOH | JOSH CHENEY | 918-619-3590 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-01 | 2020 |  | OK - 2020
J2001.000147 | PD-01012020-00908 | METRO EAST | SHAWNEE | 7433:ROCK CREEK | ROCK_CREEK_3322 | 743322 | 2020-01-01 15:12 | 2020-01-01 20:41 | 329.05 | 1 | 2 | 315.1 | 4 | DETERIORATION | 12 | POLE | SHAWNEE | 3/4ME STARLITE SS | CMI_NORMAL | NO | NO | NO | 859723 | 114164 | 22058 | 1798 | 1032 | 0.00036651 | 1.1632e-06 | 315.1 | 1 | 310 | Load | 11560 | Load | Tran1phOH | AUSTIN WELLIVER | 405-221-0200 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | #N/A
J2001.000143 |  | METRO EAST | SHAWNEE | 7433:ROCK CREEK | ROCK_CREEK_3322 | 743322 | 2020-01-01 15:12 | 2020-01-01 15:12 | 0.3 | 1032 | 0 | 275.2 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | SHAWNEE | 41873 WESTECH RD | CMI_MOMENTARY | YES | NO | NO | 859723 | 114164 | 22058 | 1798 | 1032 | 0.0003201 | 0.0012004 | 0.26667 | 1 | 0 | Feeder | ROCK CRK_3322 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-01 | 2020 |  | #N/A
J2001.000145 | PD-01012020-00907 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6024 | 836024 | 2020-01-01 15:15 | 2020-01-01 18:24 | 188.65 | 1 | 1 | 53.6333 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 2312 MARKWELL PL | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859723 | 128525 | 115804 | 5501 | 1341 | 6.2384e-05 | 1.1632e-06 | 53.6333 | 1 | 320 | Customer | 27559 | Load | Tran1phOH | CONTRACTOR BHI51 DAVID ELLIOT INC | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | OK - 2022
J2001.000153 | PD-01012020-00912 | METRO SOUTH | SOUTH | 8709:LITTLE R LAKE | LITTLE_RIVER_L_921 | 870921 | 2020-01-01 15:50 | 2020-01-01 21:11 | 320.55 | 1 | 1 | 312.8833 | 13 | PREMATURE FAILURE | 2 | TRANSFORMER OH | NORMAN | 2507 108TH NE. | CMI_NORMAL | NO | NO | NO | 859723 | 158924 | 56891 | 672 | 672 | 0.00036394 | 1.1632e-06 | 312.8833 | 1 | 320 | Load | 81198 | Load | Tran1phOH | CHAD W GLEAVE | 405-250-7464 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | #N/A
J2001.000154 | PD-01012020-00913 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1229 | 831229 | 2020-01-01 15:52 | 2020-01-01 16:26 | 33.58 | 1 | 1 | 33.5833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2029 NW.45 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167925 | 148141 | 7733 | 787 | 3.9063e-05 | 1.1632e-06 | 33.5833 | 1 | 310 | Customer | 12365 | Load | Tran1phOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | OK - 2022
J2001.000156 |  | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1524 | 811524 | 2020-01-01 16:01 | 2020-01-01 16:44 | 42.88 | 7 | 6 | 145.1333 | 27 | TREE:NON PREVENTABLE | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 2115 SW.34 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859723 | 158924 | 102033 | 6051 | 2070 | 0.00016881 | 8.1422e-06 | 20.7333 | 1 | 311 | Load | 54798 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | OK - 2022
J2001.000159 | PD-01012020-00915 | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2163 | 892163 | 2020-01-01 16:14 | 2020-01-01 17:25 | 70.8 | 1 | 1 | 52.8833 | 22 | WIND | 31 | CONDUCTOR SERVICE - OH | UNION CITY | UNION CITY | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859723 | 128525 | 12721 | 3172 | 1130 | 6.1512e-05 | 1.1632e-06 | 52.8833 | 1 | 320 | Customer | 47313 | Load | Tran1phOH | JOSH BLACK | 405-403-9382 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | OK - 2021
J2001.000164 | PD-01012020-00917 | METRO NORTH | GUTHRIE | 8807:CRESCENT | CRESCENT_723 | 880723 | 2020-01-01 16:24 | 2020-01-01 18:12 | 107.67 | 1 | 1 | 90.2667 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | CRESCENT | LT 130+131 CRES SPG | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859723 | 167925 | 19784 | 1761 | 888 | 0.000105 | 1.1632e-06 | 90.2667 | 1 | 320 | Customer | 32954 | Load | Tran1phOH | KELLEY D WATSON | 405-763-8148 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | #N/A
J2001.000166 | PD-01012020-00918 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4031 | 834031 | 2020-01-01 16:27 | 2020-01-01 17:51 | 84.1 | 1 | 1 | 40.57 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | J L DENNIS + 109TH PLACE-LT 17 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 128525 | 115804 | 10838 | 1640 | 4.719e-05 | 1.1632e-06 | 40.57 | 1 | 310 | Customer | 33642 | Load | Tran1phPad | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | #N/A
J2001.000172 |  | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4823 | 824823 | 2020-01-01 17:33 | 2020-01-01 18:50 | 77.63 | 5 | 5 | 388.2068 | 3 | DAMAGED BY PUBLIC | 12 | POLE | OKLAHOMA CITY | 3535 SW.25 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167925 | 148141 | 4181 | 1792 | 0.00045155 | 5.8158e-06 | 77.6414 | 1 | 310 | Load | 25416 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | OK - 2021
J2001.000173 |  | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4823 | 824823 | 2020-01-01 17:33 | 2020-01-01 18:50 | 77.27 | 3 | 3 | 231.8229 | 3 | DAMAGED BY PUBLIC | 12 | POLE | OKLAHOMA CITY | 3516 SW.25 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167925 | 148141 | 4181 | 1792 | 0.00026965 | 3.4895e-06 | 77.2743 | 1 | 308 | Load | 36391 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | OK - 2021
J2001.000180 | PD-01012020-00924 | NORTHEAST | SAPULPA | 3214:LONE STAR | LONE_STAR_1422 | 321422 | 2020-01-01 18:47 | 2020-01-01 20:53 | 125.55 | 14 | 7 | 1667.6333 | 22 | WIND | 23 | FUSE - PRIMARY | SAPULPA | 1/4 M S OF 151 ON 97 W | CMI_NORMAL | NO | NO | NO | 859723 | 73889 | 40686 | 2651 | 1093 | 0.0019397 | 1.6284e-05 | 119.1167 | 1 | 310 | Tap | 62375 | Fuse | FuseOH | JOSHUA N MCKINNEY | 918-863-6313 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-01 | 2020 |  | OK - 2020
J2001.000179 |  | NORTHEAST | SAPULPA | 3214:LONE STAR | LONE_STAR_1422 | 321422 | 2020-01-01 18:48 | 2020-01-01 18:48 | 0.08 | 1091 | 0 | 90.9167 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | SAPULPA | 11511 W LONE STAR RD | CMI_MOMENTARY | YES | NO | NO | 859723 | 73889 | 40686 | 2651 | 1093 | 0.00010575 | 0.001269 | 0.083333 | 1 | 0 | Feeder | LONE STR_1422 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-01 | 2020 |  | OK - 2020
J2001.000189 |  | METRO WEST | WEST | 8335:BETHANY | BETHANY_3527 | 833527 | 2020-01-01 20:08 | 2020-01-01 20:53 | 45.12 | 10 | 9 | 205.5 | 12 | POOR CONNECTION | 34 | CONDUCTOR SECONDARY - OH | WARR ACRES | 5345 NW.44 | CMI_NORMAL | NO | NO | NO | 859723 | 128532 | 115810 | 7861 | 1662 | 0.00023903 | 1.1632e-05 | 20.55 | 1 | 310 | Load | 11287 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | OK - 2022
J2001.000193 | PD-01012020-00927 | METRO WEST | WEST | 8359:YUKON | YUKON_5921 | 835921 | 2020-01-01 20:43 | 2020-01-02 14:47 | 1083.55 | 56 | 69 | 8441.0667 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | YUKON | MABEL FRY + MUSTANG | CMI_NORMAL | NO | NO | NO | 859723 | 128532 | 115810 | 6408 | 1802 | 0.0098184 | 6.5137e-05 | 150.7333 | 1 | 310 | Mainline | 17515 | Fuse | FuseRiser | BAD ORDER PRIMARY RES COORD | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | #N/A
J2001.000197 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5921 | 835921 | 2020-01-01 21:08 | 2020-01-01 21:27 | 18.63 | 1 | 1 | 18.6333 | 1 | CANCELLED | 57 | CANCELLED | YUKON | 303 ANNAWOOD DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 128532 | 115810 | 6408 | 1802 | 2.1674e-05 | 1.1632e-06 | 18.6333 | 1 | 310 | Customer | 42329 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | #N/A
J2001.000199 |  | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2922 | 812922 | 2020-01-01 21:21 | 2020-01-01 21:42 | 20.65 | 1 | 1 | 20.65 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | SW.37 + GOFF | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 158927 | 102033 | 6369 | 1134 | 2.4019e-05 | 1.1632e-06 | 20.65 | 1 | 310 | Customer | 7445 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | #N/A
J2001.000202 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_631 | 460631 | 2020-01-01 21:30 | 2020-01-01 21:41 | 10.95 | 1 | 1 | 10.95 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | WOODWARD | W-22ND + BRANW APT-WOODWARD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 53477 | 10409 | 5676 | 1170 | 1.2737e-05 | 1.1632e-06 | 10.95 | 1 | 310 | Customer | 2157 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | #N/A
J2001.000204 | PD-01012020-00930 | SOUTHERN | PAULS VALLEY | 5619:RUSH CREEK | RUSH_CREEK_1921 | 561921 | 2020-01-01 21:48 | 2020-01-01 23:04 | 76.48 | 1 | 1 | 76.4833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | PAULS VALLEY | 52O W PAUL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 77499 | 6194 | 2072 | 823 | 8.8963e-05 | 1.1632e-06 | 76.4833 | 1 | 310 | Customer | 14077 | Load | Tran1phOH | BRUCE E BEAM | 405-626-0490 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | #N/A
J2001.000213 |  | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2823 | 312823 | 2020-01-01 22:23 | 2020-01-02 00:28 | 125.07 | 2 | 2 | 229.3833 | 4 | DETERIORATION | 12 | POLE | MUSKOGEE | 714 S B ST | CMI_NORMAL | NO | NO | NO | 859723 | 73889 | 33203 | 5270 | 1391 | 0.00026681 | 2.3263e-06 | 114.6917 | 1 | 308 | Load | 4951 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-01 | 2020 |  | #N/A
J2001.000209 |  | SOUTHERN | ARDMORE | 5106:HARRIS ST | HARRIS_ST_621 | 510621 | 2020-01-01 22:28 | 2020-01-01 22:30 | 2.47 | 61 | 0 | 150.4667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 2307 HARRIS | CMI_MOMENTARY | YES | NO | NO | 859723 | 77499 | 23559 | 2066 | 61 | 0.00017502 | 7.0953e-05 | 2.4667 | 1 | 0 | Feeder | HARRIS_ST_621 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-01 | 2020 |  | #N/A
J2001.000210 |  | SOUTHERN | ARDMORE | 5106:HARRIS ST | HARRIS_ST_622 | 510622 | 2020-01-01 22:28 | 2020-01-01 22:30 | 2.47 | 1106 | 0 | 2728.1333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 2307 HARRIS | CMI_MOMENTARY | YES | NO | NO | 859723 | 77499 | 23559 | 2066 | 1106 | 0.0031733 | 0.0012865 | 2.4667 | 1 | 0 | Feeder | HARRIS_ST_622 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-01 | 2020 |  | #N/A
J2001.000214 |  | METRO WEST | WEST | 8335:BETHANY | BETHANY_3527 | 833527 | 2020-01-01 23:19 | 2020-01-01 23:33 | 14.62 | 10 | 1 | 78.8713 | 5 | ELECTRICAL TRACKING | 2 | TRANSFORMER OH | WARR ACRES | 5345 NW.44 | CMI_PLANNED | YES | NO | NO | 859723 | 128532 | 115810 | 7861 | 1662 | 9.174e-05 | 1.1632e-05 | 7.8871 | 1 | 310 | Load | 11287 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-01 | 2020 |  | OK - 2022
J2001.000226 |  | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_422 | 580422 | 2020-01-02 01:33 | 2020-01-02 01:45 | 11.75 | 1 | 1 | 11.75 | 1 | CANCELLED | 57 | CANCELLED | ADA | 500 E.20TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 77499 | 11496 | 3410 | 1426 | 1.3667e-05 | 1.1632e-06 | 11.75 | 1 | 310 | Customer | 15938 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000227 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5921 | 835921 | 2020-01-02 02:03 | 2020-01-02 02:03 | 0 | 1746 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | YUKON | 4323 N CZECH HALL RD | CMI_MOMENTARY | YES | NO | NO | 859723 | 128532 | 115810 | 6408 | 1802 | 0 | 0.0020309 | 0 | 1 | 0 | Feeder | YUKON_5921 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000229 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5921 | 835921 | 2020-01-02 02:21 | 2020-01-02 15:14 | 772.82 | 68 | 54 | 44237.4 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | YUKON | WALSH LN + MUSTANG RD | CMI_NORMAL | NO | NO | NO | 859723 | 128532 | 115810 | 6408 | 1802 | 0.051455 | 7.9095e-05 | 650.55 | 1 | 310 | Mainline | 17513 | Fuse | FuseRiser | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000231 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5921 | 835921 | 2020-01-02 02:21 | 2020-01-02 13:25 | 663.3 | 1 | 2 | 650.5333 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | YUKON | 1037 COOPER LN | CMI_NORMAL | NO | NO | NO | 859723 | 128532 | 115810 | 6408 | 1802 | 0.00075668 | 1.1632e-06 | 650.5333 | 1 | 310 | Customer | 58430 | Load | Tran1phPad | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000232 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5923 | 835923 | 2020-01-02 02:40 | 2020-01-02 02:43 | 3.37 | 1 | 1 | 3.3667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | YUKON | 108 N.11 | CMI_MOMENTARY | YES | NO | NO | 859723 | 128532 | 115810 | 6408 | 1150 | 3.916e-06 | 1.1632e-06 | 3.3667 | 1 | 310 | Customer | 19354 | Load | TranOHDeltaSplitBank | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000233 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5921 | 835921 | 2020-01-02 03:00 | 2020-01-02 03:00 | 0 | 1677 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | YUKON | 4323 N CZECH HALL RD | CMI_MOMENTARY | YES | NO | NO | 859723 | 128532 | 115810 | 6408 | 1802 | 0 | 0.0019506 | 0 | 1 | 0 | Feeder | YUKON_5921 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000235 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5921 | 835921 | 2020-01-02 03:18 | 2020-01-02 06:09 | 171.68 | 1 | 1 | 171.6833 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | YUKON | 733 HEATHER TR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 128532 | 115810 | 6408 | 1802 | 0.0001997 | 1.1632e-06 | 171.6833 | 1 | 310 | Customer | 73637 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000237 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9922 | 829922 | 2020-01-02 03:30 | 2020-01-02 03:42 | 11.35 | 1 | 1 | 11.35 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6656 NW.10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 128532 | 115810 | 9210 | 842 | 1.3202e-05 | 1.1632e-06 | 11.35 | 1 | 310 | Customer | 34523 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000240 | PD-01022020-00003 | ARKANSAS | POTEAU | 3514:HEAVENER | HEAVENER 22 | 351422 | 2020-01-02 05:15 | 2020-01-02 06:42 | 86.65 | 1 | 2 | 84.5333 | 4 | DETERIORATION | 21 | FUSE - TRANSFORMER | HEAVENER | ROUTE 1 | CMI_NORMAL | NO | NO | NO | 859723 | 82085 | 13444 | 1763 | 1301 | 9.8326e-05 | 1.1632e-06 | 84.5333 | 1 | 310 | Customer | 10310 | Load | Tran1phOH | GREGORY D SMITH | 918-839-4897 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000239 | PD-01022020-00002 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6522 | 836522 | 2020-01-02 05:17 | 2020-01-02 06:23 | 66.32 | 1 | 1 | 66.3167 | 13 | PREMATURE FAILURE | 15 | METER - SECONDARY | OKLAHOMA CITY | 6713 LYREWOOD | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859723 | 128532 | 115810 | 7416 | 1859 | 7.7137e-05 | 1.1632e-06 | 66.3167 | 1 | 310 | Customer | 47374 | Load | Tran1phPad | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000243 |  | METRO WEST | WEST | 8158:SARA | SARA_5871 | 815871 | 2020-01-02 06:27 | 2020-01-02 06:33 | 6.68 | 1 | 1 | 6.6833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | Mustang Drive & Mustang Rd Mustang Creek Apts | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 128532 | 115810 | 18198 | 5379 | 7.7738e-06 | 1.1632e-06 | 6.6833 | 1 | 310 | Customer | 238511 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2022
J2001.000245 | PD-01022020-00008 | NORTHEAST | SAPULPA | 7611:MORRISON TAP | MORRISON_TAP_1121 | 761121 | 2020-01-02 06:33 | 2020-01-02 09:42 | 189.48 | 1 | 1 | 185.4 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MORRISON | 1/2 mi. N. of Harvest Rd. on CR 240 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 73889 | 40686 | 891 | 464 | 0.00021565 | 1.1632e-06 | 185.4 | 1 | 320 | Load | 40462 | Load | Tran1phOH | BRAD WRIGHT | 918-629-1747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000247 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-01-02 06:45 | 2020-01-02 07:05 | 19.85 | 1 | 1 | 19.85 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1518 NW.102 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167942 | 148151 | 8780 | 1948 | 2.3089e-05 | 1.1632e-06 | 19.85 | 1 | 310 | Customer | 18190 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000248 | PD-01022020-00013 | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2824 | 312824 | 2020-01-02 06:55 | 2020-01-02 08:33 | 97.87 | 1 | 1 | 96.4667 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 21 | FUSE - TRANSFORMER | MUSKOGEE | 906 HANCOCK | CMI_NORMAL | NO | NO | NO | 859723 | 73889 | 33203 | 5270 | 1608 | 0.00011221 | 1.1632e-06 | 96.4667 | 1 | 310 | Customer | 3849 | Load | Tran1phOH | REID R WILLIAMS | 512-618-8800 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-01-02 | 2020 |  | OK - 2020
J2001.000254 | PD-01022020-00010 | ARKANSAS | POTEAU | 3514:HEAVENER | HEAVENER 22 | 351422 | 2020-01-02 07:19 | 2020-01-02 10:04 | 165.37 | 54 | 22 | 8267.4 | 4 | DETERIORATION | 28 | CROSSARM | HEAVENER | 1MI SW TWN HODGENS LN | CMI_NORMAL | NO | NO | NO | 859723 | 82085 | 13444 | 1763 | 1301 | 0.0096164 | 6.2811e-05 | 153.1 | 1 | 310 | Mainline | 9607 | Fuse | FuseOH | BRANDON K BRYAN | 479-831-3888 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000261 | PD-01022020-00018 | SOUTHERN | DURANT | 5512:COLBERT | COLBERT_1222 | 551222 | 2020-01-02 07:44 | 2020-01-02 09:03 | 79.08 | 1 | 1 | 79.0833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | CARTWRIGHT | 1W COLBERT.4S OF 75A | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 77499 | 15461 | 2165 | 1270 | 9.1987e-05 | 1.1632e-06 | 79.0833 | 1 | 320 | Customer | 7511 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000266 | PD-01022020-00027 | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_433 | 510433 | 2020-01-02 07:46 | 2020-01-02 09:36 | 109.5 | 1 | 2 | 91.7667 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | ARDMORE | 824 5 NE. | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859723 | 77499 | 23559 | 2316 | 1257 | 0.00010674 | 1.1632e-06 | 91.7667 | 1 | 311 | Customer | 19591 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000267 | PD-01022020-00031 | NORTHEAST | MUSKOGEE | 3327:VIAN | VIAN 22 | 332722 | 2020-01-02 08:04 | 2020-01-02 11:02 | 177.87 | 3 | 5 | 530.55 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | VIAN | 1/2BS HUNTER + RODGERS (WS) | CMI_NORMAL | NO | NO | NO | 859723 | 73889 | 33203 | 779 | 779 | 0.00061712 | 3.4895e-06 | 176.85 | 1 | 310 | Secondary | 10763 | Load | Tran1phOH | JAMES MCDONALD | 405-361-7186 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000269 |  | METRO NORTH | NORTH | 8506:PARK PLACE | PARK_PLACE_623 | 850623 | 2020-01-02 08:13 | 2020-01-02 08:13 | 0 | 783 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | 0 | 0 | CMI_MOMENTARY | YES | NO | NO | 859723 | 167942 | 148151 | 829 | 266 | 0 | 0.00091076 | 0 | 1 | 0 | Feeder | PARK_PLACE_623 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000271 | PD-01022020-00032 | NORTHEAST | MUSKOGEE | 3314:PORUM | PORUM_1421 | 331421 | 2020-01-02 08:13 | 2020-01-02 10:09 | 115.78 | 1 | 1 | 115.7833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | PORUM | 3RD/4TH + UTE, PORUM | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 73889 | 33203 | 596 | 596 | 0.00013468 | 1.1632e-06 | 115.7833 | 1 | 320 | Customer | 5771 | Load | Tran1phOH | JAMES MCDONALD | 405-361-7186 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | OK - 2022
J2001.000270 |  | METRO SOUTH | SOUTH | 8728:CHERRY CREEK | CHERRY_CREEK_2824 | 872824 | 2020-01-02 08:14 | 2020-01-02 09:03 | 48.97 | 9 | 4 | 376.05 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | NORMAN | 4301 HUNTLEIGH CT | CMI_PLANNED | YES | NO | NO | 859723 | 158927 | 56894 | 7100 | 1202 | 0.00043741 | 1.0468e-05 | 41.7833 | 1 | 310 | Load | 48948 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000278 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-02 08:17 | 2020-01-02 12:48 | 271.17 | 1 | 1 | 268.9833 | 4 | DETERIORATION | 12 | POLE | COAL HILL | 984 CR 237 | CMI_PLANNED | YES | NO | NO | 859723 | 82085 | 7527 | 1501 | 1198 | 0.00031287 | 1.1632e-06 | 268.9833 | 1 | 308 | Tap | 6393 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-02 | 2020 |  | Ark - Series 2
J2001.000275 | PD-01022020-00049 | METRO WEST | WEST | 8158:SARA | SARA_5862 | 815862 | 2020-01-02 08:18 | 2020-01-02 09:05 | 46.82 | 1 | 1 | 11.8729 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 8200 SW.44TH ST. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 128532 | 115810 | 18198 | 3586 | 1.381e-05 | 1.1632e-06 | 11.8729 | 1 | 320 | Customer | 202086 | Load | Tran3phWye | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2022
J2001.000276 | PD-01022020-00048 | METRO NORTH | NORTH | 8506:PARK PLACE | PARK_PLACE_623 | 850623 | 2020-01-02 08:22 | 2020-01-02 09:09 | 46.93 | 1 | 1 | 46.9333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 9 NE 14TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167942 | 148151 | 829 | 266 | 5.4591e-05 | 1.1632e-06 | 46.9333 | 1 | 310 | Customer | 7270 | Load | TranOpenDelta | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000283 |  | ARKANSAS | POTEAU | 3514:HEAVENER | HEAVENER 22 | 351422 | 2020-01-02 08:37 | 2020-01-02 10:14 | 97.2 | 1 | 1 | 97.2 | 1 | CANCELLED | 57 | CANCELLED | HODGEN | 2 BLKS W OF YATES - HODGENS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 82085 | 13444 | 1763 | 1301 | 0.00011306 | 1.1632e-06 | 97.2 | 1 | 310 | Load | 1342 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000284 |  | METRO NORTH | NORTH | 8430:REMINGTON PARK | REMINGTON_PARK_3022 | 843022 | 2020-01-02 08:38 | 2020-01-02 09:07 | 29.07 | 2 | 2 | 55.5167 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 7105 N.KELLEY | CMI_PLANNED | YES | NO | NO | 859723 | 167942 | 148151 | 845 | 669 | 6.4575e-05 | 2.3263e-06 | 27.7583 | 1 | 308 | Load | 24015 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000286 |  | METRO WEST | WEST | 8158:SARA | SARA_5871 | 815871 | 2020-01-02 08:47 | 2020-01-02 08:55 | 7.85 | 1 | 1 | 7.85 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | Mustang Drive & Mustang Rd Mustang Creek Apts | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 128532 | 115810 | 18198 | 5379 | 9.1308e-06 | 1.1632e-06 | 7.85 | 1 | 310 | Customer | 238511 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2022
J2001.000289 |  | ARKANSAS | POTEAU | 3514:HEAVENER | HEAVENER 22 | 351422 | 2020-01-02 08:50 | 2020-01-02 09:38 | 48.1 | 4 | 3 | 174.5333 | 4 | DETERIORATION | 28 | CROSSARM | HEAVENER | OLD HWY 59 1.5 MI S TN | CMI_PLANNED | YES | NO | NO | 859723 | 82085 | 13444 | 1763 | 1301 | 0.00020301 | 4.6527e-06 | 43.6333 | 1 | 308 | Tap | 26355 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000290 | PD-01022020-00099 | ARKANSAS | POTEAU | 3514:HEAVENER | HEAVENER 22 | 351422 | 2020-01-02 08:57 | 2020-01-02 09:58 | 61.42 | 1 | 1 | 55.15 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | HEAVENER | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 0 | 0 | 0 | 0 | 6.4149e-05 | 1.1632e-06 | 55.15 | 1 | 310 | Customer |  | 0 | 0 | TOBY C MEAD | 918-658-5596 |  |  |  |  | 06/10/2020 note from burchamc. Reference J2001.000290 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Emailed Brent Miller with blank transformer and circuit #'s. Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000293 | PD-01022020-00107 | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_521 | 320521 | 2020-01-02 09:08 | 2020-01-02 11:06 | 118.42 | 1 | 2 | 118.4167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SAPULPA | 618 S.POPLAR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 73889 | 40686 | 3833 | 1604 | 0.00013774 | 1.1632e-06 | 118.4167 | 1 | 310 | Customer | 42039 | Load | Tran1phOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | OK - 2022
J2001.000294 |  | SOUTHERN | HEALDTON | 5309:POOLEVILLE | POOLEVILLE_927 | 530927 | 2020-01-02 09:18 | 2020-01-02 10:04 | 45.9 | 1 | 0 | 42.8833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | 0 | NE NW NW SEC5 T2S R2W | CMI_PLANNED | YES | NO | NO | 859723 | 77499 | 6785 | 401 | 142 | 4.988e-05 | 1.1632e-06 | 42.8833 | 1 | 0 | Load | 25425 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000299 | PD-01022020-00116 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7029 | 817029 | 2020-01-02 09:19 | 2020-01-02 10:18 | 58.95 | 1 | 1 | 58.95 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 812 SE.86 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859723 | 158927 | 102033 | 9936 | 1756 | 6.8569e-05 | 1.1632e-06 | 58.95 | 1 | 320 | Customer | 83711 | Load | Tran3phWye | MIKE MITCHELL | 405-996-8178 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2022
J2001.000300 |  | METRO WEST | WEST | 8323:RICHARDS | RICHARDS_2323 | 832323 | 2020-01-02 09:23 | 2020-01-09 08:48 | 10044.73 | 2 | 0 | 20089.3211 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 9701 NW Expressway | CMI_PLANNED | YES | NO | NO | 859723 | 128532 | 115810 | 4997 | 1670 | 0.023367 | 2.3263e-06 | 10044.6606 | 1 | 0 | Load | 415843 | Load | Tran3phWye | OGE | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000301 |  | METRO WEST | WEST | 8222:CZECH HALL | CZECH_HALL_2224 | 822224 | 2020-01-02 09:24 | 2020-01-02 10:39 | 74.88 | 13 | 14 | 788.2333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | YUKON | 1009 WINNIPEG DR | CMI_PLANNED | YES | NO | NO | 859723 | 128532 | 115810 | 8592 | 1332 | 0.00091685 | 1.5121e-05 | 60.6333 | 1 | 310 | Load | 24614 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000302 |  | NORTHEAST | SAPULPA | 3213:BOWDEN | BOWDEN_1329 | 321329 | 2020-01-02 09:28 | 2020-01-02 13:11 | 222.62 | 10 | 0 | 2226.175 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | SAPULPA | REGENCY M/H PARK HWY 97 N. | CMI_PLANNED | YES | NO | NO | 859723 | 73889 | 40686 | 3367 | 1517 | 0.0025894 | 1.1632e-05 | 222.6175 | 1 | 0 | Load | 46516 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2020
J2001.000305 |  | METRO NORTH | NORTH | 8430:REMINGTON PARK | REMINGTON_PARK_3024 | 843024 | 2020-01-02 09:30 | 2020-01-02 10:02 | 32.57 | 1 | 0 | 32.5188 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | NE 49 AND EASTERN | CMI_PLANNED | YES | NO | NO | 859723 | 167942 | 148151 | 845 | 176 | 3.7825e-05 | 1.1632e-06 | 32.5188 | 1 | 0 | Load | 2183 | Load | Tran3phWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000306 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-02 09:32 | 2020-01-02 12:00 | 148.5 | 3 | 2 | 388.2 | 4 | DETERIORATION | 12 | POLE | HARTMAN | CIRCLE DR-SE OF MAIN + RR | CMI_PLANNED | YES | NO | NO | 859723 | 82085 | 7527 | 1501 | 1198 | 0.00045154 | 3.4895e-06 | 129.4 | 1 | 308 | Load | 17009 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-02 | 2020 |  | Ark - Series 2
J2001.000314 | PD-01022020-00154 | METRO EAST | SHAWNEE | 7433:ROCK CREEK | ROCK_CREEK_3322 | 743322 | 2020-01-02 09:49 | 2020-01-02 10:21 | 32.18 | 1 | 1 | 32.1833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SHAWNEE | 2524 N.HARRISON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 114172 | 22060 | 1799 | 1032 | 3.7435e-05 | 1.1632e-06 | 32.1833 | 1 | 310 | Customer | 11104 | Load | Tran1phPad | BRYAN K TATUM | 405-659-0746 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000318 |  | NORTHWEST | ENID | 4414:HENNESSEY | HENNESSEY_1424 | 441424 | 2020-01-02 09:51 | 2020-01-02 12:51 | 179.77 | 6 | 6 | 1067.2171 | 4 | DETERIORATION | 12 | POLE | HENNESSEY | 722 S CIMARRON | CMI_PLANNED | YES | NO | NO | 859723 | 53477 | 37553 | 1952 | 539 | 0.0012413 | 6.979e-06 | 177.8695 | 1 | 310 | Load | 4708 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000320 |  | NORTHWEST | ENID | 4414:HENNESSEY | HENNESSEY_1421 | 441421 | 2020-01-02 09:52 | 2020-01-02 11:48 | 115.62 | 8 | 0 | 925.0121 | 4 | DETERIORATION | 12 | POLE | HENNESSEY | 220 S CHEYENNE | CMI_PLANNED | YES | NO | NO | 859723 | 53477 | 37553 | 1952 | 586 | 0.0010759 | 9.3053e-06 | 115.6265 | 1 | 0 | Load | 5111 | Load | TranOHDeltaSplitBank | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000324 | PD-01022020-00163 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_723 | 870723 | 2020-01-02 09:56 | 2020-01-02 11:02 | 65.55 | 1 | 1 | 65.55 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 1826 E.LINDSEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 158927 | 56894 | 11825 | 2042 | 7.6245e-05 | 1.1632e-06 | 65.55 | 1 | 310 | Customer | 36033 | Load | Tran1phPad | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000322 |  | ARKANSAS | POTEAU | 3608:MULDROW | MULDROW 24 | 360824 | 2020-01-02 09:57 | 2020-01-02 13:13 | 196.65 | 1 | 0 | 196.5986 | 4 | DETERIORATION | 12 | POLE | 0 | .6M N 64 ON COTTONWOOD RD | CMI_PLANNED | YES | NO | NO | 859723 | 82085 | 13444 | 2267 | 521 | 0.00022868 | 1.1632e-06 | 196.5986 | 1 | 0 | Load | 16337 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000330 |  | SOUTHERN | HEALDTON | 5309:POOLEVILLE | POOLEVILLE_927 | 530927 | 2020-01-02 10:05 | 2020-01-02 11:01 | 56.15 | 2 | 0 | 102.4 | 4 | DETERIORATION | 2 | TRANSFORMER OH | 0 | 7-76 2S 4E SS | CMI_PLANNED | YES | NO | NO | 859723 | 77499 | 6785 | 401 | 142 | 0.00011911 | 2.3263e-06 | 51.2 | 1 | 0 | Load | 24982 | Load | Tran3phWye | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000331 | PD-01022020-00170 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5121 | 815121 | 2020-01-02 10:09 | 2020-01-02 11:35 | 86.02 | 1 | 1 | 86.0167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2640 SW.83 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 158927 | 102033 | 13933 | 1998 | 0.00010005 | 1.1632e-06 | 86.0167 | 1 | 310 | Customer | 17815 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000336 |  | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3224 | 813224 | 2020-01-02 10:15 | 2020-01-02 12:18 | 123.1 | 2 | 4 | 233.7 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 5700 S WESTERN AVE | CMI_PLANNED | YES | NO | NO | 859723 | 158927 | 102033 | 7592 | 1581 | 0.00027183 | 2.3263e-06 | 116.85 | 1 | 310 | Secondary | 11247 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000338 | PD-01022020-00183 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2024 | 862024 | 2020-01-02 10:22 | 2020-01-02 11:28 | 65.78 | 1 | 1 | 65.7833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 218 SW.32 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 158927 | 102033 | 4736 | 770 | 7.6517e-05 | 1.1632e-06 | 65.7833 | 1 | 311 | Customer | 13746 | Load | TranOpenDelta | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000337 | PD-01022020-00182 | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_629 | 730629 | 2020-01-02 10:23 | 2020-01-02 11:41 | 78.07 | 1 | 1 | 78.0667 | 12 | POOR CONNECTION | 50 | CONNECTOR | SEMINOLE | 3MI NW ON 3 | CMI_NORMAL | NO | NO | NO | 859723 | 114172 | 13577 | 4056 | 567 | 9.0804e-05 | 1.1632e-06 | 78.0667 | 1 | 320 | Customer | 8769 | Load | Tran1phOH | DELBERT HISAW | 405-683-1721 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000346 | PD-01022020-00192 | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2523 | 512523 | 2020-01-02 10:26 | 2020-01-02 11:24 | 57.5 | 1 | 2 | 55.2667 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | LONE GROVE | GOOSEBERRY AND HWY.70 | CMI_NORMAL | NO | NO | NO | 859723 | 77499 | 23559 | 3299 | 958 | 6.4284e-05 | 1.1632e-06 | 55.2667 | 1 | 310 | Customer | 29062 | Load | Tran1phOH | RANDAL G CALLAWAY | 580-220-8449 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000351 | PD-01022020-00199 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_861 | 830861 | 2020-01-02 10:46 | 2020-01-02 13:01 | 134.95 | 1 | 1 | 7.6738 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | EDMOND | 6077 WHITETAIL DR. | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859723 | 167942 | 148151 | 19334 | 3920 | 8.9259e-06 | 1.1632e-06 | 7.6738 | 1 | 310 | Customer | 198448 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000353 | PD-01022020-00215 | METRO EAST | CHANDLER | 7117:JACKTOWN | JACKTOWN_1742 | 711742 | 2020-01-02 10:48 | 2020-01-02 13:03 | 135.12 | 3 | 3 | 384.5 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MEEKER | 1/2ME-HWY 18,SS HWY 62 | CMI_NORMAL | NO | NO | NO | 859723 | 114172 | 7448 | 1010 | 827 | 0.00044724 | 3.4895e-06 | 128.1667 | 1 | 310 | Load | 23200 | Load | TranOpenDelta | SCOTT C PERRY | 405-258-6044 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000352 | PD-01022020-00205 | SOUTHERN | MADILL | 5408:CANEY CREEK | CANEY_CREEK_831 | 540831 | 2020-01-02 10:53 | 2020-01-02 12:56 | 123.25 | 1 | 1 | 123.25 | 13 | PREMATURE FAILURE | 15 | METER - SECONDARY | KINGSTON | LITTLES TLR PARK | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859723 | 77499 | 7198 | 1052 | 628 | 0.00014336 | 1.1632e-06 | 123.25 | 1 | 310 | Customer | 16733 | Load | Tran1phPad | DAVID TAYLOR | 580-574-4517 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000355 | PD-01022020-00212 | METRO SOUTH | SOUTH | 5607:ROSEDALE TAP | ROSEDALE_TAP_724 | 560724 | 2020-01-02 11:02 | 2020-01-02 12:45 | 103.45 | 1 | 1 | 103.45 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ROSEDALE | 1/4S OF RSDL ON 59 2 MI EAST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 158927 | 56894 | 986 | 339 | 0.00012033 | 1.1632e-06 | 103.45 | 1 | 311 | Load | 24003 | Load | Tran3phWye | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000357 |  | SOUTHERN | HEALDTON | 5309:POOLEVILLE | POOLEVILLE_927 | 530927 | 2020-01-02 11:03 | 2020-01-02 11:46 | 43.08 | 1 | 0 | 36.5833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | 0 | 2643 RANCH RD | CMI_PLANNED | YES | NO | NO | 859723 | 77499 | 6785 | 401 | 142 | 4.2552e-05 | 1.1632e-06 | 36.5833 | 1 | 0 | Load | 336119 | Load | Tran3phWye | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000361 | PD-01022020-00226 | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6224 | 866224 | 2020-01-02 11:05 | 2020-01-02 12:33 | 88.1 | 1 | 1 | 85.2167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MIDWEST CITY | 524 S.TEXAS | CMI_NORMAL | NO | NO | NO | 859723 | 114172 | 71087 | 7196 | 1778 | 9.9121e-05 | 1.1632e-06 | 85.2167 | 1 | 310 | Load | 57120 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000364 |  | METRO NORTH | NORTH | 8430:REMINGTON PARK | REMINGTON_PARK_3022 | 843022 | 2020-01-02 11:10 | 2020-01-02 12:03 | 52.98 | 2 | 0 | 105.9784 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 7105 N.KELLEY | CMI_PLANNED | YES | NO | NO | 859723 | 167942 | 148151 | 845 | 669 | 0.00012327 | 2.3263e-06 | 52.9892 | 1 | 0 | Load | 24015 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000369 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4031 | 834031 | 2020-01-02 11:13 | 2020-01-02 11:20 | 6.85 | 1 | 1 | 6.85 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | J L DENNIS + 109TH PLACE-LT 17 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 128532 | 115810 | 10838 | 1640 | 7.9677e-06 | 1.1632e-06 | 6.85 | 1 | 310 | Customer | 33642 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000368 | PD-01022020-00232 | SOUTHERN | ARDMORE | 5106:HARRIS ST | HARRIS_ST_622 | 510622 | 2020-01-02 11:14 | 2020-01-02 12:36 | 82.32 | 1 | 1 | 80.7333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ARDMORE | MT WASH RD/MESA RD,.1E,.1S | CMI_NORMAL | NO | NO | NO | 859723 | 77499 | 23559 | 2066 | 1106 | 9.3906e-05 | 1.1632e-06 | 80.7333 | 1 | 310 | Load | 28352 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000382 | PD-01022020-00265 | METRO EAST | EAST | 8542:RENO | RENO_4229 | 854229 | 2020-01-02 11:38 | 2020-01-02 13:34 | 115.87 | 1 | 1 | 78.7833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DEL CITY | 4625 TINKER EX | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 114172 | 71087 | 5208 | 1343 | 9.1638e-05 | 1.1632e-06 | 78.7833 | 1 | 310 | Customer | 40588 | Load | Tran1phPad | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2022
J2001.000381 | PD-01022020-00266 | METRO EAST | SEMINOLE | 7312:JUMPER CREEK | JUMPER_CREEK_1225 | 731225 | 2020-01-02 11:40 | 2020-01-02 14:18 | 158.48 | 1 | 1 | 158.4833 | 22 | WIND | 17 | JUMPER | KONAWA | 1MS VAMOOSA, 3/4MW, 4 SPAN N | CMI_NORMAL | NO | NO | NO | 859723 | 114172 | 13577 | 1214 | 331 | 0.00018434 | 1.1632e-06 | 158.4833 | 1 | 310 | Load | 16098 | Load | TranOpenDelta | DELBERT HISAW | 405-683-1721 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000384 | PD-01022020-00262 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5125 | 815125 | 2020-01-02 11:41 | 2020-01-02 12:56 | 74.55 | 8 | 8 | 577.6 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1009 SW.67 | CMI_NORMAL | NO | NO | NO | 859723 | 158927 | 102033 | 13933 | 1430 | 0.00067184 | 9.3053e-06 | 72.2 | 1 | 310 | Load | 17509 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000389 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_723 | 870723 | 2020-01-02 12:00 | 2020-01-02 12:08 | 8.08 | 1 | 1 | 8.0833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 2647 Classen Blvd. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 158927 | 56894 | 11825 | 2042 | 9.4023e-06 | 1.1632e-06 | 8.0833 | 1 | 310 | Customer | 376281 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000393 | PD-01022020-00273 | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3821 | 913821 | 2020-01-02 12:07 | 2020-01-02 12:59 | 51.9 | 1 | 1 | 51.9 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 919 ROGERS AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 82085 | 61114 | 2925 | 209 | 6.0368e-05 | 1.1632e-06 | 51.9 | 1 | 310 | Customer | 5485 | Load | Tran3phWye | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-02 | 2020 |  | Ark - Series 2
J2001.000392 |  | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1421 | 311421 | 2020-01-02 12:08 | 2020-01-02 12:25 | 17.23 | 1 | 1 | 17.2333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 207 N.33 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 73889 | 33203 | 4558 | 1101 | 2.0045e-05 | 1.1632e-06 | 17.2333 | 1 | 310 | Customer | 5533 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000394 |  | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9862 | 839862 | 2020-01-02 12:10 | 2020-01-02 12:17 | 7.3 | 1 | 1 | 7.3 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | LOT 26 BLK 54 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167942 | 148151 | 10648 | 2315 | 8.4911e-06 | 1.1632e-06 | 7.3 | 1 | 310 | Customer | 226459 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000396 | PD-01022020-00272 | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_623 | 880623 | 2020-01-02 12:12 | 2020-01-02 13:39 | 86.6 | 1 | 1 | 86.6 | 23 | CUSTOMER EQUIPMENT | 15 | METER - SECONDARY | GUTHRIE | 1MS HY33 1/4MWESTRN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167942 | 19791 | 5154 | 1412 | 0.00010073 | 1.1632e-06 | 86.6 | 1 | 310 | Customer | 51503 | Load | Tran1phOH | KELLEY D WATSON | 405-763-8148 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000398 |  | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6522 | 836522 | 2020-01-02 12:18 | 2020-01-02 12:23 | 5.83 | 1 | 1 | 5.8333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6720 W.WILSHIRE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 128532 | 115810 | 7416 | 1859 | 6.7851e-06 | 1.1632e-06 | 5.8333 | 1 | 310 | Customer | 38967 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000399 | PD-01022020-00284 | NORTHEAST | SAPULPA | 3220:KELLYVILLE | KELLYVILLE_2029 | 322029 | 2020-01-02 12:19 | 2020-01-02 14:31 | 131.65 | 1 | 1 | 128.0177 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SAPULPA | 3 W ON HEYBURN + 1/4 N + 1/8E | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 73889 | 40686 | 2550 | 970 | 0.00014891 | 1.1632e-06 | 128.0177 | 1 | 320 | Load | 43894 | Load | Tran1phOH | GREGORY R HOOVER | 918-261-6803 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2022
J2001.000400 | PD-01022020-00276 | METRO NORTH | NORTH | 8434:DEEP FORK | STONEWALL_7422 | 847422 | 2020-01-02 12:20 | 2020-01-02 12:47 | 27.45 | 1 | 1 | 27.45 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | ON 29TH,100 W. OF STILES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167942 | 148151 | 1224 | 1211 | 3.1929e-05 | 1.1632e-06 | 27.45 | 1 | 310 | Customer | 101346 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2022
J2001.000405 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2231 | 852231 | 2020-01-02 12:28 | 2020-01-02 18:32 | 363.97 | 1 | 2 | 25.4355 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 16070 Chery Stone Rd | CMI_PLANNED | YES | NO | NO | 859723 | 114172 | 71087 | 11611 | 1436 | 2.9586e-05 | 1.1632e-06 | 25.4355 | 1 | 310 | Load | 77190 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000409 | PD-01022020-00294 | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_522 | 560522 | 2020-01-02 12:35 | 2020-01-02 14:03 | 88.38 | 1 | 1 | 76.5 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | PAULS VALLEY | 705 N CHICKASAW PAULS VALLEY | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859723 | 77499 | 6194 | 2450 | 825 | 8.8982e-05 | 1.1632e-06 | 76.5 | 1 | 310 | Customer | 9333 | Load | Tran1phOH | BRUCE E BEAM | 405-626-0490 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | OK - 2022
J2001.000410 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6324 | 816324 | 2020-01-02 12:40 | 2020-01-02 13:43 | 63.03 | 7 | 8 | 434.5149 | 4 | DETERIORATION | 2 | TRANSFORMER OH | MOORE | 632 SW.1 PL | CMI_PLANNED | YES | NO | NO | 859723 | 158927 | 102033 | 11809 | 2048 | 0.00050541 | 8.1422e-06 | 62.0735 | 1 | 310 | Load | 17194 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000411 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_723 | 870723 | 2020-01-02 12:41 | 2020-01-02 12:58 | 16.6 | 1 | 1 | 16.6 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 2647 Classen Blvd. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 158927 | 56894 | 11825 | 2042 | 1.9309e-05 | 1.1632e-06 | 16.6 | 1 | 310 | Customer | 376281 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000417 |  | METRO EAST | EAST | 8542:RENO | RENO_4229 | 854229 | 2020-01-02 12:48 | 2020-01-02 13:23 | 34.73 | 1 | 1 | 8.7833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DEL CITY | 4625 TINKER EX | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 114172 | 71087 | 5208 | 1343 | 1.0216e-05 | 1.1632e-06 | 8.7833 | 1 | 310 | Customer | 40588 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2022
J2001.000416 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5138 | 815138 | 2020-01-02 12:49 | 2020-01-02 13:11 | 21.28 | 1 | 1 | 21.2833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1332 SW.74 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 158927 | 102033 | 13933 | 1416 | 2.4756e-05 | 1.1632e-06 | 21.2833 | 1 | 310 | Customer | 31484 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000418 |  | SOUTHERN | MADILL | 5409:LITTLE CITY | LITTLE CITY 21 | 540921 | 2020-01-02 12:51 | 2020-01-02 13:02 | 10.75 | 1 | 1 | 10.75 | 1 | CANCELLED | 57 | CANCELLED | BRIDGEVIEW | 6.5E .6S GLASSES SUB ES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 77499 | 7198 | 610 | 591 | 1.2504e-05 | 1.1632e-06 | 10.75 | 1 | 310 | Load | 31992 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000419 | PD-01022020-00303 | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5231 | 835231 | 2020-01-02 12:53 | 2020-01-02 14:05 | 72.08 | 1 | 1 | 53.6833 | 27 | TREE:NON PREVENTABLE | 9 | SPLICE - OH | THE VILLAGE | 3029 CHAUCER DR | CMI_NORMAL | NO | NO | NO | 859723 | 167942 | 148151 | 6516 | 638 | 6.2443e-05 | 1.1632e-06 | 53.6833 | 1 | 310 | Customer | 18523 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000420 |  | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_429 | 580429 | 2020-01-02 12:53 | 2020-01-02 13:34 | 41.05 | 7 | 5 | 252.9333 | 4 | DETERIORATION | 12 | POLE | ADA | 1621 SCENIC DR | CMI_PLANNED | YES | NO | NO | 859723 | 77499 | 11496 | 3410 | 1343 | 0.0002942 | 8.1422e-06 | 36.1333 | 1 | 308 | Load | 1473 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000421 |  | NORTHEAST | SAPULPA | 3218:BEGGS | BEGGS_1829 | 321829 | 2020-01-02 13:26 | 2020-01-02 14:54 | 87.9 | 35 | 2 | 383.25 | 4 | DETERIORATION | 28 | CROSSARM | MOUNDS | 3/8 SO OF MOUNDS | CMI_NORMAL | NO | NO | NO | 859723 | 73889 | 40686 | 1830 | 895 | 0.00044578 | 4.0711e-05 | 10.95 | 1 | 310 | Mainline | 60274 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2020
J2001.000438 | PD-01022020-00371 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3631 | 833631 | 2020-01-02 13:57 | 2020-01-02 14:53 | 56.37 | 9 | 8 | 157.2 | 12 | POOR CONNECTION | 50 | CONNECTOR | THE VILLAGE | 2728 PLYMOUTH LN | CMI_NORMAL | NO | NO | NO | 859723 | 167942 | 148151 | 8780 | 1333 | 0.00018285 | 1.0468e-05 | 17.4667 | 1 | 310 | Load | 27003 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000435 |  | METRO NORTH | NORTH | 8430:REMINGTON PARK | REMINGTON_PARK_3024 | 843024 | 2020-01-02 13:59 | 2020-01-02 15:18 | 79 | 1 | 0 | 83.55 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | NE 49 AND EASTERN | CMI_PLANNED | YES | NO | NO | 859723 | 167942 | 148151 | 845 | 176 | 9.7182e-05 | 1.1632e-06 | 83.55 | 1 | 0 | Load | 2183 | Load | Tran3phWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000441 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4529 | 824529 | 2020-01-02 14:12 | 2020-01-02 14:12 | 0 | 257 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 202 N COUNCIL RD | CMI_MOMENTARY | YES | NO | NO | 859723 | 128532 | 115810 | 3401 | 257 | 0 | 0.00029893 | 0 | 1 | 0 | Feeder | COUNCIL_4529 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000442 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-02 14:14 | 2020-01-02 16:56 | 162.15 | 4 | 4 | 638.3667 | 4 | DETERIORATION | 12 | POLE | COAL HILL | COAL HILL AR | CMI_PLANNED | YES | NO | NO | 859723 | 82085 | 7527 | 1501 | 1198 | 0.00074253 | 4.6527e-06 | 159.5917 | 1 | 310 | Load | 12230 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-02 | 2020 |  | Ark - Series 2
J2001.000445 | PD-01022020-00380 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3670 | 853670 | 2020-01-02 14:19 | 2020-01-02 15:05 | 46.42 | 1 | 1 | 9.3971 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 213 N CENTRAL AVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167942 | 148151 | 5913 | 1560 | 1.093e-05 | 1.1632e-06 | 9.3971 | 1 | 310 | Customer | 206968 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2022
J2001.000448 | PD-01022020-00387 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3922 | 833922 | 2020-01-02 14:22 | 2020-01-02 15:54 | 91.75 | 1 | 1 | 81.8333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1620 FW OF MERIDIAN ON NW 50TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167942 | 148151 | 7845 | 1631 | 9.5186e-05 | 1.1632e-06 | 81.8333 | 1 | 310 | Load | 76737 | Load | Tran1phOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2022
J2001.000447 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2231 | 852231 | 2020-01-02 14:23 | 2020-01-02 18:32 | 248.63 | 1 | 1 | 10.819 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | lot btwn lot 3 & 4 on SE 41st st | CMI_PLANNED | YES | NO | NO | 859723 | 114172 | 71087 | 11611 | 1436 | 1.2584e-05 | 1.1632e-06 | 10.819 | 1 | 310 | Customer | 227800 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000449 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4529 | 824529 | 2020-01-02 14:25 | 2020-01-02 14:25 | 0 | 257 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 202 N COUNCIL RD | CMI_MOMENTARY | YES | NO | NO | 859723 | 128532 | 115810 | 3401 | 257 | 0 | 0.00029893 | 0 | 1 | 0 | Feeder | COUNCIL_4529 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000450 |  | SOUTHERN | ADA | 5813:BYNG SPA | BYNG_SPA_1322 | 581322 | 2020-01-02 14:27 | 2020-01-02 15:40 | 73.52 | 4 | 3 | 252.0667 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | BYNG | W WISER GRO | CMI_PLANNED | YES | NO | NO | 859723 | 77499 | 11496 | 546 | 546 | 0.0002932 | 4.6527e-06 | 63.0167 | 1 | 308 | Load | 19740 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000455 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4529 | 824529 | 2020-01-02 14:32 | 2020-01-02 14:36 | 3.87 | 1 | 1 | 3.8667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 11 N COUNCIL | CMI_MOMENTARY | YES | NO | NO | 859723 | 128532 | 115810 | 3401 | 257 | 4.4976e-06 | 1.1632e-06 | 3.8667 | 1 | 310 | Load | 76921 | Load | Tran3phWye | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000457 | PD-01022020-00402 | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_521 | 890521 | 2020-01-02 14:34 | 2020-01-02 15:54 | 80.48 | 1 | 1 | 80.4833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | EL RENO | 505 S.FRANCES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 128532 | 12722 | 6933 | 2210 | 9.3615e-05 | 1.1632e-06 | 80.4833 | 1 | 310 | Customer | 38353 | Load | Tran1phOH | MICHAEL T MAHEN | 405-210-6029 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000458 | PD-01022020-00440 | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4529 | 824529 | 2020-01-02 14:34 | 2020-01-02 15:52 | 78.32 | 1 | 1 | 78.3167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 8205 RENO | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 128532 | 115810 | 3401 | 257 | 9.1095e-05 | 1.1632e-06 | 78.3167 | 1 | 320 | Load | 73036 | Load | Tran3phWye | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000456 | PD-01022020-00406 | METRO EAST | SHAWNEE | 7407:REMINGTON | REMINGTON 21 | 740721 | 2020-01-02 14:34 | 2020-01-02 15:30 | 56.25 | 1 | 1 | 49.6333 | 12 | POOR CONNECTION | 50 | CONNECTOR | SHAWNEE | 408 SO LINDELL | CMI_NORMAL | NO | NO | NO | 859723 | 114172 | 22060 | 3658 | 2014 | 5.7732e-05 | 1.1632e-06 | 49.6333 | 1 | 310 | Customer | 6097 | Load | Tran1phOH | BRYAN K TATUM | 405-659-0746 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000463 |  | METRO SOUTH | SOUTH | 8722:MILLENNIUM | MILLENNIUM_2231 | 872231 | 2020-01-02 14:38 | 2020-01-02 14:54 | 15.55 | 1 | 1 | 15.55 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | SUMMIT CREST LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 158927 | 56894 | 4204 | 2053 | 1.8087e-05 | 1.1632e-06 | 15.55 | 1 | 310 | Customer | 242092 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000464 | PD-01022020-00423 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5022 | 865022 | 2020-01-02 14:43 | 2020-01-02 17:02 | 138.77 | 1 | 2 | 138.7667 | 12 | POOR CONNECTION | 50 | CONNECTOR | MIDWEST CITY | 524 E.STEED DR | CMI_NORMAL | NO | NO | NO | 859723 | 114172 | 71087 | 8623 | 1660 | 0.00016141 | 1.1632e-06 | 138.7667 | 1 | 320 | Customer | 8385 | Load | Tran1phOH | THOMAS E COLE | 405-623-9338 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2022
J2001.000471 |  | METRO SOUTH | SOUTH | 8722:MILLENNIUM | MILLENNIUM_2231 | 872231 | 2020-01-02 14:45 | 2020-01-02 15:07 | 21.57 | 1 | 1 | 21.5667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | lot 8 blk 6 section 6 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 158927 | 56894 | 4204 | 2053 | 2.5086e-05 | 1.1632e-06 | 21.5667 | 1 | 310 | Customer | 223721 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000472 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3631 | 833631 | 2020-01-02 14:47 | 2020-01-02 14:58 | 11.27 | 1 | 1 | 11.2667 | 1 | CANCELLED | 57 | CANCELLED | THE VILLAGE | 2720 PLYMOUTH RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167942 | 148151 | 8780 | 1333 | 1.3105e-05 | 1.1632e-06 | 11.2667 | 1 | 310 | Customer | 12817 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000474 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-02 14:59 | 2020-01-02 15:07 | 8.78 | 2 | 0 | 17.5832 | 4 | DETERIORATION | 47 | ARRESTOR OH | COAL HILL | HWY 64, 1/4M W-COAL HILL | CMI_PLANNED | YES | NO | NO | 859723 | 82085 | 7527 | 1501 | 1198 | 2.0452e-05 | 2.3263e-06 | 8.7916 | 1 | 0 | Load | 4766 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-02 | 2020 |  | Ark - Series 2
J2001.000480 | PD-01022020-00454 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3224 | 813224 | 2020-01-02 15:18 | 2020-01-02 17:05 | 107.18 | 9 | 7 | 823.95 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1217 SW.58 | CMI_NORMAL | NO | NO | NO | 859723 | 158927 | 102033 | 7592 | 1581 | 0.00095839 | 1.0468e-05 | 91.55 | 1 | 310 | Load | 5216 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000481 | PD-01022020-00445 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3926 | 833926 | 2020-01-02 15:20 | 2020-01-02 18:50 | 210 | 9 | 11 | 1870.05 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 3520 NW.66 | CMI_NORMAL | NO | NO | NO | 859723 | 167942 | 148151 | 7845 | 1360 | 0.0021752 | 1.0468e-05 | 207.7833 | 1 | 310 | Load | 21879 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2022
J2001.000486 | PD-01022020-00468 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_771 | 870771 | 2020-01-02 15:33 | 2020-01-02 18:21 | 167.95 | 1 | 1 | 167.95 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | NORMAN | 4.5 ME OLD HWY 9 | CMI_NORMAL | NO | NO | NO | 859723 | 158927 | 56894 | 11825 | 1813 | 0.00019535 | 1.1632e-06 | 167.95 | 1 | 310 | Load | 48295 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000488 | PD-01022020-00463 | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-01-02 15:36 | 2020-01-02 16:24 | 47.55 | 1090 | 448 | 125840.5 | 3 | DAMAGED BY PUBLIC | 12 | POLE | ADA | 1806 A ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 77499 | 11496 | 2516 | 1090 | 0.14637 | 0.0012679 | 115.45 | 1 | 310 | Feeder | VALLEY_VIEW_623 | Recloser | 0 | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000493 |  | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_622 | 580622 | 2020-01-02 15:40 | 2020-01-02 18:11 | 150.62 | 3 | 2 | 335 | 0 | BREAKER | 55 | SCADA - CIRCUIT TRIP | ADA | 300 E MONTE VISTA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 77499 | 11496 | 2516 | 779 | 0.00038966 | 3.4895e-06 | 111.6667 | 1 | 310 | Load | 312410 | Load | Tran3phWye | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000496 |  | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-01-02 15:42 | 2020-01-02 17:46 | 123.5 | 1 | 1 | 109.3667 | 0 | BREAKER | 55 | SCADA - CIRCUIT TRIP | ADA | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 0 | 0 | 0 | 0 | 0.00012721 | 1.1632e-06 | 109.3667 | 1 | 310 | Customer |  | 0 | 0 | [6 empty] | 06/10/2020 note from burchamc. Reference J2001.000496 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Emailed Brent Miller with blank transformer and circuit #'s. Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000497 |  | METRO EAST | CHANDLER | 7117:JACKTOWN | JACKTOWN_1742 | 711742 | 2020-01-02 15:43 | 2020-01-02 16:01 | 18.47 | 1 | 1 | 18.4667 | 1 | CANCELLED | 57 | CANCELLED | MEEKER | 1.5MW MEEKER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 114172 | 7448 | 1010 | 827 | 2.148e-05 | 1.1632e-06 | 18.4667 | 1 | 310 | Customer | 885 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000499 |  | SOUTHERN | DURANT | 5505:DURANT | DURANT 21 | 550521 | 2020-01-02 15:43 | 2020-01-02 16:08 | 25.65 | 1 | 1 | 25.65 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DURANT | 424 N.3RD ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 77499 | 15461 | 1319 | 373 | 2.9835e-05 | 1.1632e-06 | 25.65 | 1 | 310 | Customer | 18945 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000500 |  | METRO SOUTH | SOUTH | 8722:MILLENNIUM | MILLENNIUM_2231 | 872231 | 2020-01-02 15:45 | 2020-01-02 15:51 | 5.53 | 1 | 1 | 5.5333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | LOT 24, BLK. 2 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 158927 | 56894 | 4204 | 2053 | 6.4362e-06 | 1.1632e-06 | 5.5333 | 1 | 310 | Customer | 185198 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000502 |  | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1623 | 581623 | 2020-01-02 15:46 | 2020-01-02 17:44 | 117.2 | 1 | 1 | 117.2 | 0 | BREAKER | 55 | SCADA - CIRCUIT TRIP | ADA | 715 W.19 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 77499 | 11496 | 3453 | 1649 | 0.00013632 | 1.1632e-06 | 117.2 | 1 | 310 | Customer | 12374 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000501 |  | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1621 | 581621 | 2020-01-02 15:48 | 2020-01-02 17:44 | 116.62 | 1 | 1 | 104.0333 | 3 | DAMAGED BY PUBLIC | 12 | POLE | ADA | 128 W.5 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 77499 | 11496 | 3453 | 1804 | 0.00012101 | 1.1632e-06 | 104.0333 | 1 | 310 | Customer | 5363 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000506 | PD-01022020-00495 | SOUTHERN | HEALDTON | 5306:COUNTY LINE | COUNTY LINE 21 | 530621 | 2020-01-02 15:58 | 2020-01-02 18:03 | 125.17 | 1 | 1 | 125.1667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FOX | 7/76 3S .3E .1S | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 77499 | 6785 | 755 | 342 | 0.00014559 | 1.1632e-06 | 125.1667 | 1 | 310 | Customer | 7179 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000509 |  | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3221 | 813221 | 2020-01-02 16:08 | 2020-01-02 16:17 | 9.28 | 1 | 1 | 9.2833 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1416 RANCHO DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 158927 | 102033 | 7592 | 2073 | 1.0798e-05 | 1.1632e-06 | 9.2833 | 1 | 310 | Customer | 5836 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000511 |  | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_622 | 580622 | 2020-01-02 16:09 | 2020-01-02 17:54 | 105.15 | 1 | 1 | 105.15 | 0 | BREAKER | 55 | SCADA - CIRCUIT TRIP | ADA | 908 N.CNTRY-CLB RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 77499 | 11496 | 2516 | 779 | 0.00012231 | 1.1632e-06 | 105.15 | 1 | 310 | Customer | 20875 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000513 | PD-01022020-00493 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3922 | 833922 | 2020-01-02 16:12 | 2020-01-02 19:14 | 182.32 | 1 | 1 | 181.4 | 4 | DETERIORATION | 50 | CONNECTOR | WARR ACRES | 6036 NW.49 | CMI_NORMAL | NO | NO | NO | 859723 | 167942 | 148151 | 7845 | 1631 | 0.000211 | 1.1632e-06 | 181.4 | 1 | 320 | Customer | 9458 | Load | Tran1phOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2022
J2001.000514 |  | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_621 | 870621 | 2020-01-02 16:18 | 2020-01-02 16:48 | 30.15 | 172 | 64 | 5020.7975 | 28 | OTHER (DESCRIBE) | 37 | CONDUCTOR PRIMARY - OH | NORMAN | W-SHERRY + MAIN | CMI_PLANNED | YES | NO | NO | 859723 | 158927 | 56894 | 7362 | 925 | 0.00584 | 0.00020006 | 29.1907 | 1 | 310 | Mainline | 22327 | Fuse | FuseOH | OGE | [6 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000517 |  | NORTHWEST | ENID | 4107:CLEVELAND AVE | CLEVELAND_AVE_722 | 410722 | 2020-01-02 16:27 | 2020-01-02 17:02 | 34.92 | 1 | 1 | 34.9167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ENID | 412 S POLK--ENID | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 53477 | 37553 | 4457 | 1377 | 4.0614e-05 | 1.1632e-06 | 34.9167 | 1 | 310 | Customer | 6909 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000521 |  | METRO EAST | SEMINOLE | 7321:LETHA | LETHA_2122 | 732122 | 2020-01-02 16:46 | 2020-01-02 17:01 | 14.62 | 1 | 1 | 14.6167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SEMINOLE | BLK1 LOT 4 HIDDENHL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 114172 | 13577 | 1259 | 833 | 1.7002e-05 | 1.1632e-06 | 14.6167 | 1 | 310 | Customer | 17671 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000523 | PD-01022020-00525 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3926 | 833926 | 2020-01-02 16:50 | 2020-01-02 18:34 | 103.6 | 4 | 7 | 82.0333 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 6908 N.ST-CLAIR | CMI_NORMAL | NO | NO | NO | 859723 | 167942 | 148151 | 7845 | 1360 | 9.5418e-05 | 4.6527e-06 | 20.5083 | 1 | 310 | Load | 24628 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2022
J2001.000527 | PD-01022020-00528 | METRO NORTH | NORTH | 8347:WILSHIRE | WILSHIRE_4722 | 834722 | 2020-01-02 17:04 | 2020-01-02 18:14 | 69.78 | 1 | 2 | 67.5333 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 3225 NW.68 | CMI_NORMAL | NO | NO | NO | 859723 | 167942 | 148151 | 4621 | 1588 | 7.8552e-05 | 1.1632e-06 | 67.5333 | 1 | 310 | Customer | 11114 | Load | TranOpenDelta | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2021
J2001.000530 | PD-01022020-00531 | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_521 | 530521 | 2020-01-02 17:14 | 2020-01-02 22:05 | 290.68 | 75 | 54 | 21632.5 | 4 | DETERIORATION | 27 | CUTOUT | ARDMORE | 8-TX 3N 8.1E | CMI_NORMAL | NO | NO | NO | 859723 | 77499 | 6785 | 2125 | 1257 | 0.025162 | 8.7237e-05 | 288.4333 | 1 | 310 | Mainline | 9094 | Fuse | FuseOH | ROBERT J BEARDSLEE | 580-618-2506 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | OK - 2020
J2001.000535 |  | NORTHEAST | MUSKOGEE | 3313:ILLINOIS RIVER | ILLINOIS_RIVER_1321 | 331321 | 2020-01-02 17:21 | 2020-01-02 17:41 | 20.28 | 1 | 1 | 20.2833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | GORE | 208 SW Railroad St. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 73889 | 33203 | 791 | 791 | 2.3593e-05 | 1.1632e-06 | 20.2833 | 1 | 310 | Load | 307596 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | OK - 2020
J2001.000546 |  | NORTHWEST | WOODWARD | 4608:WOODWARD DISTR | WOODWARD_DIST_846 | 460846 | 2020-01-02 17:23 | 2020-01-02 17:42 | 18.97 | 1 | 1 | 18.9667 | 17 | TRANSMISSION OPERATION | 55 | SCADA - CIRCUIT TRIP | SHARON | 2ND & INNIS AVE. | CMI_NORMAL | NO | NO | NO | 859723 | 53477 | 10409 | 1211 | 651 | 2.2061e-05 | 1.1632e-06 | 18.9667 | 1 | 308 | Customer | 10103 | Load | Tran1phOH | Transmission | [6 empty] | Equipment | N | TRANSMISSION | 138kV | 2020-01-02 | 2020 |  | OK - 2020
J2001.000545 |  | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1731 | 831731 | 2020-01-02 17:36 | 2020-01-02 17:36 | 0 | 2002 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 1327 NW 122ND ST | CMI_MOMENTARY | YES | NO | NO | 859723 | 167942 | 148151 | 6637 | 2016 | 0 | 0.0023287 | 0 | 1 | 0 | Feeder | SKYLINE_1731 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000551 | PD-01022020-00544 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2222 | 852222 | 2020-01-02 17:49 | 2020-01-02 19:42 | 113.03 | 2 | 2 | 201.8333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | HARRAH | 1023 HARRISON AV | CMI_NORMAL | NO | NO | NO | 859723 | 114172 | 71087 | 11611 | 2209 | 0.00023477 | 2.3263e-06 | 100.9167 | 1 | 310 | Load | 40417 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000554 | PD-01022020-00540 | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_622 | 580622 | 2020-01-02 18:03 | 2020-01-02 20:25 | 142.13 | 2 | 3 | 271.4833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ADA | 931 SUSAN AV | CMI_NORMAL | NO | NO | NO | 859723 | 77498 | 11496 | 2516 | 779 | 0.00031578 | 2.3263e-06 | 135.7417 | 1 | 310 | Secondary | 12357 | Load | Tran1phOH | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000559 | PD-01022020-00543 | SOUTHERN | HEALDTON | 5322:DUNDEE | DUNDEE 24 | 532224 | 2020-01-02 18:20 | 2020-01-02 21:00 | 160.17 | 1 | 1 | 160.1667 | 4 | DETERIORATION | 38 | CAPACITOR | HEALDTON | 8-TX 2.7W .4N (SHELL BLOCK 2) | CMI_NORMAL | NO | NO | NO | 859723 | 77498 | 6784 | 1011 | 4 | 0.0001863 | 1.1632e-06 | 160.1667 | 1 | 320 | Customer | 90203 | Load | 0 | CHRIS CLOSE | 405-238-0419 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000565 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9922 | 829922 | 2020-01-02 19:02 | 2020-01-02 19:13 | 10.68 | 1 | 1 | 10.6833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6628 NW.10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 128532 | 115810 | 9210 | 842 | 1.2426e-05 | 1.1632e-06 | 10.6833 | 1 | 310 | Customer | 34102 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000566 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5125 | 815125 | 2020-01-02 19:05 | 2020-01-02 19:59 | 53.63 | 99 | 69 | 4083.75 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | W,DOUGLAS AV/S,SW 66TH | CMI_PLANNED | YES | NO | NO | 859723 | 158927 | 102033 | 13933 | 1430 | 0.0047501 | 0.00011515 | 41.25 | 1 | 310 | Mainline | 9447 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000567 | PD-01022020-00548 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3222 | 813222 | 2020-01-02 19:30 | 2020-01-02 20:23 | 53.47 | 1 | 1 | 53.4667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 6100 S PENN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 158927 | 102033 | 7592 | 1482 | 6.2191e-05 | 1.1632e-06 | 53.4667 | 1 | 310 | Load | 20696 | Load | TranOpenDelta | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-02 | 2020 |  | #N/A
J2001.000569 |  | NORTHEAST | SAPULPA | 7614:KNIPE | KNIPE_1423 | 761423 | 2020-01-02 19:31 | 2020-01-02 19:49 | 17.82 | 1 | 1 | 17.8167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | PERKINS | 303 N W FIRST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 73889 | 40686 | 1824 | 790 | 2.0724e-05 | 1.1632e-06 | 17.8167 | 1 | 310 | Customer | 43305 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000570 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-01-02 19:36 | 2020-01-02 20:05 | 29.28 | 1 | 1 | 29.2833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 104 NW 25TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167942 | 148151 | 11091 | 2332 | 3.4061e-05 | 1.1632e-06 | 29.2833 | 1 | 320 | Customer | 12041 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2020
J2001.000573 | PD-01022020-00560 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7423 | 847423 | 2020-01-02 20:11 | 2020-01-02 21:09 | 58.25 | 1 | 2 | 58.25 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1427 NE.33 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167942 | 148151 | 6148 | 1284 | 6.7754e-05 | 1.1632e-06 | 58.25 | 1 | 310 | Customer | 13492 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2022
J2001.000578 | PD-01022020-00563 | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2224 | 882224 | 2020-01-02 20:53 | 2020-01-02 21:45 | 52.57 | 1 | 1 | 52.5667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | GUTHRIE | 14475 S. Coltrane | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167942 | 19791 | 5382 | 1846 | 6.1144e-05 | 1.1632e-06 | 52.5667 | 1 | 310 | Customer | 68327 | Load | Tran1phOH | JIM R HEIDEN | 405-501-1680 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | #N/A
J2001.000582 | PD-01022020-00564 | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-02 21:22 | 2020-01-02 22:05 | 43.17 | 1 | 1 | 43.1667 | 4 | DETERIORATION | 12 | POLE | MUSTANG | 1321 E Hwy 152 | CMI_NORMAL | NO | NO | NO | 859723 | 128532 | 115810 | 18198 | 4430 | 5.021e-05 | 1.1632e-06 | 43.1667 | 1 | 310 | Customer | 251861 | Load | Tran1phOH | BEAU S HUDSON | 405-306-8284 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-02 | 2020 |  | OK - 2022
J2001.000616 | PD-01032020-00008 | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2131 | 332131 | 2020-01-03 07:02 | 2020-01-03 12:15 | 312.98 | 2 | 3 | 611.85 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT GIBSON | LOT 5 BLK 2 PONDCREST FT. GIB | CMI_NORMAL | NO | NO | NO | 859723 | 73889 | 33203 | 3329 | 1172 | 0.00071168 | 2.3263e-06 | 305.925 | 1 | 310 | Load | 15296 | Load | Tran1phOH | GARY MICHAEL KNUPP | 918-577-8564 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-03 | 2020 |  | #N/A
J2001.000617 |  | NORTHWEST | ENID | 4157:NE ENID | NE_ENID_5723 | 415723 | 2020-01-03 07:24 | 2020-01-03 07:24 | 0 | 1305 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ENID | 4601 N 30TH | CMI_MOMENTARY | YES | NO | NO | 859723 | 53476 | 37552 | 1550 | 1305 | 0 | 0.0015179 | 0 | 1 | 0 | Feeder | NE ENID_5723 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000622 | PD-01032020-00056 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4821 | 824821 | 2020-01-03 07:50 | 2020-01-03 09:02 | 71.58 | 1 | 1 | 71.5833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2121 GENERAL PERSHING BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167942 | 148151 | 4181 | 240 | 8.3263e-05 | 1.1632e-06 | 71.5833 | 1 | 310 | Load | 202950 | Load | Tran3phPadWye | CONTRACTOR 2 DAVID ELLIOT INC | 918-362-1045 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2022
J2001.000624 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6122 | 836122 | 2020-01-03 08:05 | 2020-01-03 08:10 | 5.67 | 1 | 1 | 5.6667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1218 NW 19--OKC | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167942 | 148151 | 11091 | 968 | 6.5913e-06 | 1.1632e-06 | 5.6667 | 1 | 310 | Customer | 11319 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2022
J2001.000625 |  | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1723 | 861723 | 2020-01-03 08:07 | 2020-01-03 08:39 | 32.23 | 1 | 1 | 32.2333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DEL CITY | 4891 SE.44 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 114178 | 71087 | 6883 | 1546 | 3.7493e-05 | 1.1632e-06 | 32.2333 | 1 | 310 | Customer | 44984 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | #N/A
J2001.000628 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-01-03 08:14 | 2020-01-03 08:19 | 5.43 | 1 | 1 | 5.4333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1328 NW.21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167942 | 148151 | 11091 | 2035 | 6.3199e-06 | 1.1632e-06 | 5.4333 | 1 | 310 | Customer | 13944 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2021
J2001.000629 | PD-01032020-00084 | NORTHEAST | MUSKOGEE | 3326:JAMESVILLE | JAMESVILLE_2641 | 332641 | 2020-01-03 08:18 | 2020-01-03 10:42 | 143.5 | 1 | 1 | 143.5 | 12 | POOR CONNECTION | 50 | CONNECTOR | BOYNTON | BOYNTON OK | CMI_NORMAL | NO | NO | NO | 859723 | 73889 | 33203 | 1548 | 149 | 0.00016691 | 1.1632e-06 | 143.5 | 1 | 310 | Load | 2628 | Load | Tran1phOH | JOSH CHENEY | 918-619-3590 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | OK - 2020
J2001.000630 | PD-01032020-00082 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_526 | 510526 | 2020-01-03 08:20 | 2020-01-03 09:12 | 52.27 | 1 | 1 | 50.0667 | 4 | DETERIORATION | 50 | CONNECTOR | ARDMORE | 8 FREEMAN | CMI_NORMAL | NO | NO | NO | 859723 | 77498 | 23559 | 4768 | 1618 | 5.8236e-05 | 1.1632e-06 | 50.0667 | 1 | 320 | Customer | 7426 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | OK - 2020
J2001.000635 | PD-01032020-00097 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1922 | 851922 | 2020-01-03 08:35 | 2020-01-03 09:32 | 56.8 | 1 | 2 | 56.8 | 12 | POOR CONNECTION | 50 | CONNECTOR | MIDWEST CITY | 1105 HAZELWOOD DR | CMI_NORMAL | NO | NO | NO | 859723 | 114178 | 71087 | 12429 | 1794 | 6.6068e-05 | 1.1632e-06 | 56.8 | 1 | 310 | Customer | 13147 | Load | Tran1phOH | STEVEN CASKEY | 405-777-8855 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000636 |  | ARKANSAS | POTEAU | 3509:PANAMA | PANAMA 21 | 350921 | 2020-01-03 08:38 | 2020-01-03 08:38 | 0 | 315 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | 0 | 24068 OK-31 | CMI_MOMENTARY | YES | NO | NO | 859723 | 82084 | 13444 | 1383 | 817 | 0 | 0.0003664 | 0 | 1 | 0 | Mainline | 401900 | Recloser | Rec3phElectronic | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-03 | 2020 |  | #N/A
J2001.000637 |  | METRO WEST | WEST | 8222:CZECH HALL | CZECH_HALL_2224 | 822224 | 2020-01-03 08:40 | 2020-01-03 09:38 | 58.45 | 8 | 7 | 463.8667 | 4 | DETERIORATION | 1 | TRANSFORMER UG | YUKON | 0 | CMI_PLANNED | YES | NO | NO | 859723 | 128532 | 115810 | 8592 | 1332 | 0.00053955 | 9.3053e-06 | 57.9833 | 1 | 310 | Mainline | 58141-2 | Switch | SwitchDefault | Circuit Operation | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000638 | PD-01032020-00098 | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1729 | 831729 | 2020-01-03 08:41 | 2020-01-03 09:20 | 39.22 | 1 | 1 | 39.2167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 13600 BLK PLAZA TERR. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167942 | 148151 | 6637 | 647 | 4.5615e-05 | 1.1632e-06 | 39.2167 | 1 | 310 | Load | 128305 | Load | TranOH3phDelta | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000639 | PD-01032020-00099 | NORTHWEST | ENID | 4461:TURKEY CREEK | TURKEY_CREEK_6121 | 446121 | 2020-01-03 08:43 | 2020-01-03 10:04 | 81.27 | 1 | 1 | 81.2667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | HENNESSEY | ss of Loves, 1me, 1/2mn | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 53476 | 37552 | 436 | 416 | 9.4527e-05 | 1.1632e-06 | 81.2667 | 1 | 310 | Customer | 6401 | Load | Tran3phWye | STEVEN LORENZ | 580-822-3566 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | #N/A
J2001.000642 | PD-01032020-00105 | ARKANSAS | POTEAU | 3509:PANAMA | PANAMA 21 | 350921 | 2020-01-03 08:46 | 2020-01-03 10:52 | 126.17 | 1 | 1 | 123.25 | 28 | OTHER (DESCRIBE) | 23 | FUSE - PRIMARY | PANAMA | PANAMA, SOUTHEAST SIDE | CMI_NORMAL | NO | NO | NO | 859723 | 82084 | 13444 | 1383 | 817 | 0.00014336 | 1.1632e-06 | 123.25 | 1 | 310 | Customer | 2216 | Load | Tran1phOH | JOHN MEEH | 918-413-0959 | [5 empty] | Other | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | #N/A
J2001.000641 |  | METRO WEST | WEST | 8222:CZECH HALL | CZECH_HALL_2222 | 822222 | 2020-01-03 08:46 | 2020-01-03 10:14 | 88.07 | 9 | 9 | 649.5 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | 409 NORTON CI | CMI_PLANNED | YES | NO | NO | 859723 | 128532 | 115810 | 8592 | 2023 | 0.00075548 | 1.0468e-05 | 72.1667 | 1 | 310 | Load | 53127 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000652 |  | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3221 | 813221 | 2020-01-03 08:49 | 2020-01-03 10:19 | 90.23 | 6 | 5 | 410.8 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 932 SW.54 | CMI_PLANNED | YES | NO | NO | 859723 | 158927 | 102033 | 7592 | 2073 | 0.00047783 | 6.979e-06 | 68.4667 | 1 | 308 | Load | 52387 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | #N/A
J2001.000648 | PD-01032020-00142 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_629 | 870629 | 2020-01-03 08:50 | 2020-01-03 10:02 | 72.25 | 6 | 7 | 428.4 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | NORMAN | 1220 BARBOUR | CMI_NORMAL | NO | NO | NO | 859723 | 158927 | 56894 | 7362 | 1372 | 0.0004983 | 6.979e-06 | 71.4 | 1 | 310 | Load | 183723 | Load | Tran1phOH | MARK A PALMORE | 405-512-1933 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000645 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6322 | 816322 | 2020-01-03 08:54 | 2020-01-03 11:27 | 153.02 | 2 | 3 | 134.536 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 10700 S BROADWAY | CMI_PLANNED | YES | NO | NO | 859723 | 158927 | 102033 | 11809 | 1816 | 0.00015649 | 2.3263e-06 | 67.268 | 1 | 310 | Load | 17584 | Load | TranOpenDelta | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000650 |  | SOUTHERN | DURANT | 5504:BUTTERFIELD | BUTTERFIELD_429 | 550429 | 2020-01-03 08:55 | 2020-01-03 12:23 | 207.47 | 13 | 9 | 2678 | 4 | DETERIORATION | 12 | POLE | DURANT | 31O N 8TH | CMI_PLANNED | YES | NO | NO | 859723 | 77498 | 15461 | 3474 | 1267 | 0.003115 | 1.5121e-05 | 206 | 1 | 308 | Load | 889 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000660 |  | METRO WEST | WEST | 8222:CZECH HALL | CZECH_HALL_2222 | 822222 | 2020-01-03 09:20 | 2020-01-03 10:16 | 56.08 | 1 | 2 | 37.8833 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 417 RALPH CT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 128532 | 115810 | 8592 | 2023 | 4.4065e-05 | 1.1632e-06 | 37.8833 | 1 | 310 | Customer | 53126 | Load | Tran1phPad | Crew | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000659 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6922 | 846922 | 2020-01-03 09:20 | 2020-01-03 09:51 | 30.38 | 1 | 1 | 22.1667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 11721 N. BROADWAY EXT | CMI_PLANNED | YES | NO | NO | 859723 | 167942 | 148151 | 7711 | 1481 | 2.5783e-05 | 1.1632e-06 | 22.1667 | 1 | 308 | Load | 133176 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000662 | PD-01032020-00152 | METRO NORTH | NORTH | 8434:DEEP FORK | STONEWALL_7422 | 847422 | 2020-01-03 09:25 | 2020-01-03 11:25 | 120.23 | 4 | 6 | 438.8667 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 715 NE.18TH | CMI_NORMAL | NO | NO | NO | 859723 | 167942 | 148151 | 1224 | 1211 | 0.00051047 | 4.6527e-06 | 109.7167 | 1 | 310 | Secondary | 1567 | Load | TranOpenDelta | ROBERT HALL | 405-757-9640 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2022
J2001.000661 |  | METRO SOUTH | SOUTH CENTRAL | 8194:WESTMOORE | WESTMOORE_9431 | 819431 | 2020-01-03 09:25 | 2020-01-03 09:39 | 13.82 | 1 | 1 | 13.8167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | BRIARLAKE ESTATES LOT 4B | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 158927 | 102033 | 8096 | 1535 | 1.6071e-05 | 1.1632e-06 | 13.8167 | 1 | 320 | Customer | 71817 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000665 | PD-01032020-00166 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3621 | 853621 | 2020-01-03 09:29 | 2020-01-03 11:56 | 146.75 | 1 | 1 | 146.75 | 27 | TREE:NON PREVENTABLE | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 1708 MIRAMAR BL | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859723 | 167942 | 148151 | 5913 | 2162 | 0.00017069 | 1.1632e-06 | 146.75 | 1 | 310 | Customer | 181 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2022
J2001.000672 |  | METRO SOUTH | SOUTH | 8705:NORMAN | NORMAN 22 | 870522 | 2020-01-03 09:37 | 2020-01-03 13:23 | 226.43 | 1 | 1 | 106.55 | 4 | DETERIORATION | 1 | TRANSFORMER UG | NORMAN | 309 W.MAIN | CMI_PLANNED | YES | NO | NO | 859723 | 158927 | 56894 | 401 | 312 | 0.00012394 | 1.1632e-06 | 106.55 | 1 | 310 | Customer | 39498 | Load | Tran3phWye | Switching | [6 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-01-03 | 2020 |  | #N/A
J2001.000673 |  | METRO EAST | EAST | 8690:WILD MARY | WILD_MARY_9023 | 869023 | 2020-01-03 09:38 | 2020-01-03 11:25 | 107.52 | 7 | 5 | 332.5 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | S SUNNYLANE RD AND SE 99TH ST | CMI_PLANNED | YES | NO | NO | 859723 | 114178 | 71087 | 4019 | 2245 | 0.00038675 | 8.1422e-06 | 47.5 | 1 | 308 | Mainline | 36525 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000679 | PD-01032020-00182 | METRO NORTH | GUTHRIE | 8814:PINE STREET | PINE_STREET_1424 | 881424 | 2020-01-03 09:55 | 2020-01-03 14:00 | 244.72 | 1 | 1 | 244.7167 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | GUTHRIE | 25 MOCKINGBIRD LN | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859723 | 167942 | 19791 | 3096 | 1236 | 0.00028465 | 1.1632e-06 | 244.7167 | 1 | 320 | Customer | 43837 | Load | Tran1phPad | CONTRACTOR BHI51 DAVID ELLIOT INC | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000685 | PD-01032020-00189 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1922 | 851922 | 2020-01-03 09:57 | 2020-01-03 11:20 | 82.7 | 9 | 13 | 639.6 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | MIDWEST CITY | 211 SHADYBROOK PL | CMI_NORMAL | NO | NO | NO | 859723 | 114178 | 71087 | 12429 | 1794 | 0.00074396 | 1.0468e-05 | 71.0667 | 1 | 310 | Load | 40853 | Load | Tran1phOH | ADAM CLARK | 580-310-8924 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000682 | PD-01032020-00193 | NORTHEAST | SAPULPA | 7628:PIPELINE | PIPELINE 43 | 762843 | 2020-01-03 10:03 | 2020-01-03 11:26 | 82.9 | 1 | 1 | 70.75 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | CUSHING | 3S CUSHING ON LINWOOD | CMI_NORMAL | NO | NO | NO | 859723 | 73889 | 40686 | 50 | 30 | 8.2294e-05 | 1.1632e-06 | 70.75 | 1 | 320 | Load | 21507 | Load | Tran3phWye | BRAD WRIGHT | 918-629-1747 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | #N/A
J2001.000688 | PD-01032020-00194 | ARKANSAS | POTEAU | 3505:POTEAU | POTEAU_524 | 350524 | 2020-01-03 10:13 | 2020-01-03 11:44 | 90.8 | 1 | 1 | 90.8 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | POTEAU | 1/4MN 1/4ME TAYLORS | CMI_NORMAL | NO | NO | NO | 859723 | 82084 | 13444 | 2295 | 721 | 0.00010562 | 1.1632e-06 | 90.8 | 1 | 310 | Load | 15437 | Load | Tran1phOH | TOBY C MEAD | 918-658-5596 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | #N/A
J2001.000689 |  | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3224 | 813224 | 2020-01-03 10:18 | 2020-01-03 13:24 | 186 | 8 | 9 | 401.8376 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 716 SW.56 | CMI_PLANNED | YES | NO | NO | 859723 | 158927 | 102033 | 7592 | 1581 | 0.0004674 | 9.3053e-06 | 50.2297 | 1 | 310 | Load | 11590 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | #N/A
J2001.000691 | PD-01032020-00204 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6122 | 836122 | 2020-01-03 10:19 | 2020-01-03 10:45 | 26.37 | 1 | 1 | 8.9723 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1218 NW 19--OKC | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 167942 | 148151 | 11091 | 968 | 1.0436e-05 | 1.1632e-06 | 8.9723 | 1 | 310 | Customer | 11319 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2022
J2001.000697 | PD-01032020-00218 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5024 | 865024 | 2020-01-03 10:20 | 2020-01-03 12:09 | 109.3 | 7 | 7 | 219.8 | 28 | OTHER (DESCRIBE) | 31 | CONDUCTOR SERVICE - OH | MIDWEST CITY | 222 E.KITTYHAWK DR | CMI_PLANNED | YES | NO | NO | 859723 | 114178 | 71087 | 8623 | 1072 | 0.00025566 | 8.1422e-06 | 31.4 | 1 | 310 | Load | 4866 | Load | Tran1phOH | STEVEN CASKEY | 405-777-8855 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2022
J2001.000693 | PD-01032020-00213 | NORTHWEST | ENID | 4518:MENO TAP | MENO TAP 21 | 451821 | 2020-01-03 10:22 | 2020-01-03 11:06 | 44.37 | 1 | 1 | 44.3667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | LAHOMA | LAHOMA 2 3/4S, E INTO | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859723 | 53476 | 37552 | 1331 | 502 | 5.1606e-05 | 1.1632e-06 | 44.3667 | 1 | 310 | Load | 4727 | Load | Tran1phOH | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000695 | PD-01032020-00207 | ARKANSAS | POTEAU | 3509:PANAMA | PANAMA 21 | 350921 | 2020-01-03 10:24 | 2020-01-03 11:11 | 47.45 | 1 | 1 | 25.55 | 28 | OTHER (DESCRIBE) | 23 | FUSE - PRIMARY | PANAMA | PIERCE RD & RAILROAD | CMI_NORMAL | NO | NO | NO | 859723 | 82084 | 13444 | 1383 | 817 | 2.9719e-05 | 1.1632e-06 | 25.55 | 1 | 310 | Load | 2434 | Load | Tran1phOH | JOHN MEEH | 918-413-0959 | [5 empty] | Other | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | #N/A
J2001.000701 | PD-01032020-00224 | NORTHWEST | ENID | 4461:TURKEY CREEK | TURKEY_CREEK_6123 | 446123 | 2020-01-03 10:35 | 2020-01-03 11:26 | 51.47 | 1 | 1 | 51.4667 | 15 | SQUIRREL | 44 | METER - PRIMARY | HENNESSEY | 1W,1/2W,1/2S OF EXXON PLANT | CMI_NORMAL | NO | NO | NO | 859721 | 53476 | 37552 | 436 | 20 | 5.9864e-05 | 1.1632e-06 | 51.4667 | 1 | 320 | Load | 215773 | Load | 0 | STEVEN LORENZ | 580-822-3566 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | #N/A
J2001.000702 |  | SOUTHERN | MADILL | 5408:CANEY CREEK | CANEY_CREEK_831 | 540831 | 2020-01-03 10:37 | 2020-01-03 11:26 | 48.68 | 3 | 1 | 90 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | KINGSTON | 112 HANH DR | CMI_PLANNED | YES | NO | NO | 859815 | 77498 | 7198 | 1052 | 628 | 0.00010467 | 3.4891e-06 | 30 | 1 | 308 | Load | 19675 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000709 | PD-01032020-00236 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2023 | 822023 | 2020-01-03 10:52 | 2020-01-03 12:06 | 73.95 | 3 | 2 | 221.85 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2420 N.DREXEL | CMI_NORMAL | NO | NO | NO | 859815 | 167942 | 148151 | 6028 | 1028 | 0.00025802 | 3.4891e-06 | 73.95 | 1 | 311 | Load | 4252 | Load | Tran3phWye | ADAM COX | 405-328-8938 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | OK - 2022
J2001.000711 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2222 | 852222 | 2020-01-03 10:55 | 2020-01-03 11:59 | 64.73 | 1 | 2 | 60.275 | 4 | DETERIORATION | 2 | TRANSFORMER OH | HARRAH | 17869 NE.10 | CMI_PLANNED | YES | NO | NO | 859815 | 114178 | 71087 | 11611 | 2209 | 7.0102e-05 | 1.163e-06 | 60.275 | 1 | 310 | Load | 55910 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000717 | PD-01032020-00248 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3731 | 833731 | 2020-01-03 11:06 | 2020-01-03 12:19 | 72.67 | 1 | 2 | 13.4 | 4 | DETERIORATION | 50 | CONNECTOR | THE VILLAGE | 2020 CARLISLE RD | CMI_NORMAL | NO | NO | NO | 859815 | 167942 | 148151 | 5756 | 1902 | 1.5585e-05 | 1.163e-06 | 13.4 | 1 | 320 | Customer | 16309 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2020
J2001.000716 | PD-01032020-00254 | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_661 | 550661 | 2020-01-03 11:07 | 2020-01-03 15:29 | 261.93 | 1 | 2 | 257.8 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | DURANT | HWY78/FOLSOM DR SWC | CMI_NORMAL | NO | NO | NO | 859815 | 77498 | 15461 | 6727 | 445 | 0.00029983 | 1.163e-06 | 257.8 | 1 | 310 | Load | 328430 | Load | Tran3phPadWye | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000719 | PD-01032020-00255 | METRO WEST | WEST | 8157:MACARTHUR | MACARTHUR_5722 | 815722 | 2020-01-03 11:14 | 2020-01-03 12:40 | 86 | 346 | 146 | 21956.4667 | 3 | DAMAGED BY PUBLIC | 35 | CONDUCTOR PRIMARY - UG FEEDER | OKLAHOMA CITY | 3710 N MACARTHUR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 128532 | 115810 | 1853 | 347 | 0.025536 | 0.00040241 | 63.458 | 1 | 310 | Feeder | MACARTHR_5722 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-03 | 2020 |  | #N/A
J2001.000731 | PD-01032020-00273 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1122 | 511122 | 2020-01-03 11:37 | 2020-01-03 16:10 | 272.53 | 1 | 1 | 261.9333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | DICKSON | RUSTIC HILLS | CMI_PLANNED | YES | NO | NO | 859815 | 77498 | 23559 | 2205 | 1203 | 0.00030464 | 1.163e-06 | 261.9333 | 1 | 310 | Customer | 9168 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000732 | PD-01032020-00280 | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4022 | 914022 | 2020-01-03 11:39 | 2020-01-03 12:12 | 32.6 | 2 | 2 | 58.3 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 3400 DUKE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 82084 | 61114 | 4755 | 1904 | 6.7805e-05 | 2.3261e-06 | 29.15 | 1 | 310 | Secondary | 13390 | Load | Tran1phPad | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-03 | 2020 |  | Ark - Series 1
J2001.000736 | PD-01032020-00278 | ARKANSAS | POTEAU | 3505:POTEAU | POTEAU_524 | 350524 | 2020-01-03 11:44 | 2020-01-03 11:59 | 14.68 | 1 | 1 | 13.6667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | POTEAU | 1S .2W NS | CMI_NORMAL | NO | NO | NO | 859815 | 82084 | 13444 | 2295 | 721 | 1.5895e-05 | 1.163e-06 | 13.6667 | 1 | 310 | Customer | 15819 | Load | TranOpenDelta | TOBY C MEAD | 918-658-5596 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | #N/A
J2001.000742 |  | SOUTHERN | MADILL | 5409:LITTLE CITY | LITTLE CITY 21 | 540921 | 2020-01-03 11:46 | 2020-01-03 12:37 | 50.42 | 3 | 2 | 117.075 | 4 | DETERIORATION | 2 | TRANSFORMER OH | CUMBERLAND | 886 HICKS ST | CMI_PLANNED | YES | NO | NO | 859815 | 77498 | 7198 | 610 | 591 | 0.00013616 | 3.4891e-06 | 39.025 | 1 | 308 | Load | 10667 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000743 | PD-01032020-00319 | METRO SOUTH | SOUTH | 8722:MILLENNIUM | MILLENNIUM_2231 | 872231 | 2020-01-03 12:02 | 2020-01-03 13:28 | 86.33 | 1 | 1 | 80.7833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | NORMAN | 1219 36TH AV NE. | CMI_NORMAL | NO | NO | NO | 859815 | 158927 | 56894 | 4204 | 2053 | 9.3954e-05 | 1.163e-06 | 80.7833 | 1 | 310 | Load | 44082 | Load | Tran1phOH | MARK A PALMORE | 405-512-1933 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000744 | PD-01032020-00290 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-03 12:05 | 2020-01-03 13:07 | 61.57 | 2580 | 279 | 75787.3333 | 13 | PREMATURE FAILURE | 47 | ARRESTOR OH | MULBERRY | 6007 EAST HWY 64 | CMI_NORMAL | NO | NO | NO | 859815 | 82084 | 61114 | 3778 | 2580 | 0.088144 | 0.0030006 | 29.3749 | 1 | 310 | Feeder | SIMMONS_3061 | Recloser | SubRecloser | GEORGE N WORKMAN | 479-459-0918 | [5 empty] | Equipment | N | SUBSTATION | 161kV | 2020-01-03 | 2020 |  | Ark - Series 2
J2001.000748 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-03 12:09 | 2020-01-03 12:31 | 22.43 | 1 | 2 | 22.4333 | 1 | CANCELLED | 57 | CANCELLED | ALMA | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 0 | 0 | 0 | 0 | 2.6091e-05 | 1.163e-06 | 22.4333 | 1 | 310 | Customer |  | 0 | 0 | [6 empty] | 06/10/2020 note from burchamc. Reference J2001.000748 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Emailed Brent Miller with blank transformer and circuit #'s. Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-03 | 2020 |  | Ark - Series 2
J2001.000758 | PD-01032020-00303 | NORTHEAST | MUSKOGEE | 3109:HONOR HEIGHTS | HONOR_HEIGHTS_921 | 310921 | 2020-01-03 12:21 | 2020-01-03 13:42 | 81.42 | 1 | 2 | 67.65 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MUSKOGEE | MOCKINGBIRD LN | CMI_NORMAL | NO | NO | NO | 859815 | 73889 | 33203 | 1176 | 1154 | 7.868e-05 | 1.163e-06 | 67.65 | 1 | 310 | Load | 12826 | Load | Tran1phOH | JOSH CHENEY | 918-619-3590 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | OK - 2020
J2001.000766 |  | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2223 | 882223 | 2020-01-03 12:34 | 2020-01-03 13:18 | 43.7 | 3 | 2 | 80.45 | 4 | DETERIORATION | 2 | TRANSFORMER OH | EDMOND | 1817 S.GARRETT DR | CMI_PLANNED | YES | NO | NO | 859815 | 167942 | 19791 | 5382 | 1202 | 9.3567e-05 | 3.4891e-06 | 26.8167 | 1 | 308 | Load | 43861 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000769 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2231 | 852231 | 2020-01-03 12:44 | 2020-01-03 13:06 | 21.9 | 1 | 2 | 24.7313 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 4417 S.CHOCTAW RD | CMI_PLANNED | YES | NO | NO | 859815 | 114178 | 71087 | 11611 | 1436 | 2.8763e-05 | 1.163e-06 | 24.7313 | 1 | 310 | Load | 45960 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2021
J2001.000778 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-03 12:58 | 2020-01-03 13:23 | 24.98 | 1 | 1 | 24.9833 | 1 | CANCELLED | 57 | CANCELLED | MOUNTAINBURG | 1 SPAN E-HWY71 ON SIMCO,MTNBRG | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 82084 | 61114 | 3778 | 1198 | 2.9057e-05 | 1.163e-06 | 24.9833 | 1 | 310 | Customer | 4631 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-03 | 2020 |  | Ark - Series 2
J2001.000777 |  | METRO NORTH | NORTH | 8347:WILSHIRE | WILSHIRE_4723 | 834723 | 2020-01-03 13:00 | 2020-01-03 20:11 | 431.18 | 6 | 5 | 243.7918 | 4 | DETERIORATION | 17 | JUMPER | NICHOLS HILLS | 1712 DORCHESTER | CMI_PLANNED | YES | NO | NO | 859815 | 167942 | 148151 | 4621 | 1098 | 0.00028354 | 6.9782e-06 | 40.632 | 1 | 310 | Load | 14700 | Load | TranOHDeltaSplitBank | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2021
J2001.000779 | PD-01032020-00343 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3922 | 833922 | 2020-01-03 13:00 | 2020-01-03 14:05 | 64.58 | 1 | 1 | 56.7167 | 12 | POOR CONNECTION | 17 | JUMPER | OKLAHOMA CITY | *NW.50 + ANN ARBOR | CMI_NORMAL | NO | NO | NO | 859815 | 167942 | 148151 | 7845 | 1631 | 6.5964e-05 | 1.163e-06 | 56.7167 | 1 | 310 | Customer | 73159 | Load | Tran1phPad | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2022
J2001.000786 |  | METRO NORTH | NORTH | 8347:WILSHIRE | WILSHIRE_4723 | 834723 | 2020-01-03 13:05 | 2020-01-03 19:34 | 389.78 | 1 | 2 | 35.85 | 4 | DETERIORATION | 17 | JUMPER | NICHOLS HILLS | 1723 DORCHESTER PL | CMI_PLANNED | YES | NO | NO | 859815 | 167942 | 148151 | 4621 | 1098 | 4.1695e-05 | 1.163e-06 | 35.85 | 1 | 310 | Customer | 8809 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2021
J2001.000787 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6324 | 816324 | 2020-01-03 13:12 | 2020-01-03 15:31 | 139.02 | 5 | 5 | 244.5438 | 4 | DETERIORATION | 2 | TRANSFORMER OH | MOORE | 709 N JANEWAY | CMI_PLANNED | YES | NO | NO | 859815 | 158927 | 102033 | 11809 | 2048 | 0.00028441 | 5.8152e-06 | 48.9088 | 1 | 310 | Load | 22857 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2021
J2001.000784 |  | NORTHEAST | SAPULPA | 3210:HICKORY HILL | HICKORY_HILL_1024 | 321024 | 2020-01-03 13:16 | 2020-01-03 13:16 | 0 | 1210 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | SAPULPA | 9693 HICKORY HILL RD | CMI_MOMENTARY | YES | NO | NO | 859815 | 73889 | 40686 | 2682 | 1246 | 0 | 0.0014073 | 0 | 1 | 0 | Feeder | HICK HL_1024 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-03 | 2020 |  | OK - 2022
J2001.000793 | PD-01032020-00421 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_771 | 870771 | 2020-01-03 13:21 | 2020-01-03 16:11 | 169.73 | 1 | 2 | 168.1833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | NORMAN | 1835 72ND AV NE | CMI_NORMAL | NO | NO | NO | 859815 | 158927 | 56894 | 11825 | 1813 | 0.0001956 | 1.163e-06 | 168.1833 | 1 | 310 | Customer | 79570 | Load | Tran1phOH | JACOB SHANDY | 918-623-6369 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000791 |  | SOUTHERN | HEALDTON | 5122:DILLARD | DILLARD_2222 | 512222 | 2020-01-03 13:22 | 2020-01-03 13:22 | 0.05 | 697 | 0 | 34.85 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | WILSON | 7460 DILLARD RD | CMI_MOMENTARY | YES | NO | NO | 859815 | 77498 | 6784 | 1183 | 697 | 4.0532e-05 | 0.00081064 | 0.05 | 1 | 0 | Feeder | DILLARD_2222 | Breaker | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000799 | PD-01032020-00378 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4022 | 834022 | 2020-01-03 13:34 | 2020-01-03 14:08 | 33.7 | 1 | 1 | 33.7 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 9224 LANSBROOK LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 128532 | 115810 | 10838 | 1369 | 3.9194e-05 | 1.163e-06 | 33.7 | 1 | 310 | Customer | 38531 | Load | Tran1phPad | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000798 | PD-01032020-00408 | ARKANSAS | FORT SMITH | 9512:ADABELL ROAD | ADABELL_ROAD_1222 | 951222 | 2020-01-03 13:36 | 2020-01-03 14:34 | 58.05 | 1 | 1 | 58.05 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | VAN BUREN | 1111 BALDWIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 82084 | 61114 | 3119 | 1087 | 6.7515e-05 | 1.163e-06 | 58.05 | 1 | 310 | Customer | 11406 | Load | Tran1phOH | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-03 | 2020 |  | Ark - Series 1, Ark - Series 2
J2001.000814 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3831 | 913831 | 2020-01-03 13:48 | 2020-01-03 15:11 | 82.9 | 3 | 2 | 248.7 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 3901 S.18 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 82084 | 61114 | 2925 | 483 | 0.00028925 | 3.4891e-06 | 82.9 | 1 | 308 | Load | 1206 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-03 | 2020 |  | Ark - Series 2
J2001.000807 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-01-03 13:56 | 2020-01-03 14:00 | 4.9 | 1 | 1 | 4.9 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 553 N.COUNCIL RD | CMI_MOMENTARY | YES | NO | NO | 859815 | 128532 | 115810 | 3401 | 2034 | 5.6989e-06 | 1.163e-06 | 4.9 | 1 | 310 | Customer | 34638 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000810 | PD-01032020-00398 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2122 | 822122 | 2020-01-03 14:01 | 2020-01-03 14:48 | 47.13 | 1 | 1 | 42.6333 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 3817 NW.22 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859815 | 167942 | 148151 | 9235 | 2016 | 4.9584e-05 | 1.163e-06 | 42.6333 | 1 | 321 | Customer | 7838 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2020
J2001.000812 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5138 | 815138 | 2020-01-03 14:02 | 2020-01-03 14:29 | 27.62 | 1 | 1 | 27.6167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1332 SW.74 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 158927 | 102033 | 13933 | 1416 | 3.2119e-05 | 1.163e-06 | 27.6167 | 1 | 310 | Customer | 31481 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000823 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1024 | 541024 | 2020-01-03 14:10 | 2020-01-03 14:38 | 27.75 | 10 | 10 | 255.9167 | 4 | DETERIORATION | 1 | TRANSFORMER UG | MADILL | 603 W.DONEHOO | CMI_PLANNED | YES | NO | NO | 859815 | 77498 | 7198 | 2378 | 660 | 0.00029764 | 1.163e-05 | 25.5917 | 1 | 308 | Load | 7356 | Load | Tran1phPad | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000818 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9931 | 829931 | 2020-01-03 14:12 | 2020-01-03 14:21 | 8.92 | 1 | 1 | 8.9167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 5001 NW 10TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 128532 | 115810 | 9210 | 2190 | 1.037e-05 | 1.163e-06 | 8.9167 | 1 | 310 | Customer | 47897 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000820 | PD-01032020-00412 | SOUTHERN | HEALDTON | 5122:DILLARD | DILLARD_2222 | 512222 | 2020-01-03 14:15 | 2020-01-03 15:54 | 98.9 | 1 | 1 | 30.8167 | 25 | LIGHTNING | 36 | CONDUCTOR PRIMARY - UG | WILSON | WILSON HS | CMI_NORMAL | NO | NO | NO | 859815 | 77498 | 6784 | 1183 | 697 | 3.5841e-05 | 1.163e-06 | 30.8167 | 1 | 310 | Load | 30550 | Load | Tran3phWye | JIMMY DON ROWE | 580-490-6283 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000827 | PD-01032020-00422 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4122 | 814122 | 2020-01-03 14:32 | 2020-01-03 15:21 | 48.82 | 1 | 2 | 48.8167 | 4 | DETERIORATION | 15 | METER - SECONDARY | OKLAHOMA CITY | 133 SE.45 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859815 | 158927 | 102033 | 5796 | 1269 | 5.6776e-05 | 1.163e-06 | 48.8167 | 1 | 320 | Customer | 2517 | Load | Tran1phOH | JACOB SHANDY | 918-623-6369 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | #N/A
J2001.000828 |  | METRO NORTH | NORTH | 8347:WILSHIRE | WILSHIRE_4723 | 834723 | 2020-01-03 14:35 | 2020-01-03 16:56 | 141 | 7 | 0 | 883.05 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | NICHOLS HILLS | 1703 ELMHURST | CMI_PLANNED | YES | NO | NO | 859815 | 167942 | 148151 | 4621 | 1098 | 0.001027 | 8.1413e-06 | 126.15 | 1 | 0 | Load | 9527 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2021
J2001.000833 |  | SOUTHERN | HEALDTON | 5122:DILLARD | DILLARD_2222 | 512222 | 2020-01-03 14:46 | 2020-01-03 14:46 | 0 | 696 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | WILSON | 7460 DILLARD RD | CMI_MOMENTARY | YES | NO | NO | 859815 | 77498 | 6784 | 1183 | 697 | 0 | 0.00080948 | 0 | 1 | 0 | Feeder | DILLARD_2222 | Breaker | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000834 |  | METRO NORTH | NORTH | 8506:PARK PLACE | PARK_PLACE_623 | 850623 | 2020-01-03 14:48 | 2020-01-03 15:11 | 22.5 | 1 | 1 | 22.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 18 NW.17 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 167942 | 148151 | 829 | 266 | 2.6168e-05 | 1.163e-06 | 22.5 | 1 | 310 | Customer | 989 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000835 |  | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-01-03 14:49 | 2020-01-03 15:04 | 14.93 | 1 | 2 | 14.9333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DEL CITY | 2312 TROSPER PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 158927 | 102033 | 7406 | 2235 | 1.7368e-05 | 1.163e-06 | 14.9333 | 1 | 310 | Customer | 29357 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2022
J2001.000836 |  | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6522 | 836522 | 2020-01-03 14:54 | 2020-01-03 15:09 | 14.37 | 1 | 1 | 14.3667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6819 SAXON DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 128532 | 115810 | 7416 | 1859 | 1.6709e-05 | 1.163e-06 | 14.3667 | 1 | 310 | Customer | 47373 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2021
J2001.001189 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-01-03 15:00 | 2020-01-05 03:40 | 2200.43 | 1 | 1 | 2200.4333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1104 N.GLADE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 128532 | 115810 | 3401 | 2034 | 0.0025592 | 1.163e-06 | 2200.4333 | 1 | 310 | Customer | 41109 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000841 |  | METRO EAST | EAST | 8471:NE 30TH ST | NE_30TH_ST_7121 | 847121 | 2020-01-03 15:20 | 2020-01-03 15:53 | 33.85 | 7 | 1 | 205.5667 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | OKLAHOMA CITY | 1904 REDBUD DR. | CMI_PLANNED | YES | NO | NO | 859815 | 114178 | 71087 | 2396 | 342 | 0.00023908 | 8.1413e-06 | 29.3667 | 1 | 308 | Load | 45875 | Load | Tran1phPad | Contractor | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | OK - 2022
J2001.000845 | PD-01032020-00469 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3722 | 833722 | 2020-01-03 15:31 | 2020-01-03 16:04 | 32.88 | 8 | 10 | 237.0667 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | NICHOLS HILLS | 1100 TEDFORD WAY | CMI_NORMAL | NO | NO | NO | 859815 | 167942 | 148151 | 5756 | 1107 | 0.00027572 | 9.3043e-06 | 29.6333 | 1 | 310 | Load | 12236 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2022
J2001.000846 | PD-01032020-00471 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6961 | 846961 | 2020-01-03 15:38 | 2020-01-03 18:01 | 143.28 | 1 | 1 | 141.3667 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | L7,B3-OAKMOND ADDN | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859815 | 167942 | 148151 | 7711 | 1387 | 0.00016442 | 1.163e-06 | 141.3667 | 1 | 320 | Customer | 88093 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000853 |  | NORTHEAST | SAPULPA | 3214:LONE STAR | LONE_STAR_1421 | 321421 | 2020-01-03 15:45 | 2020-01-03 15:59 | 14.13 | 1 | 1 | 13.0333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SAPULPA | FAIRLANE DR HICKORY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 73889 | 40686 | 2651 | 1558 | 1.5158e-05 | 1.163e-06 | 13.0333 | 1 | 310 | Customer | 48349 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000852 | PD-01032020-00487 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1926 | 851926 | 2020-01-03 15:45 | 2020-01-03 16:56 | 70.73 | 1 | 2 | 66.5667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MIDWEST CITY | 617 MORAINE | CMI_NORMAL | NO | NO | NO | 859815 | 114178 | 71087 | 12429 | 2125 | 7.742e-05 | 1.163e-06 | 66.5667 | 1 | 310 | Customer | 29443 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2021
J2001.000856 |  | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_621 | 870621 | 2020-01-03 15:51 | 2020-01-03 16:00 | 9.68 | 1 | 1 | 9.6833 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 305 HAL-MULDROW DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 158927 | 56894 | 7362 | 925 | 1.1262e-05 | 1.163e-06 | 9.6833 | 1 | 310 | Customer | 46581 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000859 |  | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-01-03 16:05 | 2020-01-03 16:05 | 0.02 | 1822 | 0 | 30.3667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | EL RENO | 800 E RUSSELL | CMI_MOMENTARY | YES | NO | NO | 859815 | 128532 | 12722 | 6933 | 1822 | 3.5318e-05 | 0.0021191 | 0.016667 | 1 | 0 | Feeder | EL RENO_522 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000865 | PD-01032020-00509 | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1024 | 541024 | 2020-01-03 16:10 | 2020-01-03 21:51 | 340.77 | 1 | 1 | 311.0333 | 13 | PREMATURE FAILURE | 11 | REGULATOR | MADILL | N OF CITY E CARTRLK | CMI_NORMAL | NO | NO | NO | 859815 | 77498 | 7198 | 2378 | 660 | 0.00036174 | 1.163e-06 | 311.0333 | 1 | 310 | Load | 23059 | Load | Tran1phOH | JIMMY DON ROWE | 580-490-6283 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000869 | PD-01032020-00508 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-01-03 16:17 | 2020-01-03 17:24 | 66.63 | 1 | 1 | 66.6333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 4704 S.AGNEW | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 158927 | 102033 | 7592 | 2452 | 7.7497e-05 | 1.163e-06 | 66.6333 | 1 | 310 | Customer | 36562 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | #N/A
J2001.000871 | PD-01032020-00511 | NORTHEAST | SAPULPA | 3214:LONE STAR | LONE_STAR_1421 | 321421 | 2020-01-03 16:21 | 2020-01-03 18:22 | 120.9 | 1 | 1 | 120.9 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SAPULPA | FAIRLANE DR HICKORY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 73889 | 40686 | 2651 | 1558 | 0.00014061 | 1.163e-06 | 120.9 | 1 | 310 | Customer | 48349 | Load | Tran1phPad | STEPHEN BURKS | 918-639-0130 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000878 |  | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6522 | 836522 | 2020-01-03 16:38 | 2020-01-03 16:44 | 5.7 | 1 | 1 | 5.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6819 SAXON DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 128532 | 115810 | 7416 | 1859 | 6.6293e-06 | 1.163e-06 | 5.7 | 1 | 310 | Customer | 47373 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2021
J2001.000880 | PD-01032020-00522 | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3421 | 843421 | 2020-01-03 16:54 | 2020-01-03 18:34 | 100.2 | 1 | 1 | 100.2 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1915 NE.44 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 167942 | 148151 | 1224 | 498 | 0.00011654 | 1.163e-06 | 100.2 | 1 | 310 | Customer | 69675 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | #N/A
J2001.000887 |  | NORTHWEST | ENID | 4112:CHESTNUT | CHESTNUT_1222 | 411222 | 2020-01-03 17:06 | 2020-01-03 17:24 | 17.43 | 1 | 1 | 17.4333 | 1 | CANCELLED | 57 | CANCELLED | ENID | 2111 E WALNUT AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 53476 | 37552 | 2857 | 1745 | 2.0276e-05 | 1.163e-06 | 17.4333 | 1 | 308 | Customer | 7160 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | #N/A
J2001.000888 |  | ARKANSAS | FORT SMITH | 9508:WHITESIDE | WHITESIDE_821 | 950821 | 2020-01-03 17:24 | 2020-01-03 17:35 | 11.03 | 1 | 1 | 11.0333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | VAN BUREN | S. 22nd St. & jordan St. 300ft South | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 82084 | 61114 | 1918 | 1280 | 1.2832e-05 | 1.163e-06 | 11.0333 | 1 | 310 | Customer | 308899 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-03 | 2020 |  | Ark - Series 2
J2001.000889 | PD-01032020-00525 | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_923 | 910923 | 2020-01-03 17:24 | 2020-01-03 20:05 | 161.08 | 1 | 1 | 155.3 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | ARKOMA | 102 TEEN DR IN REAR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859815 | 82084 | 61114 | 5007 | 898 | 0.00018062 | 1.163e-06 | 155.3 | 1 | 310 | Customer | 13765 | Load | TranOHDeltaSplitBank | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | Ark - Series 3
J2001.000893 | PD-01032020-00528 | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-01-03 17:48 | 2020-01-03 19:11 | 83.35 | 1 | 1 | 83.35 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ADA | 818 EAST 9TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 77498 | 11496 | 2516 | 1090 | 9.6939e-05 | 1.163e-06 | 83.35 | 1 | 310 | Customer | 4470 | Load | Tran1phOH | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | #N/A
J2001.000900 |  | SOUTHERN | PAULS VALLEY | 5619:RUSH CREEK | RUSH_CREEK_1921 | 561921 | 2020-01-03 18:31 | 2020-01-03 18:53 | 21.98 | 1 | 1 | 21.9833 | 1 | CANCELLED | 57 | CANCELLED | PAULS VALLEY | 113 TANGLEWOOD DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 77512 | 6195 | 2072 | 823 | 2.5568e-05 | 1.163e-06 | 21.9833 | 1 | 308 | Customer | 3869 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | #N/A
J2001.000906 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9931 | 829931 | 2020-01-03 19:12 | 2020-01-03 19:31 | 18.77 | 1 | 1 | 18.7667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 952 N.MACARTHUR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 128547 | 115825 | 9211 | 2190 | 2.1826e-05 | 1.163e-06 | 18.7667 | 1 | 320 | Customer | 2156 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000916 | PD-01032020-00546 | METRO EAST | SHAWNEE | 7409:MCLOUD | MCLOUD_922 | 740922 | 2020-01-03 21:11 | 2020-01-04 00:10 | 179.48 | 77 | 46 | 13572.5333 | 4 | DETERIORATION | 17 | JUMPER | MCLOUD | 1/2MW MCLD RD ON EW112 | CMI_NORMAL | NO | NO | NO | 859815 | 114191 | 22067 | 2027 | 1208 | 0.015785 | 8.9554e-05 | 176.2667 | 1 | 310 | Mainline | 6640 | Fuse | FuseRiser | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | OK - 2021
J2001.000926 |  | NORTHWEST | ENID | 4135:SO 4TH ST | SO_4TH_ST_3522 | 413522 | 2020-01-03 21:23 | 2020-01-03 21:50 | 27.22 | 1 | 1 | 27.2167 | 1 | CANCELLED | 57 | CANCELLED | ENID | 1305 HITE BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 53482 | 37555 | 3094 | 1483 | 3.1654e-05 | 1.163e-06 | 27.2167 | 1 | 308 | Customer | 4457 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000927 | PD-01032020-00549 | NORTHEAST | SAPULPA | 7632:OAK GROVE | OAK_GROVE_3221 | 763221 | 2020-01-03 21:40 | 2020-01-04 | 140.05 | 1 | 1 | 128.1167 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 21 | FUSE - TRANSFORMER | OAKGROVE | .5N OAKGROVE SCH | CMI_NORMAL | NO | NO | NO | 859815 | 73896 | 40689 | 1018 | 1018 | 0.000149 | 1.163e-06 | 128.1167 | 1 | 310 | Load | 47762 | Load | Tran1phOH | GREGORY R HOOVER | 918-261-6803 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-03 | 2020 |  | OK - 2021
J2001.000929 |  | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_422 | 580422 | 2020-01-03 21:47 | 2020-01-03 22:09 | 21.9 | 1 | 1 | 17.0833 | 1 | CANCELLED | 57 | CANCELLED | ADA | 1300 KERR-LAB RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 77512 | 11498 | 3410 | 1426 | 1.9869e-05 | 1.163e-06 | 17.0833 | 1 | 308 | Customer | 17539 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000931 |  | SOUTHERN | ADA | 5809:VANOSS | VANOSS_922 | 580922 | 2020-01-03 21:58 | 2020-01-03 22:17 | 19.15 | 1 | 1 | 19.15 | 1 | CANCELLED | 57 | CANCELLED | STRATFORD | 510 GARVIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 77512 | 11498 | 977 | 977 | 2.2272e-05 | 1.163e-06 | 19.15 | 1 | 308 | Customer | 2227 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | OK - 2021
J2001.000934 |  | METRO SOUTH | SOUTH CENTRAL | 8133:WR AIRPORT | WR_AIRPORT_3323 | 813323 | 2020-01-03 22:48 | 2020-01-04 05:11 | 382.6 | 2 | 1 | 717.9333 | 3 | DAMAGED BY PUBLIC | 35 | CONDUCTOR PRIMARY - UG FEEDER | OKLAHOMA CITY | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 158939 | 102040 | 1485 | 83 | 0.00083499 | 2.3261e-06 | 358.9667 | 1 | 308 | Mainline | 317832-1 | Switch | SwitchDefault | OGE | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000936 |  | METRO SOUTH | SOUTH CENTRAL | 8133:WR AIRPORT | WR_AIRPORT_3323 | 813323 | 2020-01-03 22:58 | 2020-01-04 04:49 | 351 | 1 | 1 | 349.3 | 3 | DAMAGED BY PUBLIC | 35 | CONDUCTOR PRIMARY - UG FEEDER | OKLAHOMA CITY | SW,MACARTHUR/NEWCASTLE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859815 | 158939 | 102040 | 1485 | 83 | 0.00040625 | 1.163e-06 | 349.3 | 1 | 308 | Mainline | 22771 | Switch | 0 | OGE | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000939 | PD-01032020-00552 | NORTHEAST | SAPULPA | 3216:BEELINE | BEELINE_1633 | 321633 | 2020-01-03 23:27 | 2020-01-04 01:25 | 118.08 | 12 | 14 | 1316.2 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | GLENPOOL | S END FERN ST | CMI_NORMAL | NO | NO | NO | 859815 | 73896 | 40689 | 5554 | 1946 | 0.0015308 | 1.3956e-05 | 109.6833 | 1 | 310 | Mainline | 61718 | Fuse | FuseRiser | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000937 |  | NORTHEAST | SAPULPA | 3216:BEELINE | BEELINE_1633 | 321633 | 2020-01-03 23:27 | 2020-01-03 23:27 | 0 | 1940 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | GLENPOOL | 3594 OKMULGEE BEELINE EXPY | CMI_MOMENTARY | YES | NO | NO | 859815 | 73896 | 40689 | 5554 | 1946 | 0 | 0.0022563 | 0 | 1 | 0 | Feeder | BEELINE_1633 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-03 | 2020 |  | #N/A
J2001.000958 | PD-01042020-00008 | METRO EAST | EAST | 8471:NE 30TH ST | NE_30TH_ST_7123 | 847123 | 2020-01-04 04:21 | 2020-01-04 10:05 | 344.38 | 17 | 20 | 5704.0667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 3124 NE.14 | CMI_NORMAL | NO | NO | NO | 859806 | 114191 | 71093 | 2396 | 1288 | 0.0066341 | 1.9772e-05 | 335.5333 | 1 | 310 | Load | 11463 | Load | Tran1phOH | BRIAN E WHITE | 405-642-7075 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | OK - 2022
J2001.000970 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2124 | 822124 | 2020-01-04 07:40 | 2020-01-04 09:11 | 91 | 1 | 1 | 56.5167 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | ANN ARBOR / RENO | CMI_PLANNED | YES | NO | NO | 859806 | 167957 | 148165 | 9235 | 423 | 6.5732e-05 | 1.1631e-06 | 56.5167 | 1 | 308 | Load | 63494 | Load | Tran3phPadWye | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | OK - 2021
J2001.000972 | PD-01042020-00013 | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_522 | 560522 | 2020-01-04 07:47 | 2020-01-04 10:08 | 140.62 | 1 | 2 | 133.75 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | PAOLI | 107 S OKLAHOMA, PAOLI 73074 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859806 | 77512 | 6195 | 2450 | 825 | 0.00015556 | 1.1631e-06 | 133.75 | 1 | 320 | Customer | 13517 | Load | Tran1phOH | GARRID H BROWN | 405-207-3948 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | OK - 2022
J2001.000976 | PD-01042020-00015 | ARKANSAS | POTEAU | 3514:HEAVENER | HEAVENER 22 | 351422 | 2020-01-04 08:01 | 2020-01-04 10:18 | 136.77 | 1 | 2 | 134.4 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | HEAVENER | 445 TH STREET- BY INTAKE PUMP | CMI_NORMAL | NO | NO | NO | 859806 | 82098 | 13448 | 1763 | 1301 | 0.00015631 | 1.1631e-06 | 134.4 | 1 | 310 | Load | 220538 | Load | Tran1phOH | JOHN MEEH | 918-413-0959 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | OK - 2021
J2001.000977 | PD-01042020-00016 | NORTHEAST | SAPULPA | 3213:BOWDEN | BOWDEN_1321 | 321321 | 2020-01-04 08:11 | 2020-01-04 09:46 | 95.22 | 2 | 4 | 186.1833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | SAPULPA | 3N ON 66 W OF TPKE | CMI_NORMAL | NO | NO | NO | 859806 | 73896 | 40689 | 3368 | 820 | 0.00021654 | 2.3261e-06 | 93.0917 | 1 | 310 | Load | 46074 | Load | Tran1phOH | STEPHEN BURKS | 918-639-0130 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.000978 | PD-01042020-00017 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2263 | 852263 | 2020-01-04 08:24 | 2020-01-04 12:57 | 273.43 | 1 | 1 | 273.4333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 3801 N.HIWASSEE RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 114191 | 71093 | 11612 | 1526 | 0.00031802 | 1.1631e-06 | 273.4333 | 1 | 320 | Load | 45107 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | OK - 2021
J2001.000980 | PD-01042020-00018 | NORTHEAST | SAPULPA | 3214:LONE STAR | LONE_STAR_1421 | 321421 | 2020-01-04 08:30 | 2020-01-04 09:13 | 42.5 | 1 | 1 | 42.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SAPULPA | FAIRLANE DR HICKORY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 73896 | 40689 | 2651 | 1558 | 4.943e-05 | 1.1631e-06 | 42.5 | 1 | 310 | Customer | 48349 | Load | Tran1phPad | STEPHEN BURKS | 918-639-0130 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.000982 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2124 | 822124 | 2020-01-04 08:49 | 2020-01-04 08:50 | 0.07 | 401 | 0 | 26.7333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 4431 NW 10TH ST | CMI_MOMENTARY | YES | NO | NO | 859806 | 167957 | 148165 | 9235 | 423 | 3.1092e-05 | 0.00046638 | 0.066667 | 1 | 0 | Feeder | MERIDIAN_2124 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-04 | 2020 |  | OK - 2021
J2001.000987 |  | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_924 | 910924 | 2020-01-04 08:56 | 2020-01-04 09:18 | 22.6 | 1 | 1 | 22.6 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 60 HAVEN-HILL DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 82098 | 61123 | 5007 | 1723 | 2.6285e-05 | 1.1631e-06 | 22.6 | 1 | 308 | Customer | 8341 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | Ark - Series 3
J2001.000984 | PD-01042020-00023 | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-01-04 08:57 | 2020-01-04 11:35 | 157.9 | 1 | 1 | 137.1333 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | FORT SMITH | 412 RIDGE POINT RD | CMI_NORMAL | NO | NO | NO | 859806 | 82098 | 61123 | 1455 | 1237 | 0.00015949 | 1.1631e-06 | 137.1333 | 1 | 320 | Customer | 339458 | Load | Tran1phPad | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | Ark - Series 2
J2001.000986 | PD-01042020-00025 | METRO EAST | CHANDLER | 7117:JACKTOWN | JACKTOWN_1742 | 711742 | 2020-01-04 09:03 | 2020-01-04 11:41 | 157.87 | 8 | 7 | 1223.3333 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | MEEKER | 211 S.CLARK | CMI_NORMAL | NO | NO | NO | 859806 | 114191 | 7450 | 1010 | 827 | 0.0014228 | 9.3044e-06 | 152.9167 | 1 | 310 | Load | 8219 | Load | Tran1phOH | JIM R HEIDEN | 405-501-1680 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.000988 |  | METRO EAST | EAST | 8471:NE 30TH ST | NE_30TH_ST_7123 | 847123 | 2020-01-04 09:14 | 2020-01-04 10:23 | 69.02 | 26 | 7 | 288.1667 | 4 | DETERIORATION | 18 | INSULATOR | OKLAHOMA CITY | .2MEBRYANT .3MNNE10 | CMI_PLANNED | YES | NO | NO | 859806 | 114191 | 71093 | 2396 | 1288 | 0.00033515 | 3.0239e-05 | 11.0833 | 1 | 310 | Tap | 18158 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | OK - 2022
J2001.000993 | PD-01042020-00028 | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3421 | 843421 | 2020-01-04 09:20 | 2020-01-04 10:40 | 79.82 | 11 | 15 | 818.2167 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1212 NE.39 | CMI_NORMAL | NO | NO | NO | 859806 | 167957 | 148165 | 1224 | 498 | 0.00095163 | 1.2794e-05 | 74.3833 | 1 | 310 | Load | 5976 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Other | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | #N/A
J2001.000999 |  | NORTHWEST | ENID | 4353:OTTER | OTTER_5341 | 435341 | 2020-01-04 09:26 | 2020-01-04 09:51 | 25.02 | 1 | 1 | 25.0167 | 1 | CANCELLED | 57 | CANCELLED | COVINGTON | 404 W MAINE ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 53482 | 37555 | 960 | 792 | 2.9096e-05 | 1.1631e-06 | 25.0167 | 1 | 308 | Customer | 6419 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | OK - 2021
J2001.000997 | PD-01042020-00030 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3627 | 833627 | 2020-01-04 09:40 | 2020-01-04 11:23 | 102.87 | 1 | 1 | 65.3721 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2120 NW.118 TR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 167957 | 148165 | 8780 | 1494 | 7.6031e-05 | 1.1631e-06 | 65.3721 | 1 | 310 | Customer | 59105 | Load | Tran1phPad | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.000996 | PD-01042020-00033 | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_629 | 730629 | 2020-01-04 09:41 | 2020-01-04 14:07 | 266.37 | 1 | 1 | 266.3667 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | SEMINOLE | 2701 BOREN BLVD. | CMI_NORMAL | NO | NO | NO | 859806 | 114191 | 13581 | 4056 | 567 | 0.0003098 | 1.1631e-06 | 266.3667 | 1 | 320 | Load | 213362 | Load | 0 | BAD ORDER PRIMARY RES COORD | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | OK - 2021
J2001.001003 | PD-01042020-00035 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5136 | 815136 | 2020-01-04 09:46 | 2020-01-04 10:31 | 44.58 | 5 | 5 | 219.4167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2500 SW.84 | CMI_NORMAL | NO | NO | NO | 859806 | 158939 | 102040 | 13933 | 1299 | 0.00025519 | 5.8153e-06 | 43.8833 | 1 | 310 | Load | 46895 | Load | Tran1phOH | SHANE DRAKE | 405-326-9052 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | OK - 2021
J2001.001000 | PD-01042020-00040 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4033 | 834033 | 2020-01-04 09:48 | 2020-01-04 14:51 | 303.4 | 1 | 1 | 303.4 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 7616 DORIS PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 128547 | 115825 | 10839 | 1115 | 0.00035287 | 1.1631e-06 | 303.4 | 1 | 310 | Customer | 65543 | Load | Tran1phPad | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001009 |  | NORTHWEST | ENID | 4112:CHESTNUT | CHESTNUT_1222 | 411222 | 2020-01-04 09:56 | 2020-01-04 10:20 | 24.9 | 1 | 1 | 24.9 | 1 | CANCELLED | 57 | CANCELLED | ENID | 2111 E WALNUT AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 53482 | 37555 | 2857 | 1745 | 2.896e-05 | 1.1631e-06 | 24.9 | 1 | 308 | Customer | 7160 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | #N/A
J2001.001010 | PD-01042020-00038 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6021 | 836021 | 2020-01-04 10:07 | 2020-01-04 11:45 | 98.17 | 8 | 8 | 779.8667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | BETHANY | 2725 SHANNON AV | CMI_NORMAL | NO | NO | NO | 859806 | 128547 | 115825 | 5503 | 1450 | 0.00090703 | 9.3044e-06 | 97.4833 | 1 | 310 | Load | 23789 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | #N/A
J2001.001005 |  | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6021 | 836021 | 2020-01-04 10:07 | 2020-01-04 10:07 | 0.08 | 1450 | 0 | 120.8333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 4315 N COUNCIL RD | CMI_MOMENTARY | YES | NO | NO | 859806 | 128547 | 115825 | 5503 | 1450 | 0.00014054 | 0.0016864 | 0.083333 | 1 | 0 | Feeder | WOODLAWN_6021 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-04 | 2020 |  | #N/A
J2001.001014 |  | SOUTHERN | ADA | 5809:VANOSS | VANOSS_922 | 580922 | 2020-01-04 10:08 | 2020-01-04 10:33 | 25.27 | 1 | 1 | 25.2667 | 1 | CANCELLED | 57 | CANCELLED | STRATFORD | 510 GARVIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 77512 | 11498 | 977 | 977 | 2.9386e-05 | 1.1631e-06 | 25.2667 | 1 | 308 | Customer | 2227 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | OK - 2021
J2001.001016 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3829 | 913829 | 2020-01-04 10:11 | 2020-01-04 10:34 | 22.8 | 1 | 1 | 22.8 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 1700 JENNY-LIND | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 82098 | 61123 | 2926 | 1182 | 2.6518e-05 | 1.1631e-06 | 22.8 | 1 | 308 | Customer | 11608 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-04 | 2020 |  | Ark - Series 2
J2001.001015 | PD-01042020-00042 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_722 | 870722 | 2020-01-04 10:25 | 2020-01-04 11:14 | 48.6 | 3993 | 1648 | 181605.9 | 15 | SQUIRREL | 56 | SCADA - LOCKOUT | NORMAN | 1798 E LINDSEY | CMI_NORMAL | NO | NO | NO | 859806 | 158939 | 56899 | 11825 | 0 | 0.21122 | 0.0046441 | 45.4811 | 1 | 310 | Substation | WILKINSON_122 | Breaker | SubRecloser | [6 empty] | 06/10/2020 note from burchamc. Reference J2001.001015 in iDashboard report OSI_Job_Detail_Viewer. The job references Device WILKINSN_722L and WILKINSN_724L. Probably should have been two jobs. Used Lead Device ID WILKINSN_122 to Manually completed blank Job Region, Job Area, etc. | Animals | N | SUBSTATION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001017 | PD-01042020-00052 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_723 | 870723 | 2020-01-04 10:25 | 2020-01-04 11:30 | 64.67 | 20 | 6 | 910.1667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | EASTGATE DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 158939 | 56899 | 11825 | 2042 | 0.0010586 | 2.3261e-05 | 45.5083 | 1 | 310 | Load | 71916 | Load | Tran1phPad | SHANE DRAKE | 405-326-9052 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001019 | PD-01042020-00051 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_771 | 870771 | 2020-01-04 10:29 | 2020-01-04 11:24 | 54.78 | 1 | 1 | 41.1833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | 3107 WOOD VALLEY RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 158939 | 56899 | 11825 | 1813 | 4.7898e-05 | 1.1631e-06 | 41.1833 | 1 | 310 | Customer | 367293 | Load | Tran1phPad | SHANE DRAKE | 405-326-9052 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001018 | PD-01042020-00053 | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2731 | 872731 | 2020-01-04 10:30 | 2020-01-04 11:27 | 57.02 | 1 | 1 | 40.8167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | 614 UTAH AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 158939 | 56899 | 6452 | 1349 | 4.7472e-05 | 1.1631e-06 | 40.8167 | 1 | 310 | Customer | 44657 | Load | Tran1phOH | SHANE DRAKE | 405-326-9052 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001020 | PD-01042020-00050 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1221 | 831221 | 2020-01-04 10:31 | 2020-01-04 13:36 | 185.15 | 1 | 1 | 183.5333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | NICHOLS HILLS | 0 | CMI_NORMAL | NO | NO | NO | 859806 | 0 | 0 | 0 | 0 | 0.00021346 | 1.1631e-06 | 183.5333 | 1 | 310 | Customer |  | 0 | 0 | KIRK REILLEY | 405-550-3062 |  |  |  |  | 06/10/2020 note from burchamc. Reference J2001.001020 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Manually completed blank Job Region, Job Area, etc. | Animals | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | OK - 2022
J2001.001022 | PD-01042020-00045 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5022 | 865022 | 2020-01-04 10:31 | 2020-01-04 12:32 | 120.52 | 6 | 9 | 605.3 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MIDWEST CITY | 2504 N.TOWRY DR | CMI_NORMAL | NO | NO | NO | 859806 | 114191 | 71093 | 8623 | 1660 | 0.000704 | 6.9783e-06 | 100.8833 | 1 | 310 | Load | 12761 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | OK - 2022
J2001.001026 | PD-01042020-00049 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_629 | 870629 | 2020-01-04 10:34 | 2020-01-04 11:53 | 78.8 | 14 | 18 | 1070.7667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | NORMAN | 909 IOWA | CMI_NORMAL | NO | NO | NO | 859806 | 158939 | 56899 | 7362 | 1372 | 0.0012454 | 1.6283e-05 | 76.4833 | 1 | 310 | Load | 36638 | Load | Tran1phOH | SHANE DRAKE | 405-326-9052 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001027 | PD-01042020-00055 | METRO SOUTH | SOUTH | 8719:PLEASANT VLY | PLEASANT_VAL_1924 | 871924 | 2020-01-04 10:42 | 2020-01-04 11:33 | 51.23 | 1 | 1 | 51.2333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | 4004 PLEASANT GROVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 158939 | 56899 | 2107 | 928 | 5.9587e-05 | 1.1631e-06 | 51.2333 | 1 | 310 | Customer | 79771 | Load | Tran1phPad | SHANE DRAKE | 405-326-9052 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001030 |  | METRO WEST | EL RENO | 8910:OKARCHE | OKARCHE_1021 | 891021 | 2020-01-04 10:46 | 2020-01-04 11:16 | 30.68 | 1 | 1 | 30.6833 | 1 | CANCELLED | 57 | CANCELLED | OKARCHE | 224 S.4 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 128547 | 12722 | 725 | 725 | 3.5686e-05 | 1.1631e-06 | 30.6833 | 1 | 308 | Customer | 38750 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | #N/A
J2001.001032 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1862 | 941862 | 2020-01-04 10:46 | 2020-01-04 11:17 | 30.97 | 1 | 1 | 30.9667 | 1 | CANCELLED | 57 | CANCELLED | LAMAR | 130 DEER FIELD RD. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 82098 | 7527 | 730 | 730 | 3.6016e-05 | 1.1631e-06 | 30.9667 | 1 | 308 | Customer | 248995 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | Ark - Series 2
J2001.001033 | PD-01042020-00047 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9929 | 829929 | 2020-01-04 11:03 | 2020-01-04 15:13 | 250.12 | 1 | 1 | 250.1167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | BETHANY | 7801 NW.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 128547 | 115825 | 9211 | 2203 | 0.0002909 | 1.1631e-06 | 250.1167 | 1 | 310 | Customer | 28506 | Load | TranOH3phDelta | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001040 |  | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2169 | 892169 | 2020-01-04 11:03 | 2020-01-04 11:26 | 22.72 | 1 | 1 | 21.5167 | 1 | CANCELLED | 57 | CANCELLED | CALUMET | 401 FREEHOME | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 128547 | 12722 | 3171 | 428 | 2.5025e-05 | 1.1631e-06 | 21.5167 | 1 | 308 | Customer | 50108 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | OK - 2020
J2001.001035 | PD-01042020-00054 | NORTHEAST | SAPULPA | 3216:BEELINE | BEELINE_1629 | 321629 | 2020-01-04 11:06 | 2020-01-04 12:11 | 64.67 | 1 | 1 | 64.6667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | GLENPOOL | 808 137ST-S GLEN-PINES M/H PK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 73896 | 40689 | 5554 | 1250 | 7.5211e-05 | 1.1631e-06 | 64.6667 | 1 | 310 | Customer | 43163 | Load | Tran1phPad | STEPHEN BURKS | 918-639-0130 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001037 | PD-01042020-00048 | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3421 | 843421 | 2020-01-04 11:09 | 2020-01-04 12:57 | 108.35 | 11 | 7 | 1175.5333 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1309 NE.34 | CMI_NORMAL | NO | NO | NO | 859806 | 167957 | 148165 | 1224 | 498 | 0.0013672 | 1.2794e-05 | 106.8667 | 1 | 310 | Load | 13489 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | #N/A
J2001.001036 | PD-01042020-00056 | METRO SOUTH | SOUTH | 8728:CHERRY CREEK | CHERRY_CREEK_2831 | 872831 | 2020-01-04 11:09 | 2020-01-04 11:36 | 26.63 | 1 | 1 | 26.6333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | S END OF "F"ST WEST LOT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 158939 | 56899 | 7100 | 1642 | 3.0976e-05 | 1.1631e-06 | 26.6333 | 1 | 310 | Customer | 79334 | Load | Tran1phPad | SHANE DRAKE | 405-326-9052 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001042 |  | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3421 | 843421 | 2020-01-04 11:22 | 2020-01-04 11:36 | 14.02 | 1 | 1 | 14.0167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 610 NE.50 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 167957 | 148165 | 1224 | 498 | 1.6302e-05 | 1.1631e-06 | 14.0167 | 1 | 310 | Customer | 14429 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | #N/A
J2001.001047 |  | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2124 | 332124 | 2020-01-04 11:26 | 2020-01-04 11:48 | 21.9 | 1 | 1 | 21.9 | 1 | CANCELLED | 57 | CANCELLED | FORT GIBSON | 212 S Capitol | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 73896 | 33207 | 3329 | 1218 | 2.5471e-05 | 1.1631e-06 | 21.9 | 1 | 308 | Customer | 13215 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-04 | 2020 |  | #N/A
J2001.001049 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3831 | 913831 | 2020-01-04 11:30 | 2020-01-04 11:49 | 18.43 | 3 | 3 | 55.3 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 3920 S.18, 3 POLE S-JACKSON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 82098 | 61123 | 2926 | 483 | 6.4317e-05 | 3.4892e-06 | 18.4333 | 1 | 308 | Secondary | 5540 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-04 | 2020 |  | Ark - Series 2
J2001.001045 | PD-01042020-00060 | NORTHWEST | ENID | 4119:GLENWOOD | GLENWOOD_1924 | 411924 | 2020-01-04 11:34 | 2020-01-04 12:46 | 72.5 | 1 | 1 | 72.5 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ENID | 3W.5N BAMBOO CLUB | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 53482 | 37555 | 5410 | 1413 | 8.4321e-05 | 1.1631e-06 | 72.5 | 1 | 310 | Customer | 4293 | Load | Tran1phOH | KEVIN N PERRYMAN | 601-528-2473 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001051 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3831 | 913831 | 2020-01-04 11:36 | 2020-01-04 12:06 | 30.8 | 11 | 7 | 338.8 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 3920 S.18, 3 POLE S-JACKSON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 82098 | 61123 | 2926 | 483 | 0.00039404 | 1.2794e-05 | 30.8 | 1 | 308 | Load | 5540 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-04 | 2020 |  | Ark - Series 2
J2001.001052 | PD-01042020-00062 | METRO EAST | EAST | 8542:RENO | RENO_4222 | 854222 | 2020-01-04 11:51 | 2020-01-04 19:35 | 464 | 14 | 15 | 6352.9667 | 27 | TREE:NON PREVENTABLE | 31 | CONDUCTOR SERVICE - OH | MIDWEST CITY | 6212 SE.8 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859806 | 114191 | 71093 | 5209 | 1689 | 0.0073888 | 1.6283e-05 | 453.7833 | 1 | 310 | Load | 16355 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001053 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_722 | 870722 | 2020-01-04 11:53 | 2020-01-04 12:06 | 12.58 | 1 | 1 | 12.5833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 2500 MEADOWOOD BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 158939 | 56899 | 11825 | 1583 | 1.4635e-05 | 1.1631e-06 | 12.5833 | 1 | 310 | Customer | 250484 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001057 | PD-01042020-00064 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1926 | 851926 | 2020-01-04 12:12 | 2020-01-04 13:22 | 70.32 | 4 | 4 | 241 | 15 | SQUIRREL | 20 | FUSE BARREL | MIDWEST CITY | 1228 MCDONALD DR | CMI_NORMAL | NO | NO | NO | 859806 | 114191 | 71093 | 12429 | 2125 | 0.0002803 | 4.6522e-06 | 60.25 | 1 | 311 | Secondary | 21591 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | OK - 2021
J2001.001067 | PD-01042020-00072 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1522 | 811522 | 2020-01-04 13:01 | 2020-01-04 14:29 | 88.12 | 1 | 1 | 80.7 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2829 SW.31 | CMI_NORMAL | NO | NO | NO | 859806 | 158939 | 102040 | 6051 | 1938 | 9.3858e-05 | 1.1631e-06 | 80.7 | 1 | 310 | Customer | 54802 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | OK - 2022
J2001.001069 | PD-01042020-00073 | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_647 | 890647 | 2020-01-04 13:10 | 2020-01-04 19:55 | 404.67 | 1067 | 137 | 123722.2 | 3 | DAMAGED BY PUBLIC | 45 | SUBSTATION CIRCUIT | SOUTHARD | HWY 51 AND HWY 51A, GO.5 MILE SOUTH, .5 MILE EAST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 128547 | 12722 | 1363 | 1067 | 0.1439 | 0.001241 | 115.9533 | 1 | 310 | Feeder | SOUTHARD_647 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001075 | PD-01042020-00074 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-01-04 13:24 | 2020-01-04 15:28 | 124.43 | 17 | 14 | 2019.3167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | DEL CITY | 2321 MUSTANG | CMI_NORMAL | NO | NO | NO | 859806 | 158939 | 102040 | 7407 | 2235 | 0.0023486 | 1.9772e-05 | 118.7833 | 1 | 310 | Load | 13886 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | OK - 2022
J2001.001079 | PD-01042020-00076 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3021 | 743021 | 2020-01-04 13:30 | 2020-01-04 19:29 | 359.25 | 7 | 13 | 2424.8 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | SHAWNEE | 1027 E.WALLACE | CMI_NORMAL | NO | NO | NO | 859806 | 114191 | 22067 | 6632 | 1698 | 0.0028202 | 8.1414e-06 | 346.4 | 1 | 310 | Load | 4226 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | OK - 2021
J2001.001080 | PD-01042020-00077 | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_623 | 410623 | 2020-01-04 13:43 | 2020-01-04 15:02 | 78.77 | 1 | 1 | 78.7667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ENID | 2316 SINGLE TREE LANE--ENID | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 53482 | 37555 | 6009 | 1546 | 9.161e-05 | 1.1631e-06 | 78.7667 | 1 | 310 | Customer | 12448 | Load | Tran1phPad | KEVIN N PERRYMAN | 601-528-2473 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | #N/A
J2001.001085 | PD-01042020-00078 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3924 | 833924 | 2020-01-04 14:04 | 2020-01-04 14:59 | 54.97 | 1 | 1 | 54.9667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 3500-3510 NW EXPRESSWAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 167957 | 148165 | 7846 | 795 | 6.3929e-05 | 1.1631e-06 | 54.9667 | 1 | 310 | Customer | 18709 | Load | Tran3phPadWye | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | OK - 2022
J2001.001088 |  | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-01-04 14:09 | 2020-01-04 19:04 | 294.58 | 1 | 1 | 95.2 | 4 | DETERIORATION | 21 | FUSE - TRANSFORMER | EL RENO | 1/8M W HY81 ON JONE | CMI_PLANNED | YES | NO | NO | 859806 | 128547 | 12722 | 6933 | 1822 | 0.00011072 | 1.1631e-06 | 95.2 | 1 | 308 | Load | 65424 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001094 | PD-01042020-00081 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-01-04 14:24 | 2020-01-04 15:23 | 58.62 | 7 | 7 | 398.1833 | 4 | DETERIORATION | 20 | FUSE BARREL | OKLAHOMA CITY | 9901 N MCKINLEY | CMI_NORMAL | NO | NO | NO | 859806 | 167957 | 148165 | 8780 | 1948 | 0.00046311 | 8.1414e-06 | 56.8833 | 1 | 310 | Load | 19000 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | OK - 2021
J2001.001092 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-01-04 14:24 | 2020-01-04 14:24 | 0 | 1948 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 2204 HEFNER RD | CMI_MOMENTARY | YES | NO | NO | 859806 | 167957 | 148165 | 8780 | 1948 | 0 | 0.0022656 | 0 | 1 | 0 | Feeder | TENNESSE_3635 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-04 | 2020 |  | OK - 2021
J2001.001093 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_722 | 870722 | 2020-01-04 14:28 | 2020-01-04 14:34 | 6.5 | 1 | 1 | 6.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 1406 GLEN-OAKS CT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 158939 | 56899 | 11825 | 1583 | 7.5598e-06 | 1.1631e-06 | 6.5 | 1 | 310 | Customer | 67191 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001099 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_722 | 870722 | 2020-01-04 14:51 | 2020-01-04 15:01 | 10.05 | 1 | 1 | 10.05 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 818 BEAUMONT SQUARE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 158939 | 56899 | 11825 | 1583 | 1.1689e-05 | 1.1631e-06 | 10.05 | 1 | 310 | Customer | 229408 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001103 | PD-01042020-00086 | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1022 | 541022 | 2020-01-04 15:26 | 2020-01-04 17:08 | 102.35 | 873 | 231 | 89337 | 3 | DAMAGED BY PUBLIC | 28 | CROSSARM | MADILL | 12537 HIGHWAY 199 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 77512 | 7201 | 2379 | 873 | 0.1039 | 0.0010153 | 102.3333 | 1 | 311 | Feeder | GLASSES_1022 | Recloser | SubRecloser | GARRETT YOUNG | 580-276-6194 | [5 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001105 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1022 | 541022 | 2020-01-04 15:30 | 2020-01-04 20:10 | 279.77 | 1 | 1 | 97.7833 | 1 | CANCELLED | 57 | CANCELLED | MADILL | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 0 | 0 | 0 | 0 | 0.00011373 | 1.1631e-06 | 97.7833 | 1 | 310 | Customer |  | 0 | 0 | [6 empty] | 06/10/2020 note from burchamc. Reference J2001.001105 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001107 | PD-01042020-00088 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9921 | 829921 | 2020-01-04 15:35 | 2020-01-04 16:20 | 44.88 | 6 | 8 | 269.3 | 27 | TREE:NON PREVENTABLE | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 524 N.PENIEL | CMI_NORMAL | NO | NO | NO | 859806 | 128547 | 115825 | 9211 | 1632 | 0.00031321 | 6.9783e-06 | 44.8833 | 1 | 310 | Load | 2078 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001106 | PD-01042020-00087 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9921 | 829921 | 2020-01-04 15:35 | 2020-01-04 18:44 | 188.85 | 4 | 7 | 725.9667 | 3 | DAMAGED BY PUBLIC | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 508 N.PENIEL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 128547 | 115825 | 9211 | 1632 | 0.00084434 | 4.6522e-06 | 181.4917 | 1 | 310 | Load | 22911 | Load | Tran1phOH | BEAU S HUDSON | 405-306-8284 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001109 |  | METRO EAST | EAST | 8542:RENO | RENO_4222 | 854222 | 2020-01-04 15:44 | 2020-01-04 19:36 | 232.6 | 1 | 2 | 221.45 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | MIDWEST CITY | 6125.5 SE.8 | CMI_PLANNED | YES | NO | NO | 859806 | 114191 | 71093 | 5209 | 1689 | 0.00025756 | 1.1631e-06 | 221.45 | 1 | 310 | Customer | 37801 | Load | Tran1phOH | WORK TREE | [6 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001112 |  | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6021 | 836021 | 2020-01-04 16:09 | 2020-01-04 16:14 | 5.13 | 1450 | 18 | 1836.6667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 4315 N COUNCIL RD | CMI_MOMENTARY | YES | NO | NO | 859806 | 128547 | 115825 | 5503 | 1450 | 0.0021361 | 0.0016864 | 1.2667 | 1 | 310 | Feeder | WOODLAWN_6021 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-04 | 2020 |  | #N/A
J2001.001118 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9923 | 829923 | 2020-01-04 16:17 | 2020-01-04 16:31 | 14.23 | 1 | 1 | 14.2333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 937 N.ROCKWELL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 128547 | 115825 | 9211 | 863 | 1.6554e-05 | 1.1631e-06 | 14.2333 | 1 | 310 | Customer | 42432 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001119 | PD-01042020-00094 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7431 | 847431 | 2020-01-04 16:19 | 2020-01-04 17:18 | 59.32 | 1 | 1 | 59.3167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 805 NE.35 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 167957 | 148165 | 6148 | 373 | 6.8988e-05 | 1.1631e-06 | 59.3167 | 1 | 310 | Customer | 24309 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | OK - 2022
J2001.001127 | PD-01042020-00098 | METRO SOUTH | SOUTH CENTRAL | 8717:TURNER | TURNER_1721 | 871721 | 2020-01-04 16:47 | 2020-01-04 17:46 | 59.48 | 1 | 1 | 59.4833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 428 SW 168TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 158939 | 102040 | 3082 | 1985 | 6.9182e-05 | 1.1631e-06 | 59.4833 | 1 | 310 | Customer | 340056 | Load | Tran1phPad | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001128 | PD-01042020-00100 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9921 | 829921 | 2020-01-04 17:04 | 2020-01-04 17:53 | 48.92 | 1 | 1 | 48.9167 | 3 | DAMAGED BY PUBLIC | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 524 N.PENIEL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 128547 | 115825 | 9211 | 1632 | 5.6893e-05 | 1.1631e-06 | 48.9167 | 1 | 310 | Customer | 2078 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001132 | PD-01042020-00106 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3222 | 813222 | 2020-01-04 17:36 | 2020-01-04 18:34 | 57.63 | 1 | 1 | 57.6333 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 5508 S PENN | CMI_NORMAL | NO | NO | NO | 859806 | 158939 | 102040 | 7592 | 1482 | 6.7031e-05 | 1.1631e-06 | 57.6333 | 1 | 320 | Customer | 3004 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | #N/A
J2001.001135 | PD-01042020-00107 | SOUTHERN | DURANT | 5505:DURANT | DURANT 22 | 550522 | 2020-01-04 18:04 | 2020-01-04 20:11 | 126.57 | 1 | 1 | 126.5667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | BLUE | 1/4 E/PIRTLE SS/70 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 77515 | 15465 | 1319 | 798 | 0.0001472 | 1.1631e-06 | 126.5667 | 1 | 310 | Load | 26944 | Load | Tran1phOH | JUSTIN MARSHALL | 580-504-0986 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001139 | PD-01042020-00109 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6021 | 836021 | 2020-01-04 18:38 | 2020-01-05 01:40 | 421.95 | 2 | 2 | 823.3 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | COUNCIL / NW 27TH | CMI_NORMAL | NO | NO | NO | 859806 | 128547 | 115825 | 5502 | 1450 | 0.00095754 | 2.3261e-06 | 411.65 | 1 | 310 | Secondary | 70073 | Load | Tran1phOH | SHANE DRAKE | 405-326-9052 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | #N/A
J2001.001143 |  | NORTHWEST | ENID | 4153:IMO | IMO_5324 | 415324 | 2020-01-04 19:07 | 2020-01-04 19:22 | 14.87 | 1 | 1 | 14.8667 | 1 | CANCELLED | 57 | CANCELLED | IMO | MM STA.-2 W,3/4 S. EAST INTO. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 53480 | 37554 | 1177 | 671 | 1.7291e-05 | 1.1631e-06 | 14.8667 | 1 | 310 | Customer | 13386 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001146 | PD-01042020-00113 | SOUTHERN | HEALDTON | 5322:DUNDEE | DUNDEE 22 | 532222 | 2020-01-04 19:18 | 2020-01-04 23:19 | 240.95 | 8 | 8 | 1870 | 4 | DETERIORATION | 2 | TRANSFORMER OH | RINGLING | 215 E F ST | CMI_NORMAL | NO | NO | NO | 859806 | 77515 | 6784 | 1011 | 1000 | 0.0021749 | 9.3044e-06 | 233.75 | 1 | 310 | Load | 9042 | Load | Tran1phOH | ROBERT J BEARDSLEE | 580-618-2506 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001149 |  | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6021 | 836021 | 2020-01-04 20:26 | 2020-01-05 01:48 | 322.38 | 6 | 8 | 1866.3 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 8108 NW.25 | CMI_PLANNED | YES | NO | NO | 859806 | 128547 | 115825 | 5502 | 1450 | 0.0021706 | 6.9783e-06 | 311.05 | 1 | 310 | Load | 27892 | Load | Tran1phOH | Crew | [6 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | #N/A
J2001.001153 |  | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_422 | 580422 | 2020-01-04 20:36 | 2020-01-04 20:57 | 20.68 | 1 | 1 | 17.7167 | 1 | CANCELLED | 57 | CANCELLED | ADA | 1300 KERR-LAB RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 77515 | 11499 | 3410 | 1426 | 2.0605e-05 | 1.1631e-06 | 17.7167 | 1 | 308 | Customer | 17539 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | #N/A
J2001.001154 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-04 20:50 | 2020-01-04 21:06 | 16.88 | 1 | 1 | 16.8833 | 1 | CANCELLED | 57 | CANCELLED | LAVACA | 1801 N.18 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 82099 | 61123 | 2732 | 2120 | 1.9636e-05 | 1.1631e-06 | 16.8833 | 1 | 308 | Load | 14298 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | Ark - Series 2
J2001.001155 |  | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6021 | 836021 | 2020-01-04 20:59 | 2020-01-05 01:48 | 288.85 | 4 | 6 | 1111.4 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 8128 NW.25 | CMI_PLANNED | YES | NO | NO | 859806 | 128547 | 115825 | 5502 | 1450 | 0.0012926 | 4.6522e-06 | 277.85 | 1 | 310 | Load | 27893 | Load | Tran1phOH | Crew | [6 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | #N/A
J2001.001156 |  | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6021 | 836021 | 2020-01-04 20:59 | 2020-01-05 01:47 | 288.68 | 2 | 4 | 555.7167 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2437 N.COUNCIL RD | CMI_PLANNED | YES | NO | NO | 859806 | 128547 | 115825 | 5502 | 1450 | 0.00064633 | 2.3261e-06 | 277.8583 | 1 | 310 | Secondary | 27891 | Load | TranOpenDelta | Crew | [6 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | #N/A
J2001.001159 | PD-01042020-00123 | SOUTHERN | ARDMORE | 5117:MARIETTA | MARIETTA_1721 | 511721 | 2020-01-04 22:01 | 2020-01-04 22:30 | 28.87 | 1 | 1 | 28.8667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ARDMORE | LOT 7 OVERBROOK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 77515 | 23564 | 1594 | 637 | 3.3573e-05 | 1.1631e-06 | 28.8667 | 1 | 310 | Customer | 5872 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | #N/A
J2001.001163 |  | NORTHWEST | ENID | 4105:ENID | ENID_523 | 410523 | 2020-01-04 22:17 | 2020-01-04 22:36 | 19.08 | 1 | 1 | 19.0833 | 1 | CANCELLED | 57 | CANCELLED | ENID | 501 E MAPLE--ENID | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 53480 | 37554 | 1325 | 406 | 2.2195e-05 | 1.1631e-06 | 19.0833 | 1 | 308 | Customer | 192 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | #N/A
J2001.001167 |  | SOUTHERN | ADA | 5809:VANOSS | VANOSS_922 | 580922 | 2020-01-04 22:35 | 2020-01-04 22:53 | 17.87 | 1 | 1 | 17.8667 | 1 | CANCELLED | 57 | CANCELLED | STRATFORD | 510 GARVIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 77515 | 11499 | 978 | 978 | 2.078e-05 | 1.1631e-06 | 17.8667 | 1 | 308 | Customer | 2227 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-04 | 2020 |  | OK - 2021
J2001.001176 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_622 | 460622 | 2020-01-04 22:46 | 2020-01-04 23:08 | 21.92 | 1 | 1 | 21.9167 | 1 | CANCELLED | 57 | CANCELLED | WOODWARD | 3ME,1.5MN-WOODWARD ON 34C | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 53480 | 10411 | 5677 | 765 | 2.549e-05 | 1.1631e-06 | 21.9167 | 1 | 308 | Load | 2221 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | #N/A
J2001.001164 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_621 | 460621 | 2020-01-04 22:46 | 2020-01-04 22:46 | 0 | 787 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | WOODWARD | 1005 CEDAR AVE | CMI_MOMENTARY | YES | NO | NO | 859806 | 53480 | 10411 | 5677 | 787 | 0 | 0.00091532 | 0 | 1 | 0 | Feeder | CEDAR_AVE_621 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-04 | 2020 |  | #N/A
J2001.001179 |  | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_622 | 580622 | 2020-01-04 23:17 | 2020-01-04 23:35 | 18 | 1 | 1 | 18 | 1 | CANCELLED | 57 | CANCELLED | ADA | 2216 WOODLAND DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 77515 | 11499 | 2516 | 779 | 2.0935e-05 | 1.1631e-06 | 18 | 1 | 308 | Customer | 7276 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-04 | 2020 |  | #N/A
J2001.001186 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-05 01:27 | 2020-01-05 01:48 | 20.58 | 1 | 1 | 20.5833 | 1 | CANCELLED | 57 | CANCELLED | LAVACA | 1801 N.18 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859806 | 82099 | 61123 | 2732 | 2120 | 2.394e-05 | 1.1631e-06 | 20.5833 | 1 | 308 | Load | 14298 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-05 | 2020 |  | Ark - Series 2
J2001.001193 |  | NORTHEAST | SAPULPA | 3220:KELLYVILLE | KELLYVILLE_2024 | 322024 | 2020-01-05 05:59 | 2020-01-05 06:20 | 21.18 | 1 | 1 | 21.1833 | 1 | CANCELLED | 57 | CANCELLED | SAPULPA | 1/8E REESE HILL RD ON HWY33 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 73899 | 40689 | 2550 | 1580 | 2.4636e-05 | 1.163e-06 | 21.1833 | 1 | 308 | Load | 18305 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2020
J2001.001195 |  | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_861 | 550861 | 2020-01-05 06:23 | 2020-01-05 06:40 | 16.88 | 1 | 1 | 16.8833 | 1 | CANCELLED | 57 | CANCELLED | COBB | NW OF CITY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 77515 | 15465 | 1101 | 480 | 1.9635e-05 | 1.163e-06 | 16.8833 | 1 | 308 | Load | 2854 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001198 |  | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1224 | 911224 | 2020-01-05 06:28 | 2020-01-05 06:46 | 17.72 | 1 | 1 | 17.7167 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 1410 N.21, 3 POLE S-N.L ST. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 82099 | 61123 | 6590 | 1795 | 2.0605e-05 | 1.163e-06 | 17.7167 | 1 | 308 | Customer | 3926 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-05 | 2020 |  | Ark - Series 1
J2001.001204 | PD-01052020-00011 | NORTHWEST | ENID | 4158:FAIRMONT | FAIRMONT_5829 | 415829 | 2020-01-05 07:16 | 2020-01-05 09:01 | 105.43 | 2 | 3 | 198.4667 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 23 | FUSE - PRIMARY | BRECKENRIDGE | 1/2mn of Breckenridge Rd | CMI_NORMAL | NO | NO | NO | 859842 | 53480 | 37554 | 1640 | 1622 | 0.00023082 | 2.326e-06 | 99.2333 | 1 | 310 | Load | 251410 | Load | Tran1phOH | KEVIN N PERRYMAN | 601-528-2473 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2021
J2001.001203 | PD-01052020-00010 | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2822 | 312822 | 2020-01-05 07:24 | 2020-01-05 08:19 | 54.93 | 6 | 9 | 316 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MUSKOGEE | 436 GRANDVIEW BL | CMI_NORMAL | NO | NO | NO | 859842 | 73899 | 33210 | 5271 | 1107 | 0.00036751 | 6.978e-06 | 52.6667 | 1 | 310 | Load | 7684 | Load | Tran1phOH | REID R WILLIAMS | 512-618-8800 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-01-05 | 2020 |  | OK - 2020
J2001.001208 | PD-01052020-00012 | METRO NORTH | NORTH | 8506:PARK PLACE | PARK_PLACE_622 | 850622 | 2020-01-05 07:48 | 2020-01-05 09:41 | 112.98 | 1 | 1 | 112.9833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 100 N. Broadway | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167957 | 148165 | 830 | 8 | 0.0001314 | 1.163e-06 | 112.9833 | 1 | 310 | Customer | 60002 | Load | TranUGComSumersible | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001213 | PD-01052020-00013 | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_521 | 320521 | 2020-01-05 07:50 | 2020-01-05 09:12 | 81.65 | 8 | 10 | 568.5333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | SAPULPA | 922 S.OKLAHOMA | CMI_NORMAL | NO | NO | NO | 859842 | 73899 | 40689 | 3833 | 1604 | 0.00066121 | 9.304e-06 | 71.0667 | 1 | 310 | Load | 41694 | Load | Tran1phOH | STEPHEN BURKS | 918-639-0130 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-05 | 2020 |  | OK - 2022
J2001.001210 |  | NORTHWEST | ENID | 4135:SO 4TH ST | SO_4TH_ST_3522 | 413522 | 2020-01-05 07:52 | 2020-01-05 07:52 | 0 | 1482 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ENID | 2318 S LEONA MITCHELL BLVD | CMI_MOMENTARY | YES | NO | NO | 859842 | 53480 | 37554 | 3094 | 1483 | 0 | 0.0017236 | 0 | 1 | 0 | Feeder | SOUTH 4_3522 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001219 | PD-01052020-00014 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5123 | 815123 | 2020-01-05 07:57 | 2020-01-05 11:06 | 189.32 | 7 | 11 | 1291.15 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1404 SW.81 | CMI_NORMAL | NO | NO | NO | 859842 | 158940 | 102040 | 13933 | 1326 | 0.0015016 | 8.141e-06 | 184.45 | 1 | 310 | Load | 31204 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001211 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5123 | 815123 | 2020-01-05 07:57 | 2020-01-05 07:57 | 0 | 1326 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 8101 S PENNSYLVANIA AVE | CMI_MOMENTARY | YES | NO | NO | 859842 | 158940 | 102040 | 13933 | 1326 | 0 | 0.0015421 | 0 | 1 | 0 | Feeder | PENNSYLV_5123 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001221 | PD-01052020-00016 | METRO EAST | SHAWNEE | 7407:REMINGTON | REMINGTON 21 | 740721 | 2020-01-05 08:15 | 2020-01-05 13:11 | 296.1 | 1 | 4 | 119.1167 | 4 | DETERIORATION | 15 | METER - SECONDARY | EARLSBORO | 1 E OF HWY 3 + HWY 9A ( SS ) | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859842 | 114193 | 22067 | 3658 | 2014 | 0.00013853 | 1.163e-06 | 119.1167 | 1 | 310 | Customer | 114 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-05 | 2020 |  | OK - 2021
J2001.001225 | PD-01052020-00018 | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_824 | 870824 | 2020-01-05 08:31 | 2020-01-05 10:32 | 121.12 | 9 | 8 | 1060.2 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | NORMAN | 1005 WOODLAND DR | CMI_NORMAL | NO | NO | NO | 859842 | 158940 | 56900 | 6775 | 1460 | 0.001233 | 1.0467e-05 | 117.8 | 1 | 310 | Load | 46198 | Load | TranOHDeltaSplitBank | MONTY WISELEY | 405-471-2592 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001235 | PD-01052020-00019 | SOUTHERN | HEALDTON | 5309:POOLEVILLE | POOLEVILLE_925 | 530925 | 2020-01-05 08:55 | 2020-01-05 13:48 | 292.77 | 175 | 101 | 34627.8333 | 29 | TREES : GROW IN | 37 | CONDUCTOR PRIMARY - OH | ARDMORE | .7N OF HWY 53 ON POOLEVILLE RD | CMI_NORMAL | NO | NO | NO | 859842 | 77515 | 6784 | 401 | 258 | 0.040272 | 0.00020353 | 197.8733 | 1 | 310 | Mainline | 151485 | Recloser | Rec3phHydralic | [7 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001228 |  | SOUTHERN | HEALDTON | 5309:POOLEVILLE | POOLEVILLE_925 | 530925 | 2020-01-05 08:55 | 2020-01-05 08:55 | 0 | 258 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | RATLIFF CITY | 2779 WILDCAT JIM RD | CMI_MOMENTARY | YES | NO | NO | 859842 | 77515 | 6784 | 401 | 258 | 0 | 0.00030006 | 0 | 1 | 0 | Feeder | POOLEVILLE_925 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001241 |  | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1929 | 851929 | 2020-01-05 09:32 | 2020-01-05 09:32 | 0 | 826 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 8205 NE 10TH ST | CMI_MOMENTARY | YES | NO | NO | 859842 | 114193 | 71095 | 12429 | 826 | 0 | 0.00096064 | 0 | 1 | 0 | Feeder | NE 10TH_1929 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-05 | 2020 |  | OK - 2022
J2001.001243 | PD-01052020-00020 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6322 | 816322 | 2020-01-05 09:40 | 2020-01-05 09:51 | 11.12 | 1 | 1 | 8.2105 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MOORE | 1008 NW.21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 158940 | 102040 | 11809 | 1816 | 9.5488e-06 | 1.163e-06 | 8.2105 | 1 | 310 | Customer | 46568 | Load | Tran1phPad | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001249 | PD-01052020-00025 | NORTHEAST | SAPULPA | 3208:TIBBENS ROAD | TIBBENS_RD_821 | 320821 | 2020-01-05 10:18 | 2020-01-05 12:34 | 136.47 | 1 | 2 | 128 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | SAPULPA | 8307 S 49TH | CMI_NORMAL | NO | NO | NO | 859842 | 73899 | 40689 | 3138 | 1167 | 0.00014886 | 1.163e-06 | 128 | 1 | 310 | Load | 40931 | Load | Tran1phOH | STEPHEN BURKS | 918-639-0130 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001251 | PD-01052020-00023 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2224 | 852224 | 2020-01-05 10:30 | 2020-01-05 11:39 | 69.03 | 2 | 3 | 134.0167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | CHOCTAW | 13731 NE.9 | CMI_NORMAL | NO | NO | NO | 859842 | 114193 | 71095 | 11613 | 1522 | 0.00015586 | 2.326e-06 | 67.0083 | 1 | 310 | Load | 32211 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001255 | PD-01052020-00024 | METRO EAST | EAST | 8416:DUNJEE | DUNJEE_1623 | 841623 | 2020-01-05 10:36 | 2020-01-05 15:00 | 264.22 | 3 | 3 | 1050.35 | 12 | POOR CONNECTION | 17 | JUMPER | OKLAHOMA CITY | 11401 NE.50 | CMI_NORMAL | NO | NO | NO | 859842 | 114193 | 71095 | 3537 | 1986 | 0.0012216 | 3.489e-06 | 350.1167 | 1 | 310 | Load | 26320 | Load | Tran1phOH | BRIAN E WHITE | 405-642-7075 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001254 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3629 | 833629 | 2020-01-05 10:44 | 2020-01-05 10:49 | 5.27 | 1 | 1 | 5.2667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | THE VILLAGE | 2237 DOWNING | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167957 | 148165 | 8780 | 1396 | 6.1252e-06 | 1.163e-06 | 5.2667 | 1 | 310 | Customer | 85285 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001257 | PD-01052020-00026 | METRO EAST | SHAWNEE | 7411:DALE | DALE_1129 | 741129 | 2020-01-05 10:48 | 2020-01-05 14:03 | 195.5 | 65 | 2 | 17778.5833 | 4 | DETERIORATION | 13 | PIN | MCLOUD | 1MI W I-40+DALE EXIT | CMI_NORMAL | NO | NO | NO | 859842 | 114193 | 22067 | 966 | 965 | 0.020677 | 7.5595e-05 | 273.5167 | 1 | 310 | Mainline | 1636 | Fuse | FuseOH | DAVID M CLEMMONS | 405-777-8355 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2021
J2001.001256 |  | METRO EAST | SHAWNEE | 7411:DALE | DALE_1129 | 741129 | 2020-01-05 10:48 | 2020-01-05 10:48 | 0.07 | 965 | 0 | 64.3333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MCCLOUD | 32401 45TH ST | CMI_MOMENTARY | YES | NO | NO | 859842 | 114193 | 22067 | 966 | 965 | 7.482e-05 | 0.0011223 | 0.066667 | 1 | 0 | Feeder | DALE_1129 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-05 | 2020 |  | OK - 2021
J2001.001260 |  | METRO EAST | SHAWNEE | 7411:DALE | DALE_1129 | 741129 | 2020-01-05 10:56 | 2020-01-05 15:28 | 272.17 | 1 | 1 | 265.2667 | 4 | DETERIORATION | 28 | CROSSARM | MCLOUD | 33401 45th St | CMI_NORMAL | NO | NO | NO | 859842 | 114193 | 22067 | 966 | 965 | 0.00030851 | 1.163e-06 | 265.2667 | 1 | 310 | Load | 312687 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2021
J2001.001271 | PD-01052020-00028 | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2224 | 882224 | 2020-01-05 11:11 | 2020-01-05 13:50 | 159.38 | 1 | 1 | 159.3833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | EDMOND | N.5L19 KAN WAT ACRES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167957 | 19792 | 5382 | 1846 | 0.00018536 | 1.163e-06 | 159.3833 | 1 | 310 | Customer | 45595 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001272 | PD-01052020-00030 | METRO EAST | SEMINOLE | 7512:CROMWELL | CROMWELL 47 | 751247 | 2020-01-05 11:16 | 2020-01-05 16:29 | 312.97 | 1 | 1 | 244.9833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | SHAWNEE | 1-1\2 MN OF CROMWELL SUB | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 114193 | 13581 | 308 | 308 | 0.00028492 | 1.163e-06 | 244.9833 | 1 | 310 | Customer | 9233 | Load | Tran1phOH | KEVIN M RICH | 405-802-2121 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-05 | 2020 |  | #N/A
J2001.001277 | PD-01052020-00031 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5024 | 865024 | 2020-01-05 11:40 | 2020-01-05 12:14 | 34.25 | 1 | 1 | 31.4164 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MIDWEST CITY | 516 E Gruman Dr | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 114193 | 71095 | 8623 | 1072 | 3.6537e-05 | 1.163e-06 | 31.4164 | 1 | 310 | Customer | 334986 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2022
J2001.001282 |  | METRO EAST | SHAWNEE | 7411:DALE | DALE_1129 | 741129 | 2020-01-05 12:06 | 2020-01-05 15:30 | 203.92 | 1 | 1 | 195.4167 | 4 | DETERIORATION | 28 | CROSSARM | MCLOUD | S-INTRSTATE 40 ON HWY 102 | CMI_NORMAL | NO | NO | NO | 859842 | 114193 | 22067 | 966 | 965 | 0.00022727 | 1.163e-06 | 195.4167 | 1 | 310 | Customer | 19271 | Load | Tran1phOH | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2021
J2001.001285 | PD-01052020-00034 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3729 | 833729 | 2020-01-05 12:06 | 2020-01-05 12:24 | 17.87 | 12 | 15 | 1670.2 | 22 | WIND | 17 | JUMPER | OKLAHOMA CITY | 337 NW.90 | CMI_NORMAL | NO | NO | NO | 859842 | 167957 | 148165 | 5754 | 1400 | 0.0019424 | 1.3956e-05 | 139.1833 | 1 | 310 | Load | 24303 | Load | Tran1phOH | Ties | [6 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2021
J2001.001290 | PD-01052020-00042 | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_423 | 710423 | 2020-01-05 12:12 | 2020-01-05 17:37 | 325.27 | 23 | 6 | 7254.5833 | 4 | DETERIORATION | 27 | CUTOUT | CHANDLER | ALY S 5TH ON IOWA | CMI_NORMAL | NO | NO | NO | 859842 | 114193 | 7450 | 2818 | 975 | 0.0084371 | 2.6749e-05 | 315.4167 | 1 | 310 | Mainline | 1151 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001284 |  | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_423 | 710423 | 2020-01-05 12:12 | 2020-01-05 12:12 | 0.05 | 851 | 0 | 42.55 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | CHANDLER | N 3450 RD AND HWY 66 | CMI_MOMENTARY | YES | NO | NO | 859842 | 114193 | 7450 | 2818 | 975 | 4.9486e-05 | 0.00098972 | 0.05 | 1 | 0 | Feeder | BELLCOW_423 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001288 | PD-01052020-00036 | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1224 | 911224 | 2020-01-05 12:18 | 2020-01-05 15:31 | 193.28 | 1 | 2 | 177.7 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | FORT SMITH | 1410 N.21, 3 POLE S-N.L ST. | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859842 | 82099 | 61123 | 6590 | 1795 | 0.00020667 | 1.163e-06 | 177.7 | 1 | 310 | Customer | 3926 | Load | Tran1phOH | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-05 | 2020 |  | Ark - Series 1
J2001.001289 | PD-01052020-00040 | SOUTHERN | ARDMORE | 5106:HARRIS ST | HARRIS_ST_621 | 510621 | 2020-01-05 12:26 | 2020-01-05 13:55 | 89.37 | 1 | 1 | 89.3667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ARDMORE | 1000 MAXWELL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 77515 | 23564 | 2067 | 61 | 0.00010393 | 1.163e-06 | 89.3667 | 1 | 310 | Customer | 13053 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-05 | 2020 |  | #N/A
J2001.001291 | PD-01052020-00038 | METRO NORTH | NORTH | 8209:CLASSEN | CLASSEN_923 | 820923 | 2020-01-05 12:29 | 2020-01-05 13:09 | 40.12 | 1 | 2 | 40.1167 | 13 | PREMATURE FAILURE | 15 | METER - SECONDARY | OKLAHOMA CITY | 1408 NW.8 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859842 | 167957 | 148165 | 3877 | 1146 | 4.6656e-05 | 1.163e-06 | 40.1167 | 1 | 310 | Customer | 1748 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001293 | PD-01052020-00043 | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_421 | 710421 | 2020-01-05 12:32 | 2020-01-05 17:07 | 275.62 | 1 | 1 | 275.6167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | CHANDLER | 13TH + MANVEL-CHANDLER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 114193 | 7450 | 2818 | 1171 | 0.00032054 | 1.163e-06 | 275.6167 | 1 | 310 | Customer | 19818 | Load | Tran1phOH | JIM R HEIDEN | 405-501-1680 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2021
J2001.001296 | PD-01052020-00041 | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5821 | 845821 | 2020-01-05 12:40 | 2020-01-05 14:21 | 100.52 | 1 | 1 | 100.5167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 10300 NE.78 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 114193 | 71095 | 2983 | 1189 | 0.0001169 | 1.163e-06 | 100.5167 | 1 | 310 | Load | 55002 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-05 | 2020 |  | OK - 2020
J2001.001303 |  | METRO EAST | SHAWNEE | 7411:DALE | DALE_1129 | 741129 | 2020-01-05 13:38 | 2020-01-05 15:31 | 112.7 | 7 | 2 | 718.7833 | 4 | DETERIORATION | 28 | CROSSARM | MCLOUD | 1MI W I-40+DALE EXIT | CMI_NORMAL | NO | NO | NO | 859842 | 114193 | 22067 | 966 | 965 | 0.00083595 | 8.141e-06 | 102.6833 | 1 | 310 | Mainline | 1636 | Fuse | FuseOH | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2021
J2001.001305 | PD-01052020-00047 | NORTHWEST | ENID | 4153:IMO | IMO_5324 | 415324 | 2020-01-05 13:59 | 2020-01-05 14:55 | 56.15 | 1 | 1 | 56.15 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | IMO | MM STA.-2 W,3/4 S. EAST INTO. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 53480 | 37554 | 1177 | 671 | 6.5303e-05 | 1.163e-06 | 56.15 | 1 | 310 | Customer | 13386 | Load | Tran1phPad | KEVIN N PERRYMAN | 601-528-2473 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001306 | PD-01052020-00046 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3621 | 853621 | 2020-01-05 14:03 | 2020-01-05 14:23 | 20.17 | 1 | 1 | 20.1667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1164 N.MISSOURI | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167957 | 148165 | 5913 | 2162 | 2.3454e-05 | 1.163e-06 | 20.1667 | 1 | 310 | Customer | 7039 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2022
J2001.001315 |  | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_522 | 560522 | 2020-01-05 14:58 | 2020-01-05 19:11 | 253.92 | 2 | 2 | 433.0333 | 1 | CANCELLED | 57 | CANCELLED | PAOLI | PAOLI SR CITIZEN S CTR-HWY 145 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 77515 | 6195 | 2450 | 825 | 0.00050362 | 2.326e-06 | 216.5167 | 1 | 308 | Secondary | 25339 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-05 | 2020 |  | OK - 2022
J2001.001316 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3831 | 913831 | 2020-01-05 15:01 | 2020-01-05 19:11 | 249.52 | 2 | 2 | 162.6667 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 1216 S. KNOXVILLE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 82099 | 61123 | 2926 | 483 | 0.00018918 | 2.326e-06 | 81.3333 | 1 | 308 | Secondary | 16522 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-05 | 2020 |  | Ark - Series 2
J2001.001314 | PD-01052020-00050 | SOUTHERN | ARDMORE | 5124:BERWYN | BERWYN_2422 | 512422 | 2020-01-05 15:06 | 2020-01-05 18:15 | 189.23 | 1 | 1 | 189.2333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ARDMORE | MT PLEASANT CHURCH,.7S,ES | CMI_NORMAL | NO | NO | NO | 859842 | 77515 | 23564 | 1034 | 260 | 0.00022008 | 1.163e-06 | 189.2333 | 1 | 310 | Load | 27564 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001318 | PD-01052020-00051 | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2522 | 512522 | 2020-01-05 15:25 | 2020-01-05 16:20 | 55.1 | 1 | 1 | 55.1 | 5 | ELECTRICAL TRACKING | 21 | FUSE - TRANSFORMER | LONE GROVE | LG 5N ON NWPT RD | CMI_NORMAL | NO | NO | NO | 859842 | 77515 | 23564 | 3301 | 562 | 6.4082e-05 | 1.163e-06 | 55.1 | 1 | 310 | Load | 20337 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2021
J2001.001320 | PD-01052020-00049 | SOUTHERN | SULPHUR | 5707:MILL CREEK | MILL CREEK 23 | 570723 | 2020-01-05 15:28 | 2020-01-05 18:17 | 168.87 | 1 | 1 | 168.8667 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | MILL CREEK | 2.1S/7 WS/1 N/MILL CREEK | CMI_NORMAL | NO | NO | NO | 859842 | 77515 | 6807 | 210 | 191 | 0.00019639 | 1.163e-06 | 168.8667 | 1 | 310 | Customer | 27850 | Load | Tran1phOH | GARRID H BROWN | 405-207-3948 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001322 |  | ARKANSAS | POTEAU | 3608:MULDROW | MULDROW 23 | 360823 | 2020-01-05 15:32 | 2020-01-05 17:12 | 100 | 1 | 1 | 79.2 | 4 | DETERIORATION | 12 | POLE | MULDROW | 310 WILLARD | CMI_NORMAL | NO | NO | NO | 859842 | 82099 | 13450 | 2268 | 487 | 9.211e-05 | 1.163e-06 | 79.2 | 1 | 310 | Customer | 8208 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-05 | 2020 |  | #N/A
J2001.001325 |  | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-01-05 15:47 | 2020-01-05 16:14 | 27.77 | 1 | 1 | 27.7667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DEL CITY | 4208 SE 25TH ST DEL CITY 731152536 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 158940 | 102040 | 7407 | 2235 | 3.2293e-05 | 1.163e-06 | 27.7667 | 1 | 310 | Customer | 304879 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2022
J2001.001328 | PD-01052020-00059 | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3421 | 843421 | 2020-01-05 15:55 | 2020-01-05 16:22 | 26.68 | 1 | 1 | 26.6833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1534 NE.42 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167957 | 148165 | 1224 | 498 | 3.1033e-05 | 1.163e-06 | 26.6833 | 1 | 310 | Customer | 24342 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-05 | 2020 |  | #N/A
J2001.001329 | PD-01052020-00054 | SOUTHERN | MADILL | 5408:CANEY CREEK | CANEY_CREEK_831 | 540831 | 2020-01-05 15:57 | 2020-01-05 17:08 | 70.72 | 1 | 1 | 36.7333 | 23 | CUSTOMER EQUIPMENT | 15 | METER - SECONDARY | KINGSTON | KINGSTON, HWY70-32, 0.5MW, ES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 77515 | 7201 | 1052 | 628 | 4.2721e-05 | 1.163e-06 | 36.7333 | 1 | 310 | Load | 25994 | Load | Tran1phPad | GARRETT YOUNG | 580-276-6194 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001334 | PD-01052020-00062 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3221 | 813221 | 2020-01-05 16:17 | 2020-01-05 16:59 | 41.62 | 1 | 1 | 12.977 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1213 SW 41st | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 158940 | 102040 | 7592 | 2073 | 1.5092e-05 | 1.163e-06 | 12.977 | 1 | 310 | Customer | 31405 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-05 | 2020 |  | #N/A
J2001.001335 |  | METRO WEST | EL RENO | 8908:ROMAN NOSE | ROMAN_NOSE_847 | 890847 | 2020-01-05 16:24 | 2020-01-05 17:05 | 41.5 | 1 | 1 | 41.5 | 1 | CANCELLED | 57 | CANCELLED | WATONGA | Hwy33 3ME 1N | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 128547 | 12722 | 523 | 214 | 4.8265e-05 | 1.163e-06 | 41.5 | 1 | 310 | Load | 238682 | Load | Tran3phPadWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2020
J2001.001336 | PD-01052020-00063 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-01-05 16:25 | 2020-01-05 23:53 | 448.1 | 6 | 4 | 2633.65 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | DEL CITY | 4217 SE.26 | CMI_NORMAL | NO | NO | NO | 859842 | 158940 | 102040 | 7407 | 2235 | 0.0030629 | 6.978e-06 | 438.9417 | 1 | 310 | Load | 22115 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2022
J2001.001339 | PD-01052020-00064 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-01-05 16:30 | 2020-01-05 17:32 | 61.9 | 1 | 1 | 7.0964 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 2301 SW.44 | CMI_NORMAL | NO | NO | NO | 859842 | 158940 | 102040 | 7592 | 2452 | 8.2532e-06 | 1.163e-06 | 7.0964 | 1 | 310 | Customer | 17692 | Load | TranOpenDelta | MONTY WISELEY | 405-471-2592 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-05 | 2020 |  | #N/A
J2001.001344 | PD-01052020-00071 | ARKANSAS | FORT SMITH | 9508:WHITESIDE | WHITESIDE_822 | 950822 | 2020-01-05 16:49 | 2020-01-05 17:52 | 62.7 | 6 | 7 | 350.4 | 5 | ELECTRICAL TRACKING | 21 | FUSE - TRANSFORMER | VAN BUREN | 612 SYCAMORE | CMI_NORMAL | NO | NO | NO | 859842 | 82099 | 61123 | 1919 | 209 | 0.00040752 | 6.978e-06 | 58.4 | 1 | 310 | Load | 485 | Load | Tran1phOH | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-05 | 2020 |  | Ark - Series 2
J2001.001342 | PD-01052020-00069 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2031 | 862031 | 2020-01-05 16:54 | 2020-01-05 18:20 | 86.42 | 1 | 1 | 85.05 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 832 SE.26 | CMI_NORMAL | NO | NO | NO | 859842 | 158940 | 102040 | 4736 | 1439 | 9.8914e-05 | 1.163e-06 | 85.05 | 1 | 310 | Customer | 22117 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2021
J2001.001343 | PD-01052020-00070 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3721 | 833721 | 2020-01-05 16:54 | 2020-01-05 18:37 | 102.62 | 1 | 1 | 102.6167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 7503 BROADWAY EXT. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167957 | 148165 | 5754 | 725 | 0.00011934 | 1.163e-06 | 102.6167 | 1 | 310 | Load | 85842 | Load | Tran3phWye | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2022
J2001.001347 | PD-01052020-00075 | SOUTHERN | MADILL | 5906:TISHOMINGO | TISHOMINGO_621 | 590621 | 2020-01-05 17:04 | 2020-01-05 20:45 | 220.82 | 1 | 2 | 215.0333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | TISHOMINGO | 105 S Chisholm | CMI_NORMAL | NO | NO | NO | 859842 | 77515 | 7201 | 967 | 916 | 0.00025008 | 1.163e-06 | 215.0333 | 1 | 310 | Customer | 304837 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2021
J2001.001348 | PD-01052020-00084 | SOUTHERN | MADILL | 5906:TISHOMINGO | TISHOMINGO_621 | 590621 | 2020-01-05 17:04 | 2020-01-05 20:49 | 224.82 | 2 | 3 | 430.0667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | TISHOMINGO | S BEAMS LN | CMI_NORMAL | NO | NO | NO | 859842 | 77515 | 7201 | 967 | 916 | 0.00050017 | 2.326e-06 | 215.0333 | 1 | 310 | Secondary | 16753 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2021
J2001.001358 | PD-01052020-00077 | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_623 | 550623 | 2020-01-05 17:53 | 2020-01-05 19:01 | 68.17 | 2 | 2 | 133.7333 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 23 | FUSE - PRIMARY | ARMSTRONG | 210 MAIN ST | CMI_NORMAL | NO | NO | NO | 859842 | 77515 | 15465 | 6729 | 1716 | 0.00015553 | 2.326e-06 | 66.8667 | 1 | 310 | Secondary | 10063 | Load | Tran1phOH | JUSTIN MARSHALL | 580-504-0986 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001360 | PD-01052020-00078 | NORTHEAST | MUSKOGEE | 3111:FIVE TRIBES | FIVE_TRIBES_1129 | 311129 | 2020-01-05 17:56 | 2020-01-05 19:18 | 82.35 | 1 | 2 | 80.2 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | MUSKOGEE | DAVIS PARK ADD | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859842 | 73899 | 33210 | 1679 | 864 | 9.3273e-05 | 1.163e-06 | 80.2 | 1 | 320 | Customer | 12318 | Load | Tran1phPad | CONTRACTOR 5 DAVID ELLIOT INC | 918-639-5055 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-05 | 2020 |  | #N/A
J2001.001361 | PD-01052020-00080 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2031 | 862031 | 2020-01-05 18:05 | 2020-01-05 19:07 | 61.7 | 1 | 1 | 13.3167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 832 SE.26 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 158943 | 102043 | 4736 | 1439 | 1.5487e-05 | 1.163e-06 | 13.3167 | 1 | 310 | Customer | 22117 | Load | Tran1phOH | SHANE DRAKE | 405-326-9052 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2021
J2001.001363 |  | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-05 18:16 | 2020-01-05 20:08 | 111.75 | 4 | 0 | 446.9629 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | MUSTANG | 418 W LINDEN DR | CMI_PLANNED | YES | NO | NO | 859842 | 128550 | 115828 | 18201 | 4430 | 0.00051982 | 4.652e-06 | 111.7407 | 1 | 0 | Load | 47700 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2022
J2001.001367 | PD-01052020-00081 | METRO NORTH | NORTH | 8209:CLASSEN | CLASSEN_961 | 820961 | 2020-01-05 18:30 | 2020-01-05 19:03 | 32.7 | 1 | 1 | 32.7 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1432 NW.2 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167962 | 148169 | 3877 | 866 | 3.803e-05 | 1.163e-06 | 32.7 | 1 | 310 | Customer | 22294 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001369 |  | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_524 | 510524 | 2020-01-05 18:34 | 2020-01-05 18:34 | 0 | 1434 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 228 C ST | CMI_MOMENTARY | YES | NO | NO | 859842 | 77521 | 23565 | 4769 | 1434 | 0 | 0.0016677 | 0 | 1 | 0 | Feeder | ARDMORE_524 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-05 | 2020 |  | OK - 2021
J2001.001371 | PD-01052020-00082 | METRO WEST | EL RENO | 8908:ROMAN NOSE | ROMAN_NOSE_847 | 890847 | 2020-01-05 18:37 | 2020-01-05 20:55 | 137.63 | 1 | 1 | 137.6333 | 22 | WIND | 17 | JUMPER | WATONGA | 1MN + 2-1/4ME WATONGA | CMI_NORMAL | NO | NO | NO | 859842 | 128550 | 12722 | 523 | 214 | 0.00016007 | 1.163e-06 | 137.6333 | 1 | 320 | Customer | 76025 | Load | Tran3phWye | MICHAEL T MAHEN | 405-210-6029 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2020
J2001.001374 |  | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_622 | 770622 | 2020-01-05 18:48 | 2020-01-05 19:10 | 21.97 | 1 | 1 | 21.9667 | 1 | CANCELLED | 57 | CANCELLED | BRISTOW | 30425 W Hwy 16 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 73901 | 40689 | 3777 | 2007 | 2.5547e-05 | 1.163e-06 | 21.9667 | 1 | 308 | Customer | 260860 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-05 | 2020 |  | #N/A
J2001.001372 |  | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_924 | 910924 | 2020-01-05 18:59 | 2020-01-05 19:15 | 15.92 | 1 | 1 | 15.9167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 1616 S.HOUSTON, E-S.16TH ST. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 82099 | 61123 | 5007 | 1723 | 1.8511e-05 | 1.163e-06 | 15.9167 | 1 | 310 | Customer | 5215 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-05 | 2020 |  | Ark - Series 3
J2001.001376 | PD-01052020-00085 | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2731 | 872731 | 2020-01-05 19:11 | 2020-01-05 19:51 | 40.33 | 1 | 2 | 40.3333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | 915 N.FLOOD AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 158943 | 56900 | 6452 | 1349 | 4.6908e-05 | 1.163e-06 | 40.3333 | 1 | 310 | Customer | 33793 | Load | TranOpenDelta | SHANE DRAKE | 405-326-9052 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001377 | PD-01052020-00086 | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4024 | 914024 | 2020-01-05 19:20 | 2020-01-05 21:11 | 110.63 | 1 | 2 | 110.6333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 2217 S.SAVANNAH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 82099 | 61123 | 4755 | 1159 | 0.00012867 | 1.163e-06 | 110.6333 | 1 | 310 | Customer | 5504 | Load | Tran1phOH | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-05 | 2020 |  | Ark - Series 2
J2001.001402 | PD-01052020-00093 | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9869 | 839869 | 2020-01-05 19:35 | 2020-01-05 23:48 | 253.65 | 15 | 23 | 3355.5 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | 17380 N. PENN | CMI_NORMAL | NO | NO | NO | 859842 | 167962 | 148169 | 10648 | 2994 | 0.0039025 | 1.7445e-05 | 223.7 | 1 | 310 | Mainline | 161213 | Fuse | FuseRiser | BRIAN E WHITE | 405-642-7075 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2022
J2001.001384 |  | METRO EAST | CHANDLER | 7119:WARWICK | WARWICK_1941 | 711941 | 2020-01-05 19:37 | 2020-01-05 19:57 | 20 | 1 | 1 | 20 | 1 | CANCELLED | 57 | CANCELLED | WELLSTON | SEVENTH + DOGWOOD-WELLSTON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 114196 | 7451 | 2414 | 1459 | 2.326e-05 | 1.163e-06 | 20 | 1 | 308 | Customer | 2475 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2021
J2001.001385 |  | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3421 | 843421 | 2020-01-05 20:00 | 2020-01-05 20:12 | 11.7 | 1 | 1 | 11.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1628 MEYERS PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167962 | 148169 | 1224 | 498 | 1.3607e-05 | 1.163e-06 | 11.7 | 1 | 310 | Customer | 15050 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-05 | 2020 |  | #N/A
J2001.001387 |  | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2731 | 872731 | 2020-01-05 20:21 | 2020-01-05 20:25 | 3.55 | 1 | 1 | 3.55 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 915 N.FLOOD AV | CMI_MOMENTARY | YES | NO | NO | 859842 | 158943 | 56900 | 6452 | 1349 | 4.1287e-06 | 1.163e-06 | 3.55 | 1 | 315 | Customer | 33793 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | #N/A
J2001.001389 |  | ARKANSAS | POTEAU | 3505:POTEAU | POTEAU_524 | 350524 | 2020-01-05 20:40 | 2020-01-05 20:59 | 19.1 | 1 | 1 | 19.1 | 1 | CANCELLED | 57 | CANCELLED | POTEAU | .5MS BOWLING ALLEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 82099 | 13450 | 2295 | 721 | 2.2213e-05 | 1.163e-06 | 19.1 | 1 | 308 | Customer | 15766 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-05 | 2020 |  | #N/A
J2001.001391 |  | SOUTHERN | ADA | 5809:VANOSS | VANOSS_922 | 580922 | 2020-01-05 21:00 | 2020-01-05 21:19 | 19.02 | 1 | 1 | 19.0167 | 1 | CANCELLED | 57 | CANCELLED | STRATFORD | 510 GARVIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 77521 | 11503 | 978 | 978 | 2.2116e-05 | 1.163e-06 | 19.0167 | 1 | 308 | Customer | 2227 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2021
J2001.001392 |  | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1424 | 311424 | 2020-01-05 21:08 | 2020-01-05 21:25 | 17.23 | 1 | 1 | 17.2333 | 1 | CANCELLED | 57 | CANCELLED | MUSKOGEE | 3015 ELGIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 73901 | 33212 | 4559 | 796 | 2.0042e-05 | 1.163e-06 | 17.2333 | 1 | 308 | Customer | 2241 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-05 | 2020 |  | OK - 2020
J2001.001393 | PD-01052020-00100 | SOUTHERN | MADILL | 5906:TISHOMINGO | TISHOMINGO_621 | 590621 | 2020-01-05 21:32 | 2020-01-05 23:02 | 90.25 | 1 | 1 | 90.25 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | TISHOMINGO | 602 E.21ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 77521 | 7201 | 967 | 916 | 0.00010496 | 1.163e-06 | 90.25 | 1 | 320 | Customer | 3198 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2021
J2001.001396 |  | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_646 | 730646 | 2020-01-05 21:44 | 2020-01-05 22:14 | 30.33 | 1 | 1 | 30.3333 | 1 | CANCELLED | 57 | CANCELLED | EARLSBORO | 310 N LAYTON AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 114196 | 13583 | 4055 | 282 | 3.5278e-05 | 1.163e-06 | 30.3333 | 1 | 308 | Customer | 7477 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-05 | 2020 |  | OK - 2021
J2001.001401 |  | NORTHEAST | SAPULPA | 7608:TIGER CREEK | TIGER_CREEK_821 | 760821 | 2020-01-05 22:27 | 2020-01-05 22:44 | 17.07 | 1 | 1 | 17.0667 | 1 | CANCELLED | 57 | CANCELLED | DRUMRIGHT | 423.5 E.BROADWAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 73901 | 40689 | 773 | 344 | 1.9849e-05 | 1.163e-06 | 17.0667 | 1 | 308 | Customer | 40917 | Load | TranOH3phDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-05 | 2020 |  | #N/A
J2001.001408 |  | METRO NORTH | GUTHRIE | 8819:LIBERTY LAKE | LIBERTY_LAKE_1921 | 881921 | 2020-01-06 00:14 | 2020-01-06 00:33 | 18.45 | 1 | 1 | 18.45 | 1 | CANCELLED | 57 | CANCELLED | GUTHRIE | L8BF GREEN ACRES II | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167962 | 19793 | 3347 | 1523 | 2.1457e-05 | 1.163e-06 | 18.45 | 1 | 308 | Customer | 43995 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001416 |  | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1421 | 911421 | 2020-01-06 02:48 | 2020-01-06 03:11 | 22.38 | 1 | 1 | 22.3833 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 4409 VIRGINIA AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 82099 | 61123 | 4735 | 1746 | 2.6032e-05 | 1.163e-06 | 22.3833 | 1 | 308 | Customer | 11131 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-06 | 2020 |  | Ark - Series 1
J2001.001417 |  | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_623 | 880623 | 2020-01-06 02:51 | 2020-01-06 03:10 | 19.32 | 1 | 1 | 19.3167 | 1 | CANCELLED | 57 | CANCELLED | GUTHRIE | L3 B1 CANYON HEIGHTS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167962 | 19793 | 5155 | 1413 | 2.2465e-05 | 1.163e-06 | 19.3167 | 1 | 308 | Customer | 82640 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001418 |  | METRO EAST | SEMINOLE | 7312:JUMPER CREEK | JUMPER_CREEK_1227 | 731227 | 2020-01-06 03:16 | 2020-01-06 03:33 | 17.57 | 1 | 1 | 17.5667 | 1 | CANCELLED | 57 | CANCELLED | KONAWA | 420 W.4TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 114196 | 13583 | 1215 | 884 | 2.043e-05 | 1.163e-06 | 17.5667 | 1 | 308 | Customer | 8860 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | OK - 2021
J2001.001424 |  | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_924 | 910924 | 2020-01-06 04:06 | 2020-01-06 04:28 | 22.47 | 1 | 1 | 22.4667 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 60 HAVEN-HILL DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 82099 | 61123 | 5007 | 1723 | 2.6129e-05 | 1.163e-06 | 22.4667 | 1 | 308 | Customer | 8341 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | Ark - Series 3
J2001.001428 | PD-01062020-00007 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6965 | 846965 | 2020-01-06 04:53 | 2020-01-06 08:37 | 224.02 | 1 | 1 | 220.5333 | 13 | PREMATURE FAILURE | 2 | TRANSFORMER OH | OKLAHOMA CITY | 301 NW 132nd St. | CMI_NORMAL | NO | NO | NO | 859842 | 167962 | 148169 | 7713 | 46 | 0.00025648 | 1.163e-06 | 220.5333 | 1 | 310 | Load | 246569 | Load | Tran1phOH | BEAU S HUDSON | 405-306-8284 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001432 |  | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_622 | 770622 | 2020-01-06 05:27 | 2020-01-06 05:46 | 18.93 | 1 | 1 | 15.9 | 1 | CANCELLED | 57 | CANCELLED | BRISTOW | 30425 W Hwy 16 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 73901 | 40689 | 3777 | 2007 | 1.8492e-05 | 1.163e-06 | 15.9 | 1 | 308 | Customer | 260860 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001433 | PD-01062020-00009 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-01-06 05:34 | 2020-01-06 07:03 | 89.17 | 7 | 4 | 225.4 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 10432 N.MCKINLEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167962 | 148169 | 8780 | 1948 | 0.00026214 | 8.141e-06 | 32.2 | 1 | 308 | Load | 19145 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2021
J2001.001436 |  | NORTHEAST | SAPULPA | 3220:KELLYVILLE | KELLYVILLE_2024 | 322024 | 2020-01-06 05:48 | 2020-01-06 06:06 | 17.68 | 1 | 1 | 17.6833 | 1 | CANCELLED | 57 | CANCELLED | SAPULPA | 1/8E REESE HILL RD ON HWY33 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 73901 | 40689 | 2550 | 1580 | 2.0566e-05 | 1.163e-06 | 17.6833 | 1 | 308 | Load | 18305 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2020
J2001.001438 |  | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_622 | 770622 | 2020-01-06 05:56 | 2020-01-06 06:20 | 24.1 | 1 | 1 | 15.8333 | 1 | CANCELLED | 57 | CANCELLED | BRISTOW | 30425 W Hwy 16 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 73901 | 40689 | 3777 | 2007 | 1.8414e-05 | 1.163e-06 | 15.8333 | 1 | 308 | Customer | 260860 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001441 | PD-01062020-00010 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-01-06 06:21 | 2020-01-06 06:58 | 36.78 | 1 | 1 | 36.7833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | THE VILLAGE | NW 103RD + MCKINLEY AVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167962 | 148169 | 8780 | 1948 | 4.2779e-05 | 1.163e-06 | 36.7833 | 1 | 310 | Customer | 19147 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2021
J2001.001444 |  | NORTHWEST | ENID | 4135:SO 4TH ST | SO_4TH_ST_3522 | 413522 | 2020-01-06 06:24 | 2020-01-06 06:42 | 18.27 | 1 | 1 | 18.2667 | 1 | CANCELLED | 57 | CANCELLED | ENID | 1305 HITE BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 53483 | 37557 | 3094 | 1483 | 2.1244e-05 | 1.163e-06 | 18.2667 | 1 | 308 | Customer | 4457 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001443 |  | NORTHEAST | SAPULPA | 7605:DRUMRIGHT | DRUMRIGHT_541 | 760541 | 2020-01-06 06:36 | 2020-01-06 07:22 | 46.22 | 2 | 0 | 41.2667 | 20 | WILDFIRE | 34 | CONDUCTOR SECONDARY - OH | SHAMROCK | 3BLK E HY16 N OF 2ND ST. | CMI_NORMAL | NO | NO | NO | 859842 | 73901 | 40689 | 1691 | 322 | 4.7993e-05 | 2.326e-06 | 20.6333 | 1 | 0 | Load | 48054 | Load | Tran1phOH | Crew | [6 empty] | Other | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001453 | PD-01062020-00030 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2133 | 822133 | 2020-01-06 07:58 | 2020-01-06 08:36 | 37.73 | 1 | 2 | 37.7333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 315 S.MERIDIAN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167962 | 148169 | 9234 | 236 | 4.3884e-05 | 1.163e-06 | 37.7333 | 1 | 310 | Load | 50096 | Load | Tran3phPadWye | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2022
J2001.001456 | PD-01062020-00045 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1122 | 511122 | 2020-01-06 08:08 | 2020-01-06 09:16 | 67.77 | 1 | 1 | 67.7667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | DICKSON | HWY 70 8.2E 1.55 | CMI_NORMAL | NO | NO | NO | 859842 | 77521 | 23565 | 2207 | 1206 | 7.8813e-05 | 1.163e-06 | 67.7667 | 1 | 310 | Load | 18599 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001457 | PD-01062020-00051 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6924 | 846924 | 2020-01-06 08:10 | 2020-01-06 08:41 | 30.7 | 1 | 1 | 30.7 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3/8MS-MEMORIAL + EASTERN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167962 | 148169 | 7713 | 1143 | 3.5704e-05 | 1.163e-06 | 30.7 | 1 | 310 | Customer | 75412 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001461 | PD-01062020-00055 | METRO WEST | WEST | 8157:MACARTHUR | MACARTHUR_5722 | 815722 | 2020-01-06 08:17 | 2020-01-06 10:09 | 112.43 | 1 | 1 | 112.4333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4316 NEWCASTLE BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 128550 | 115828 | 1853 | 347 | 0.00013076 | 1.163e-06 | 112.4333 | 1 | 320 | Customer | 246990 | Load | TranOpenDelta | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001467 | PD-01062020-00065 | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2722 | 872722 | 2020-01-06 08:23 | 2020-01-06 09:34 | 70.57 | 18 | 7 | 1270.2 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | NORMAN | 225 WOODCREST DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 158943 | 56900 | 6452 | 1361 | 0.0014772 | 2.0934e-05 | 70.5667 | 1 | 310 | Load | 36917 | Load | Tran1phPad | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001463 |  | METRO EAST | SHAWNEE | 7407:REMINGTON | REMINGTON 21 | 740721 | 2020-01-06 08:25 | 2020-01-06 09:42 | 77.73 | 1 | 1 | 24.0167 | 4 | DETERIORATION | 2 | TRANSFORMER OH | EARLSBORO | 1/4MS OF HWY3 ON KINGS RD ES | CMI_PLANNED | YES | NO | NO | 859842 | 114196 | 22067 | 3658 | 2014 | 2.7931e-05 | 1.163e-06 | 24.0167 | 1 | 308 | Load | 186474 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | OK - 2021
J2001.001464 | PD-01062020-00091 | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2731 | 872731 | 2020-01-06 08:31 | 2020-01-06 10:07 | 96.18 | 1 | 1 | 96.1833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 915 N.FLOOD AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 158943 | 56900 | 6452 | 1349 | 0.00011186 | 1.163e-06 | 96.1833 | 1 | 310 | Customer | 33793 | Load | TranOpenDelta | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001468 | PD-01062020-00098 | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_529 | 320529 | 2020-01-06 08:37 | 2020-01-06 09:42 | 64.98 | 1 | 1 | 64.9833 | 12 | POOR CONNECTION | 50 | CONNECTOR | SAPULPA | 1021 E.THOMPSON | CMI_NORMAL | NO | NO | NO | 859842 | 73901 | 40689 | 3833 | 510 | 7.5576e-05 | 1.163e-06 | 64.9833 | 1 | 310 | Customer | 40371 | Load | Tran1phOH | CGI ADMIN | 918-261-6802 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | OK - 2022
J2001.001469 | PD-01062020-00085 | NORTHEAST | SAPULPA | 3216:BEELINE | BEELINE_1629 | 321629 | 2020-01-06 08:38 | 2020-01-06 10:17 | 98.77 | 1 | 1 | 98.7667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | KIEFER | 3400 W 151ST ST. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 73901 | 40689 | 5554 | 1250 | 0.00011487 | 1.163e-06 | 98.7667 | 1 | 320 | Customer | 309189 | Load | Tran3phPadWye | PHIL STICKLER | 918-991-1321 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001474 | PD-01062020-00100 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2124 | 822124 | 2020-01-06 08:43 | 2020-01-06 10:26 | 102.57 | 1 | 2 | 102.5667 | 13 | PREMATURE FAILURE | 23 | FUSE - PRIMARY | OKLAHOMA CITY | ANN ARBOR / RENO | CMI_NORMAL | NO | NO | NO | 859842 | 167962 | 148169 | 9234 | 423 | 0.00011929 | 1.163e-06 | 102.5667 | 1 | 310 | Load | 70249 | Load | Tran3phPadWye | STEVEN GILES | 405-227-2802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2021
J2001.001475 |  | METRO EAST | SEMINOLE | 7506:SASAKWA | SASAKWA 29 | 750629 | 2020-01-06 08:46 | 2020-01-06 08:52 | 6.47 | 1 | 1 | 6.4667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SASAKWA | S OF FLORENCE ON PINE SASAKWA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 114196 | 13583 | 300 | 228 | 7.5208e-06 | 1.163e-06 | 6.4667 | 1 | 310 | Customer | 4088 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001480 | PD-01062020-00099 | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1722 | 911722 | 2020-01-06 08:49 | 2020-01-06 10:08 | 79.07 | 1 | 1 | 79.0667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 8405 HWY 59T | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 82099 | 61123 | 4235 | 1473 | 9.1955e-05 | 1.163e-06 | 79.0667 | 1 | 310 | Customer | 2002 | Load | Tran1phOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-06 | 2020 |  | #N/A
J2001.001481 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5132 | 815132 | 2020-01-06 08:59 | 2020-01-06 09:08 | 9.65 | 1 | 1 | 9.65 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7504 S.SHERWOOD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 158943 | 102043 | 13933 | 2003 | 1.1223e-05 | 1.163e-06 | 9.65 | 1 | 320 | Customer | 71054 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001484 | PD-01062020-00116 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2625 | 862625 | 2020-01-06 09:02 | 2020-01-06 10:51 | 109.12 | 7 | 9 | 749.7 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | DEL CITY | 1309 MALLARD DR | CMI_NORMAL | NO | NO | NO | 859842 | 158943 | 102043 | 7408 | 1267 | 0.0008719 | 8.141e-06 | 107.1 | 1 | 310 | Load | 17189 | Load | Tran1phOH | ADAM CLARK | 580-310-8924 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2022
J2001.001485 | PD-01062020-00138 | METRO WEST | WEST | 8359:YUKON | YUKON_5922 | 835922 | 2020-01-06 09:05 | 2020-01-06 09:42 | 37.42 | 1 | 1 | 37.4167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | YUKON | 400 S.RANCHWOOD BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 128550 | 115828 | 6411 | 1634 | 4.3516e-05 | 1.163e-06 | 37.4167 | 1 | 310 | Customer | 38781 | Load | Tran1phPad | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001487 |  | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3222 | 813222 | 2020-01-06 09:08 | 2020-01-06 09:28 | 20.15 | 9 | 6 | 160.65 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 6408 S.CNTRY-CLB DR | CMI_PLANNED | YES | NO | NO | 859842 | 158943 | 102043 | 7592 | 1482 | 0.00018684 | 1.0467e-05 | 17.85 | 1 | 308 | Load | 12219 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001489 | PD-01062020-00129 | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_622 | 580622 | 2020-01-06 09:11 | 2020-01-06 14:35 | 323.77 | 1 | 2 | 320.1833 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | ADA | 2216 WOODLAND DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859842 | 77521 | 11503 | 2517 | 779 | 0.00037237 | 1.163e-06 | 320.1833 | 1 | 310 | Customer | 7276 | Load | Tran1phOH | JOE LOFTIS | 918-884-5349 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001490 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5921 | 835921 | 2020-01-06 09:14 | 2020-01-06 11:57 | 163.3 | 6 | 5 | 189.2 | 4 | DETERIORATION | 2 | TRANSFORMER OH | YUKON | 857 INDUSTRIAL BL | CMI_PLANNED | YES | NO | NO | 859842 | 128550 | 115828 | 6411 | 1803 | 0.00022004 | 6.978e-06 | 31.5333 | 1 | 308 | Load | 65114 | Load | TranOpenDelta | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001492 | PD-01062020-00150 | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1422 | 911422 | 2020-01-06 09:19 | 2020-01-06 09:55 | 36.1 | 1 | 1 | 36.1 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 4702 BERKLEY AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 82099 | 61123 | 4735 | 1952 | 4.1984e-05 | 1.163e-06 | 36.1 | 1 | 310 | Customer | 11563 | Load | Tran1phOH | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-06 | 2020 |  | Ark - Series 1
J2001.001498 |  | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3222 | 813222 | 2020-01-06 09:31 | 2020-01-06 09:36 | 5.67 | 2 | 2 | 11.3333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 6408 S.CNTRY-CLB DR | CMI_PLANNED | YES | NO | NO | 859842 | 158943 | 102043 | 7592 | 1482 | 1.3181e-05 | 2.326e-06 | 5.6667 | 1 | 310 | Secondary | 12219 | Load | TranOpenDelta | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001497 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3821 | 913821 | 2020-01-06 09:32 | 2020-01-06 13:13 | 220.93 | 2 | 1 | 396.9333 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 1023 ROGERS AV | CMI_PLANNED | YES | NO | NO | 859842 | 82099 | 61123 | 2926 | 209 | 0.00046164 | 2.326e-06 | 198.4667 | 1 | 308 | Load | 2027 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-06 | 2020 |  | Ark - Series 2
J2001.001513 | PD-01062020-00168 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3924 | 833924 | 2020-01-06 09:36 | 2020-01-06 12:28 | 172.45 | 88 | 45 | 15012.8 | 4 | DETERIORATION | 17 | JUMPER | OKLAHOMA CITY | NW.63 + PORTLAND | CMI_NORMAL | NO | NO | NO | 859842 | 167962 | 148169 | 7846 | 795 | 0.01746 | 0.00010234 | 170.6 | 1 | 310 | Mainline | 9112 | Fuse | FuseOH | GARY D FRANKLIN | 405-637-2002 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2022
J2001.001510 | PD-01062020-00170 | METRO EAST | SEMINOLE | 7505:WEWOKA | WEWOKA 21 | 750521 | 2020-01-06 09:42 | 2020-01-06 11:05 | 83.1 | 1 | 1 | 83.1 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | WEWOKA | 1.5 M W WEW | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 114196 | 13583 | 2467 | 1281 | 9.6646e-05 | 1.163e-06 | 83.1 | 1 | 310 | Customer | 495 | Load | Tran1phOH | DELBERT HISAW | 405-683-1721 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | OK - 2021
J2001.001515 |  | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3926 | 833926 | 2020-01-06 09:44 | 2020-01-06 12:32 | 167.98 | 1 | 1 | 162.6167 | 4 | DETERIORATION | 17 | JUMPER | OKLAHOMA CITY | 4032 FONTANA | CMI_NORMAL | NO | NO | NO | 859842 | 167962 | 148169 | 7846 | 1360 | 0.00018912 | 1.163e-06 | 162.6167 | 1 | 310 | Customer | 69346 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2022
J2001.001521 |  | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1523 | 811523 | 2020-01-06 09:52 | 2020-01-06 10:10 | 18.07 | 1 | 1 | 18.0667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1700 SW.15 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 158943 | 102043 | 6052 | 804 | 2.1012e-05 | 1.163e-06 | 18.0667 | 1 | 310 | Customer | 727 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | OK - 2022
J2001.001524 |  | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2223 | 882223 | 2020-01-06 09:54 | 2020-01-06 16:48 | 413.45 | 14 | 3 | 1489.1333 | 4 | DETERIORATION | 12 | POLE | EDMOND | .1ME COLTRAN + NE.206 | CMI_PLANNED | YES | NO | NO | 859842 | 167962 | 19793 | 5383 | 1202 | 0.0017319 | 1.6282e-05 | 106.3667 | 1 | 310 | Tap | 6376 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001527 | PD-01062020-00182 | METRO EAST | SHAWNEE | 7411:DALE | DALE_1129 | 741129 | 2020-01-06 09:57 | 2020-01-06 11:13 | 76.13 | 1 | 1 | 76.1333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | BETHEL ACRES | NW CNR OF HARDESTY + 102 | CMI_NORMAL | NO | NO | NO | 859842 | 114196 | 22067 | 966 | 965 | 8.8543e-05 | 1.163e-06 | 76.1333 | 1 | 320 | Load | 19319 | Load | TranOH3phDelta | BRYAN K TATUM | 405-659-0746 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2021
J2001.001528 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5921 | 835921 | 2020-01-06 10:00 | 2020-01-06 11:57 | 117.53 | 10 | 8 | 280.8333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | YUKON | 865 INDUSTRIAL BL | CMI_PLANNED | YES | NO | NO | 859842 | 128550 | 115828 | 6411 | 1803 | 0.00032661 | 1.163e-05 | 28.0833 | 1 | 308 | Load | 65115 | Load | TranOpenDelta | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001533 | PD-01062020-00188 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-01-06 10:00 | 2020-01-06 10:59 | 58.88 | 15 | 14 | 820.25 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2717 SW.42 | CMI_NORMAL | NO | NO | NO | 859842 | 158943 | 102043 | 7592 | 2452 | 0.00095395 | 1.7445e-05 | 54.6833 | 1 | 310 | Load | 4424 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001530 |  | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-01-06 10:00 | 2020-01-06 10:00 | 0 | 279 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | SW 43RD AND BARNES | CMI_MOMENTARY | YES | NO | NO | 859842 | 158943 | 102043 | 7592 | 2452 | 0 | 0.00032448 | 0 | 1 | 0 | Mainline | 336920 | Recloser | Rec3phElectronic | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001534 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-06 10:07 | 2020-01-06 12:07 | 119.63 | 1 | 0 | 119.6452 | 4 | DETERIORATION | 12 | POLE | COAL HILL | COAL HILL AR | CMI_PLANNED | YES | NO | NO | 859842 | 82099 | 7526 | 1501 | 1198 | 0.00013915 | 1.163e-06 | 119.6452 | 1 | 0 | Load | 598 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-06 | 2020 |  | Ark - Series 2
J2001.001539 |  | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3222 | 813222 | 2020-01-06 10:11 | 2020-01-06 11:23 | 72.17 | 8 | 8 | 505.4667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 1436 SW.63 | CMI_PLANNED | YES | NO | NO | 859842 | 158943 | 102043 | 7592 | 1482 | 0.00058786 | 9.304e-06 | 63.1833 | 1 | 308 | Load | 17801 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001541 | PD-01062020-00196 | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_924 | 910924 | 2020-01-06 10:12 | 2020-01-06 11:10 | 57.68 | 1 | 1 | 57.6833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 2817 S.14 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 82099 | 61123 | 5007 | 1723 | 6.7086e-05 | 1.163e-06 | 57.6833 | 1 | 310 | Customer | 4461 | Load | Tran1phOH | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | Ark - Series 3
J2001.001542 |  | METRO EAST | EAST | 8542:RENO | RENO_4231 | 854231 | 2020-01-06 10:14 | 2020-01-06 10:18 | 4.35 | 1 | 1 | 4.35 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DEL CITY | 47 EASTBROOK DR | CMI_MOMENTARY | YES | NO | NO | 859842 | 114196 | 71095 | 5209 | 956 | 5.0591e-06 | 1.163e-06 | 4.35 | 1 | 310 | Customer | 26862 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2021
J2001.001554 | PD-01062020-00225 | METRO NORTH | NORTH | 8430:REMINGTON PARK | REMINGTON_PARK_3022 | 843022 | 2020-01-06 10:27 | 2020-01-06 11:58 | 90.75 | 7 | 5 | 601.5333 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | OKLAHOMA CITY | KELLY + NE.65 | CMI_NORMAL | NO | NO | NO | 859842 | 167962 | 148169 | 846 | 669 | 0.00069959 | 8.141e-06 | 85.9333 | 1 | 310 | Tap | 19482 | Fuse | FuseOH | ADAM COX | 405-328-8938 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001553 | PD-01062020-00212 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_723 | 870723 | 2020-01-06 10:30 | 2020-01-06 12:56 | 145.9 | 1 | 1 | 147.9511 | 5 | ELECTRICAL TRACKING | 20 | FUSE BARREL | NORMAN | .5 M West of 24th on Imhoff | CMI_NORMAL | NO | NO | NO | 859842 | 158943 | 56900 | 11826 | 2042 | 0.00017207 | 1.163e-06 | 147.9511 | 1 | 310 | Load | 83153 | Load | Tran3phPadWye | MARK A PALMORE | 405-512-1933 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001557 | PD-01062020-00236 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-01-06 10:34 | 2020-01-06 13:06 | 152.28 | 1 | 1 | 152.2833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 915 NW.30 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167962 | 148169 | 11095 | 2334 | 0.00017711 | 1.163e-06 | 152.2833 | 1 | 310 | Customer | 12414 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2020
J2001.001559 | PD-01062020-00221 | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2223 | 882223 | 2020-01-06 10:36 | 2020-01-06 14:50 | 254.52 | 1 | 1 | 65.1 | 1 | CANCELLED | 57 | CANCELLED | EDMOND | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 0 | 0 | 0 | 0 | 7.5712e-05 | 1.163e-06 | 65.1 | 1 | 310 | Customer |  | 0 | 0 | [6 empty] | 06/02/2020 note from burchamc. Reference J2001.001559 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Emailed Brent Miller with blank transformer and circuit #'s. Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001564 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-01-06 10:48 | 2020-01-06 10:48 | 0.03 | 1958 | 0 | 65.2667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 4431 NW 10TH ST | CMI_MOMENTARY | YES | NO | NO | 859842 | 167962 | 148169 | 9234 | 1940 | 7.5905e-05 | 0.0022772 | 0.033333 | 1 | 0 | Feeder | MERIDIAN_2128 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-06 | 2020 |  | OK - 2021
J2001.001567 | PD-01062020-00241 | METRO WEST | WEST | 8335:BETHANY | BETHANY_3529 | 833529 | 2020-01-06 10:53 | 2020-01-06 12:24 | 90.98 | 1 | 1 | 90.9833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 4300 NW.39 EXPRESSWAY | CMI_NORMAL | NO | NO | NO | 859842 | 128550 | 115828 | 7861 | 2015 | 0.00010581 | 1.163e-06 | 90.9833 | 1 | 320 | Customer | 1226 | Load | TranOpenDelta | ADAM COX | 405-328-8938 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001570 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1024 | 541024 | 2020-01-06 10:58 | 2020-01-06 11:10 | 12.07 | 1 | 1 | 12.0667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MADILL | 307.5 NO 2ND ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 77521 | 7201 | 2379 | 661 | 1.4034e-05 | 1.163e-06 | 12.0667 | 1 | 310 | Customer | 6960 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001581 | PD-01062020-00315 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-01-06 10:58 | 2020-01-06 12:48 | 109.98 | 3 | 3 | 323.2 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 4912 NW.18 | CMI_NORMAL | NO | NO | NO | 859842 | 167962 | 148169 | 9234 | 1940 | 0.00037588 | 3.489e-06 | 107.7333 | 1 | 310 | Secondary | 27315 | Load | Tran1phOH | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2021
J2001.001572 | PD-01062020-00249 | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_631 | 730631 | 2020-01-06 11:00 | 2020-01-06 12:24 | 84.25 | 1 | 1 | 84.25 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | SEMINOLE | MORNING GLORY LN LAKEWOOD EST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 114196 | 13583 | 4055 | 665 | 9.7983e-05 | 1.163e-06 | 84.25 | 1 | 310 | Customer | 193041 | Load | Tran1phPad | RANDY HOPPER | 405-534-6402 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001576 | PD-01062020-00277 | NORTHEAST | SAPULPA | 3216:BEELINE | BEELINE_1628 | 321628 | 2020-01-06 11:08 | 2020-01-06 12:00 | 51.83 | 1 | 1 | 20.2333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | GLENPOOL | 1/4S 126, ES HWY 75, 1/8ME | CMI_NORMAL | NO | NO | NO | 859842 | 73901 | 40689 | 5554 | 1439 | 2.3531e-05 | 1.163e-06 | 20.2333 | 1 | 320 | Load | 41689 | Load | Tran3phWye | PHIL STICKLER | 918-991-1321 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001577 | PD-01062020-00327 | METRO NORTH | NORTH | 8506:PARK PLACE | PARK_PLACE_623 | 850623 | 2020-01-06 11:09 | 2020-01-06 13:40 | 151.15 | 1 | 1 | 151.15 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 725 NE.14 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167962 | 148169 | 830 | 266 | 0.00017579 | 1.163e-06 | 151.15 | 1 | 310 | Customer | 12722 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001583 | PD-01062020-00280 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-01-06 11:18 | 2020-01-06 12:20 | 61.67 | 3 | 3 | 179.3 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2408 SW 51 | CMI_NORMAL | NO | NO | NO | 859842 | 158943 | 102043 | 7592 | 2452 | 0.00020853 | 3.489e-06 | 59.7667 | 1 | 310 | Secondary | 11376 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001587 | PD-01062020-00289 | NORTHEAST | MUSKOGEE | 3312:CHECOTAH | CHECOTAH 22 | 331222 | 2020-01-06 11:26 | 2020-01-06 12:37 | 70.98 | 1 | 2 | 70.9833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | CHECOTAH | ROCK POINT | CMI_NORMAL | NO | NO | NO | 859842 | 73901 | 33212 | 2882 | 1528 | 8.2554e-05 | 1.163e-06 | 70.9833 | 1 | 310 | Customer | 13171 | Load | Tran1phOH | NICHOLAS SELVIDGE | 918-652-1986 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | OK - 2020
J2001.001604 | PD-01062020-00299 | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1621 | 581621 | 2020-01-06 11:33 | 2020-01-06 13:45 | 132.5 | 1 | 2 | 128.4333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ADA | 1230 N.CHERRY | CMI_NORMAL | NO | NO | NO | 859842 | 77521 | 11503 | 3457 | 1807 | 0.00014937 | 1.163e-06 | 128.4333 | 1 | 310 | Load | 15321 | Load | Tran1phOH | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001602 | PD-01062020-00298 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_526 | 510526 | 2020-01-06 11:39 | 2020-01-06 12:31 | 51.95 | 6 | 4 | 295.9 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ARDMORE | 310 8 NW. | CMI_NORMAL | NO | NO | NO | 859842 | 77521 | 23565 | 4769 | 1619 | 0.00034413 | 6.978e-06 | 49.3167 | 1 | 310 | Load | 1073 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | OK - 2020
J2001.001601 |  | METRO NORTH | GUTHRIE | 8819:LIBERTY LAKE | LIBERTY_LAKE_1923 | 881923 | 2020-01-06 11:42 | 2020-01-06 12:57 | 75.08 | 19 | 4 | 755.25 | 29 | TREES : GROW IN | 37 | CONDUCTOR PRIMARY - OH | EDMOND | .3MS SMPSN .2MWEASTERN | CMI_PLANNED | YES | NO | NO | 859842 | 167962 | 19793 | 3347 | 1824 | 0.00087836 | 2.2097e-05 | 39.75 | 1 | 310 | Tap | 7424 | Fuse | FuseOH | Crew | [6 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001603 |  | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1523 | 811523 | 2020-01-06 11:44 | 2020-01-06 11:51 | 7.37 | 1 | 1 | 7.3667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1700 SW.15 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 158943 | 102043 | 6052 | 804 | 8.5675e-06 | 1.163e-06 | 7.3667 | 1 | 310 | Customer | 727 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | OK - 2022
J2001.001605 |  | METRO NORTH | GUTHRIE | 8819:LIBERTY LAKE | LIBERTY_LAKE_1923 | 881923 | 2020-01-06 11:45 | 2020-01-06 12:57 | 71.43 | 16 | 5 | 582.6667 | 29 | TREES : GROW IN | 37 | CONDUCTOR PRIMARY - OH | GUTHRIE | 1/4MS SMPSN + EASTERN | CMI_PLANNED | YES | NO | NO | 859842 | 167962 | 19793 | 3347 | 1824 | 0.00067764 | 1.8608e-05 | 36.4167 | 1 | 310 | Mainline | 7422 | Fuse | FuseOH | Crew | [6 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001608 | PD-01062020-00306 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6121 | 836121 | 2020-01-06 11:46 | 2020-01-06 12:53 | 66.85 | 11 | 10 | 652.4833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 509 NW.34 | CMI_NORMAL | NO | NO | NO | 859842 | 167962 | 148169 | 11095 | 1637 | 0.00075884 | 1.2793e-05 | 59.3167 | 1 | 310 | Load | 15354 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2021
J2001.001610 | PD-01062020-00317 | METRO WEST | WEST | 8157:MACARTHUR | MACARTHUR_5724 | 815724 | 2020-01-06 11:51 | 2020-01-06 13:48 | 117.32 | 1 | 1 | 117.3167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2400 S.MACARTHUR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 128550 | 115828 | 1853 | 1252 | 0.00013644 | 1.163e-06 | 117.3167 | 1 | 310 | Customer | 38822 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001626 |  | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_522 | 560522 | 2020-01-06 12:29 | 2020-01-06 13:58 | 89.15 | 2 | 0 | 156.5833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | 0 | 3.5M NW PAULS VALLEY ON SH 19 | CMI_PLANNED | YES | NO | NO | 859842 | 77521 | 6195 | 2450 | 825 | 0.00018211 | 2.326e-06 | 78.2917 | 1 | 0 | Load | 19856 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | OK - 2022
J2001.001631 |  | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1722 | 911722 | 2020-01-06 12:30 | 2020-01-06 14:33 | 123.12 | 2 | 1 | 526.1 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 9212 ROYALRIDGE DR | CMI_PLANNED | YES | NO | NO | 859842 | 82099 | 61123 | 4235 | 1473 | 0.00061186 | 2.326e-06 | 263.05 | 1 | 308 | Load | 13242 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-06 | 2020 |  | #N/A
J2001.001636 | PD-01062020-00353 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2229 | 852229 | 2020-01-06 12:34 | 2020-01-06 14:34 | 120.2 | 1 | 2 | 118.8167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | HARRAH | 20001 NE.23 | CMI_NORMAL | NO | NO | NO | 859842 | 114196 | 71095 | 11613 | 1386 | 0.00013818 | 1.163e-06 | 118.8167 | 1 | 310 | Load | 61713 | Load | Tran1phOH | ADAM CLARK | 580-310-8924 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001630 |  | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-01-06 12:35 | 2020-01-06 12:47 | 11.7 | 1 | 1 | 11.7 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 2408 SW 51 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 158943 | 102043 | 7592 | 2452 | 1.3607e-05 | 1.163e-06 | 11.7 | 1 | 310 | Customer | 11376 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001633 | PD-01062020-00359 | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1371 | 831371 | 2020-01-06 12:41 | 2020-01-06 14:24 | 103.38 | 1 | 1 | 103.3833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 11207 Coachman's Way | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 128550 | 115828 | 7863 | 3774 | 0.00012024 | 1.163e-06 | 103.3833 | 1 | 310 | Customer | 382822 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001635 | PD-01062020-00349 | METRO EAST | EAST | 8471:NE 30TH ST | NE_30TH_ST_7121 | 847121 | 2020-01-06 12:46 | 2020-01-06 14:59 | 133.2 | 1 | 1 | 98.1746 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4240 NE.19 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 114196 | 71095 | 2397 | 342 | 0.00011418 | 1.163e-06 | 98.1746 | 1 | 320 | Customer | 26099 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | OK - 2022
J2001.001638 | PD-01062020-00358 | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2921 | 812921 | 2020-01-06 12:51 | 2020-01-06 14:54 | 123.35 | 12 | 14 | 1263.2 | 3 | DAMAGED BY PUBLIC | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 3332 SW.49 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 158943 | 102043 | 6371 | 1479 | 0.0014691 | 1.3956e-05 | 105.2667 | 1 | 310 | Load | 17589 | Load | Tran1phOH | THOMAS E COLE | 405-623-9338 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001640 |  | METRO EAST | EAST | 8542:RENO | RENO_4231 | 854231 | 2020-01-06 12:57 | 2020-01-06 13:03 | 6.6 | 1 | 1 | 6.6 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DEL CITY | 47 EASTBROOK DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 114196 | 71095 | 5209 | 956 | 7.6758e-06 | 1.163e-06 | 6.6 | 1 | 310 | Customer | 26862 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2021
J2001.001642 |  | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2721 | 872721 | 2020-01-06 12:58 | 2020-01-06 13:08 | 9.13 | 1 | 1 | 9.1333 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 402 MIMOSA DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 158943 | 56900 | 6452 | 934 | 1.0622e-05 | 1.163e-06 | 9.1333 | 1 | 310 | Customer | 36445 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001641 | PD-01062020-00463 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3924 | 833924 | 2020-01-06 13:00 | 2020-01-06 15:56 | 176.33 | 1 | 1 | 176.3333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 3837 NW.67 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167962 | 148169 | 7846 | 795 | 0.00020508 | 1.163e-06 | 176.3333 | 1 | 310 | Customer | 21574 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2022
J2001.001643 |  | METRO NORTH | GUTHRIE | 8807:CRESCENT | CRESCENT_721 | 880721 | 2020-01-06 13:00 | 2020-01-06 14:09 | 68.5 | 5 | 6 | 274.0833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | CRESCENT | 211 W.ADAMS | CMI_PLANNED | YES | NO | NO | 859842 | 167962 | 19793 | 1763 | 873 | 0.00031876 | 5.815e-06 | 54.8167 | 1 | 310 | Load | 37329 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001651 | PD-01062020-00485 | METRO NORTH | NORTH | 8430:REMINGTON PARK | REMINGTON_PARK_3022 | 843022 | 2020-01-06 13:22 | 2020-01-06 15:40 | 138.33 | 4 | 3 | 541.8667 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 821 NE.65 | CMI_NORMAL | NO | NO | NO | 859842 | 167962 | 148169 | 846 | 669 | 0.00063019 | 4.652e-06 | 135.4667 | 1 | 310 | Load | 27817 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001653 | PD-01062020-00394 | METRO NORTH | NORTH | 8430:REMINGTON PARK | REMINGTON_PARK_3024 | 843024 | 2020-01-06 13:23 | 2020-01-06 14:50 | 86.65 | 1 | 1 | 86.65 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2509 NE 71 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167962 | 148169 | 846 | 177 | 0.00010077 | 1.163e-06 | 86.65 | 1 | 310 | Load | 69292 | Load | TranOpenDelta | PETER BILICKI | 619-726-8332 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001657 | PD-01062020-00395 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1521 | 811521 | 2020-01-06 13:28 | 2020-01-06 14:44 | 76.17 | 1 | 1 | 76.1667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 533 SW.12 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 158943 | 102043 | 6052 | 1239 | 8.8582e-05 | 1.163e-06 | 76.1667 | 1 | 320 | Customer | 31 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | OK - 2022
J2001.001658 | PD-01062020-00399 | METRO NORTH | NORTH | 8430:REMINGTON PARK | REMINGTON_PARK_3022 | 843022 | 2020-01-06 13:30 | 2020-01-06 20:23 | 413.03 | 5 | 3 | 1277.0833 | 3 | DAMAGED BY PUBLIC | 12 | POLE | OKLAHOMA CITY | NW.62 + SANTA FE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167962 | 148169 | 846 | 669 | 0.0014853 | 5.815e-06 | 255.4167 | 1 | 310 | Mainline | 11648 | Fuse | FuseOH | BRIAN E WHITE | 405-642-7075 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001660 | PD-01062020-00423 | NORTHEAST | SAPULPA | 3218:BEGGS | BEGGS_1824 | 321824 | 2020-01-06 13:30 | 2020-01-06 17:03 | 212.65 | 1 | 1 | 212.65 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | BEGGS | N ISPARCHER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 73901 | 40689 | 1830 | 935 | 0.00024731 | 1.163e-06 | 212.65 | 1 | 320 | Customer | 43664 | Load | Tran1phOH | RYAN ADEE | 918-506-3082 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2020
J2001.001670 |  | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1371 | 831371 | 2020-01-06 13:35 | 2020-01-06 14:06 | 31.1 | 1 | 1 | 31.1 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 11228 NW 96TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 128550 | 115828 | 7863 | 3774 | 3.6169e-05 | 1.163e-06 | 31.1 | 1 | 308 | Customer | 307936 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001665 | PD-01062020-00422 | METRO EAST | SHAWNEE | 7407:REMINGTON | REMINGTON 21 | 740721 | 2020-01-06 13:38 | 2020-01-06 14:57 | 79.18 | 1 | 2 | 68 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | EARLSBORO | 2.5ME CC | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859842 | 114196 | 22067 | 3658 | 2014 | 7.9084e-05 | 1.163e-06 | 68 | 1 | 320 | Load | 6116 | Load | Tran1phOH | BRYAN K TATUM | 405-659-0746 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | OK - 2021
J2001.001675 | PD-01062020-00424 | SOUTHERN | ARDMORE | 5108:WOLF CREEK | WOLF CREEK 22 | 510822 | 2020-01-06 13:44 | 2020-01-06 15:34 | 109.5 | 8 | 10 | 833.8667 | 4 | DETERIORATION | 47 | ARRESTOR OH | LONE GROVE | HWY70-CHEEK-1W-.3N | CMI_NORMAL | NO | NO | NO | 859842 | 77521 | 23565 | 448 | 236 | 0.00096979 | 9.304e-06 | 104.2333 | 1 | 310 | Tap | 8984 | Fuse | FuseRiser | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001678 |  | METRO NORTH | NORTH | 8209:CLASSEN | CLASSEN_961 | 820961 | 2020-01-06 13:57 | 2020-01-06 14:12 | 14.93 | 1 | 1 | 14.9333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1316 NW.2 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167962 | 148169 | 3877 | 866 | 1.7368e-05 | 1.163e-06 | 14.9333 | 1 | 310 | Customer | 2722 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001691 | PD-01062020-00465 | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_523 | 530523 | 2020-01-06 14:04 | 2020-01-06 14:35 | 30.7 | 1 | 2 | 150.0167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | WILSON | 762 WOODWORTH RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 77521 | 6784 | 2125 | 868 | 0.00017447 | 1.163e-06 | 150.0167 | 1 | 310 | Load | 302335 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001682 | PD-01062020-00436 | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1224 | 911224 | 2020-01-06 14:04 | 2020-01-06 14:36 | 31.67 | 1 | 1 | 31.6667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 2727 GRAND AV,2 POLE W-MAY AVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 82099 | 61123 | 6590 | 1795 | 3.6828e-05 | 1.163e-06 | 31.6667 | 1 | 320 | Customer | 4619 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | Ark - Series 1
J2001.001683 | PD-01062020-00437 | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_523 | 530523 | 2020-01-06 14:04 | 2020-01-06 16:00 | 115.67 | 1 | 2 | 150.3 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | WILSON | SANTE FE/RIDGE RD .5W SS | CMI_NORMAL | NO | NO | NO | 859842 | 77521 | 6784 | 2125 | 868 | 0.0001748 | 1.163e-06 | 150.3 | 1 | 310 | Customer | 383097 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001681 |  | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_523 | 530523 | 2020-01-06 14:04 | 2020-01-06 14:04 | 0 | 868 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | HEALDTON | 128 S 8TH ST | CMI_MOMENTARY | YES | NO | NO | 859842 | 77521 | 6784 | 2125 | 868 | 0 | 0.0010095 | 0 | 1 | 0 | Feeder | HEALDTON_523 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001685 | PD-01062020-00459 | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1862 | 941862 | 2020-01-06 14:15 | 2020-01-06 14:46 | 31.3 | 1 | 1 | 19.163 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | LAMAR | CAZORT ST. + LAMB ST. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 82099 | 7526 | 729 | 729 | 2.2287e-05 | 1.163e-06 | 19.163 | 1 | 310 | Customer | 18214 | Load | Tran1phPad | KRIS L HALMES | 479-430-9447 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | Ark - Series 2
J2001.001687 | PD-01062020-00453 | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2731 | 872731 | 2020-01-06 14:18 | 2020-01-06 14:45 | 27.27 | 1 | 1 | 27.2667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 915 N.FLOOD AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 158943 | 56900 | 6452 | 1349 | 3.1711e-05 | 1.163e-06 | 27.2667 | 1 | 310 | Customer | 33793 | Load | TranOpenDelta | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001693 | PD-01062020-00460 | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5821 | 845821 | 2020-01-06 14:22 | 2020-01-06 16:09 | 106.95 | 1 | 1 | 106.95 | 3 | DAMAGED BY PUBLIC | 36 | CONDUCTOR PRIMARY - UG | JONES | 9000 Highland Ave | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 114196 | 71095 | 2983 | 1189 | 0.00012438 | 1.163e-06 | 106.95 | 1 | 310 | Load | 420950 | Load | Tran1phPad | BAD ORDER PRIMARY RES COORD | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | OK - 2020
J2001.001695 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7029 | 817029 | 2020-01-06 14:25 | 2020-01-06 17:13 | 167.63 | 14 | 4 | 1395.5667 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | OKLAHOMA CITY | 634 CITY-VIEW DR | CMI_PLANNED | YES | NO | NO | 859842 | 158943 | 102043 | 9937 | 1757 | 0.0016231 | 1.6282e-05 | 99.6833 | 1 | 308 | Load | 33415 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2022
J2001.001697 | PD-01062020-00467 | NORTHEAST | SAPULPA | 3218:BEGGS | BEGGS_1824 | 321824 | 2020-01-06 14:27 | 2020-01-06 17:30 | 183.35 | 1 | 1 | 176.1833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | BEGGS | 1E.,+ 1/4N.OF BEGGS | CMI_NORMAL | NO | NO | NO | 859842 | 73901 | 40689 | 1830 | 935 | 0.0002049 | 1.163e-06 | 176.1833 | 1 | 310 | Load | 44410 | Load | Tran1phOH | STEPHEN BURKS | 918-639-0130 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2020
J2001.001700 | PD-01062020-00473 | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_523 | 530523 | 2020-01-06 14:31 | 2020-01-06 16:15 | 104.03 | 1 | 2 | 123.2333 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | WILSON | H70/76 1E 1.5S ES | CMI_NORMAL | NO | NO | NO | 859842 | 77521 | 6784 | 2125 | 868 | 0.00014332 | 1.163e-06 | 123.2333 | 1 | 310 | Load | 30843 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001706 |  | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_523 | 530523 | 2020-01-06 14:47 | 2020-01-06 17:16 | 149.78 | 1 | 1 | 107.5333 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | WILSON | 70+76 1MS .4ME SS | CMI_NORMAL | NO | NO | NO | 859842 | 77521 | 6784 | 2125 | 868 | 0.00012506 | 1.163e-06 | 107.5333 | 1 | 310 | Load | 30568 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001709 |  | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_523 | 530523 | 2020-01-06 14:57 | 2020-01-06 17:15 | 138.22 | 1 | 1 | 97.0333 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | WILSON | 70-76 1E 1S .1E SS | CMI_NORMAL | NO | NO | NO | 859842 | 77521 | 6784 | 2125 | 868 | 0.00011285 | 1.163e-06 | 97.0333 | 1 | 310 | Load | 19037 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001712 | PD-01062020-00508 | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1722 | 831722 | 2020-01-06 15:02 | 2020-01-06 15:57 | 55.22 | 1 | 1 | 55.2167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 324 NW.118 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167962 | 148169 | 6639 | 1201 | 6.4217e-05 | 1.163e-06 | 55.2167 | 1 | 310 | Customer | 69607 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001715 |  | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_523 | 530523 | 2020-01-06 15:02 | 2020-01-06 17:14 | 132.3 | 1 | 1 | 92.4667 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | CORNISH | REED 34-1 | CMI_NORMAL | NO | NO | NO | 859842 | 77521 | 6784 | 2125 | 868 | 0.00010754 | 1.163e-06 | 92.4667 | 1 | 310 | Load | 12059 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001717 |  | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2921 | 812921 | 2020-01-06 15:09 | 2020-01-06 15:14 | 4.68 | 1 | 1 | 4.6833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3332 SW.49 | CMI_MOMENTARY | YES | NO | NO | 859842 | 158943 | 102043 | 6371 | 1479 | 5.4467e-06 | 1.163e-06 | 4.6833 | 1 | 310 | Customer | 17589 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001718 |  | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_523 | 530523 | 2020-01-06 15:13 | 2020-01-06 17:13 | 120.28 | 1 | 1 | 81.1833 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | WILSON | 3122 Ridge Rd | CMI_NORMAL | NO | NO | NO | 859842 | 77521 | 6784 | 2125 | 868 | 9.4417e-05 | 1.163e-06 | 81.1833 | 1 | 310 | Load | 404689 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001729 | PD-01062020-00520 | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_924 | 910924 | 2020-01-06 15:13 | 2020-01-06 16:38 | 84.6 | 1 | 2 | 71.3167 | 12 | POOR CONNECTION | 50 | CONNECTOR | FORT SMITH | 60 HAVEN-HILL DR | CMI_NORMAL | NO | NO | NO | 859842 | 82099 | 61123 | 5007 | 1723 | 8.2942e-05 | 1.163e-06 | 71.3167 | 1 | 320 | Customer | 8341 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | Ark - Series 3
J2001.001719 | PD-01062020-00544 | SOUTHERN | HEALDTON | 5122:DILLARD | DILLARD_2222 | 512222 | 2020-01-06 15:15 | 2020-01-06 16:00 | 44.52 | 1 | 1 | 44.5167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | WILSON | 215 NE 5TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 77521 | 6784 | 1183 | 697 | 5.1773e-05 | 1.163e-06 | 44.5167 | 1 | 310 | Customer | 7575 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001720 |  | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2921 | 812921 | 2020-01-06 15:16 | 2020-01-06 15:18 | 2.18 | 1 | 1 | 2.1833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3332 SW.49 | CMI_MOMENTARY | YES | NO | NO | 859842 | 158943 | 102043 | 6371 | 1479 | 2.5392e-06 | 1.163e-06 | 2.1833 | 1 | 320 | Customer | 17589 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001721 |  | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_621 | 770621 | 2020-01-06 15:18 | 2020-01-06 15:27 | 9.1 | 8 | 0 | 72.6241 | 4 | DETERIORATION | 2 | TRANSFORMER OH | BRISTOW | 210 W 11TH | CMI_PLANNED | YES | NO | NO | 859842 | 73901 | 40689 | 3777 | 1573 | 8.4462e-05 | 9.304e-06 | 9.078 | 1 | 0 | Load | 41185 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | OK - 2021
J2001.001727 | PD-01062020-00523 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2223 | 832223 | 2020-01-06 15:25 | 2020-01-06 16:51 | 85.82 | 1 | 1 | 85.8167 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | OKLAHOMA CITY | 3750 N INTERSTATE-240 | CMI_NORMAL | NO | NO | NO | 859842 | 167962 | 148169 | 9168 | 1444 | 9.9805e-05 | 1.163e-06 | 85.8167 | 1 | 310 | Customer | 59998 | Load | Tran3phPadWye | KIRK REILLEY | 405-550-3062 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | OK - 2021
J2001.001728 | PD-01062020-00527 | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1721 | 861721 | 2020-01-06 15:26 | 2020-01-06 16:19 | 53.48 | 1 | 1 | 53.4833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 5016 OAK-MANOR DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 114196 | 71095 | 6883 | 1503 | 6.2201e-05 | 1.163e-06 | 53.4833 | 1 | 320 | Customer | 33623 | Load | Tran1phPad | THOMAS E COLE | 405-623-9338 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001735 | PD-01062020-00554 | NORTHWEST | ENID | 4135:SO 4TH ST | SO_4TH_ST_3524 | 413524 | 2020-01-06 15:42 | 2020-01-06 16:52 | 69.58 | 1 | 1 | 69.5833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ENID | 1221 RAMONA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 53483 | 37557 | 3094 | 1611 | 8.0926e-05 | 1.163e-06 | 69.5833 | 1 | 310 | Customer | 253 | Load | Tran1phOH | KEVIN N PERRYMAN | 601-528-2473 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001740 | PD-01062020-00550 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9931 | 829931 | 2020-01-06 15:45 | 2020-01-06 17:01 | 75.67 | 1 | 3 | 60.25 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 5001 NW 10TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 128550 | 115828 | 9212 | 2191 | 7.0071e-05 | 1.163e-06 | 60.25 | 1 | 310 | Customer | 47897 | Load | Tran1phPad | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001738 | PD-01062020-00545 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1926 | 851926 | 2020-01-06 15:57 | 2020-01-06 16:46 | 49 | 1 | 1 | 49 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MIDWEST CITY | 10516 NE.3 | CMI_NORMAL | NO | NO | NO | 859842 | 114196 | 71095 | 12429 | 2125 | 5.6987e-05 | 1.163e-06 | 49 | 1 | 310 | Customer | 10413 | Load | Tran1phOH | KYLE L GOODIN | 405-426-9802 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2021
J2001.001743 | PD-01062020-00555 | METRO WEST | WEST | 8158:SARA | SARA_5864 | 815864 | 2020-01-06 15:59 | 2020-01-06 23:33 | 454.33 | 17 | 7 | 7566.1333 | 3 | DAMAGED BY PUBLIC | 32 | CONDUCTOR SECONDARY - UG | MUSTANG | 322 W.MAPLEBRNCH WY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 128550 | 115828 | 18201 | 4805 | 0.0087994 | 1.9771e-05 | 445.0667 | 1 | 310 | Load | 65363 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2022
J2001.001739 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3631 | 833631 | 2020-01-06 15:59 | 2020-01-06 16:07 | 7.52 | 1 | 1 | 7.5167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | THE VILLAGE | 10637 N.MAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167962 | 148169 | 8780 | 1333 | 8.7419e-06 | 1.163e-06 | 7.5167 | 1 | 310 | Customer | 18919 | Load | Tran3phWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2021
J2001.001742 |  | METRO EAST | SHAWNEE | 7407:REMINGTON | REMINGTON 22 | 740722 | 2020-01-06 16:04 | 2020-01-06 16:14 | 9.58 | 1 | 1 | 9.5833 | 4 | DETERIORATION | 12 | POLE | SHAWNEE | 926 E.INDEPENDENCE | CMI_PLANNED | YES | NO | NO | 859842 | 114196 | 22067 | 3658 | 1644 | 1.1145e-05 | 1.163e-06 | 9.5833 | 1 | 310 | Customer | 7886 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001744 |  | METRO NORTH | GUTHRIE | 8807:CRESCENT | CRESCENT_723 | 880723 | 2020-01-06 16:04 | 2020-01-06 16:46 | 41.58 | 1 | 1 | 41.5833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | CASHION | N MAIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167962 | 19793 | 1763 | 890 | 4.8362e-05 | 1.163e-06 | 41.5833 | 1 | 310 | Customer | 40483 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001745 |  | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_523 | 530523 | 2020-01-06 16:10 | 2020-01-06 17:08 | 58.12 | 1 | 1 | 24.5 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | WILSON | HWY 70 & 76 1E 3.1S .1W | CMI_NORMAL | NO | NO | NO | 859842 | 77521 | 6784 | 2125 | 868 | 2.8494e-05 | 1.163e-06 | 24.5 | 1 | 310 | Load | 221430 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001749 |  | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_523 | 530523 | 2020-01-06 16:16 | 2020-01-06 17:08 | 52.45 | 1 | 2 | 18.9167 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | WILSON | 70-76 1E 1S .1E NS | CMI_NORMAL | NO | NO | NO | 859842 | 77521 | 6784 | 2125 | 868 | 2.2e-05 | 1.163e-06 | 18.9167 | 1 | 310 | Load | 18686 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001759 |  | NORTHWEST | ALVA | 4707:KNOBHILL | KNOBHILL_730 | 470730 | 2020-01-06 16:20 | 2020-01-06 16:44 | 24 | 1 | 1 | 24 | 1 | CANCELLED | 57 | CANCELLED | DACOMA | 2E-ALVA (NELSON ADD) | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 53483 | 5515 | 1740 | 525 | 2.7912e-05 | 1.163e-06 | 24 | 1 | 308 | Load | 8305 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001752 | PD-01062020-00571 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5021 | 865021 | 2020-01-06 16:24 | 2020-01-06 17:51 | 87.07 | 1 | 1 | 87.0667 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | MIDWEST CITY | 321 E.STEED DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859842 | 114196 | 71095 | 8623 | 1291 | 0.00010126 | 1.163e-06 | 87.0667 | 1 | 320 | Customer | 8390 | Load | Tran1phOH | KYLE L GOODIN | 405-426-9802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001762 |  | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_621 | 550621 | 2020-01-06 16:32 | 2020-01-06 17:01 | 29.17 | 1 | 1 | 29.1667 | 1 | CANCELLED | 57 | CANCELLED | MEAD | 8567 US Hwy 70 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 77521 | 15465 | 6729 | 899 | 3.3921e-05 | 1.163e-06 | 29.1667 | 1 | 308 | Load | 302882 | Load | Tran3phWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001757 |  | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_523 | 530523 | 2020-01-06 16:34 | 2020-01-06 17:10 | 35.58 | 1 | 1 | 0.28333 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | WILSON | 70-76 1E 2.5S | CMI_NORMAL | NO | NO | NO | 859842 | 77521 | 6784 | 2125 | 868 | 3.2952e-07 | 1.163e-06 | 0.28333 | 1 | 310 | Load | 25979 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001761 |  | ARKANSAS | OZARK | 9412:ALTUS | ALTUS_1229 | 941229 | 2020-01-06 16:45 | 2020-01-06 17:20 | 35.47 | 5 | 5 | 151.9167 | 4 | DETERIORATION | 12 | POLE | OZARK | W CK 1 M S-BORDER | CMI_PLANNED | YES | NO | NO | 859842 | 82099 | 7526 | 862 | 862 | 0.00017668 | 5.815e-06 | 30.3833 | 1 | 310 | Tap | 6137 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-06 | 2020 |  | Ark - Series 2
J2001.001765 | PD-01062020-00597 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6922 | 846922 | 2020-01-06 16:49 | 2020-01-06 17:38 | 49.48 | 1 | 1 | 45.0333 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 414 NW.97 | CMI_NORMAL | NO | NO | NO | 859842 | 167962 | 148169 | 7713 | 1482 | 5.2374e-05 | 1.163e-06 | 45.0333 | 1 | 311 | Customer | 28984 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001770 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6324 | 816324 | 2020-01-06 17:22 | 2020-01-06 18:21 | 58.9 | 13 | 13 | 635.2667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | MOORE | 845 NW 12TH | CMI_PLANNED | YES | NO | NO | 859842 | 158943 | 102043 | 11809 | 2048 | 0.00073882 | 1.5119e-05 | 48.8667 | 1 | 310 | Load | 44354 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2021
J2001.001771 |  | ARKANSAS | OZARK | 9412:ALTUS | ALTUS_1229 | 941229 | 2020-01-06 17:24 | 2020-01-06 17:36 | 12.05 | 1 | 1 | 12.05 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OZARK | RT 1 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 82099 | 7526 | 862 | 862 | 1.4014e-05 | 1.163e-06 | 12.05 | 1 | 310 | Load | 7810 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-06 | 2020 |  | Ark - Series 2
J2001.001772 | PD-01062020-00616 | NORTHWEST | ENID | 4112:CHESTNUT | CHESTNUT_1222 | 411222 | 2020-01-06 17:24 | 2020-01-06 19:10 | 105.7 | 1 | 2 | 102.0667 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | ENID | 1925 E BROADWAY | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859842 | 53483 | 37557 | 2857 | 1745 | 0.0001187 | 1.163e-06 | 102.0667 | 1 | 310 | Customer | 4711 | Load | Tran1phOH | KEVIN N PERRYMAN | 601-528-2473 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | #N/A
J2001.001780 |  | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3024 | 743024 | 2020-01-06 17:55 | 2020-01-06 18:06 | 10.75 | 1 | 1 | 10.75 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SHAWNEE | 136 N.CENTER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 114196 | 22067 | 6632 | 1639 | 1.2502e-05 | 1.163e-06 | 10.75 | 1 | 310 | Customer | 3282 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001782 |  | NORTHWEST | ENID | 4135:SO 4TH ST | SO_4TH_ST_3522 | 413522 | 2020-01-06 17:55 | 2020-01-06 18:17 | 22.33 | 1 | 1 | 22.3333 | 1 | CANCELLED | 57 | CANCELLED | ENID | 1305 HITE BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 53483 | 37557 | 3094 | 1483 | 2.5974e-05 | 1.163e-06 | 22.3333 | 1 | 308 | Customer | 4457 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001785 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-06 18:29 | 2020-01-06 19:18 | 49.28 | 3 | 2 | 118.15 | 4 | DETERIORATION | 47 | ARRESTOR OH | FORT SMITH | 5710 SO. 73 PLACE | CMI_PLANNED | YES | NO | NO | 859842 | 82100 | 61125 | 2732 | 2120 | 0.00013741 | 3.489e-06 | 39.3833 | 1 | 308 | Load | 19275 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | Ark - Series 2
J2001.001791 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6326 | 816326 | 2020-01-06 19:17 | 2020-01-06 20:22 | 65.37 | 3 | 1 | 121.8 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 14000 S MERIDIAN | CMI_PLANNED | YES | NO | NO | 859842 | 158943 | 102043 | 11809 | 1255 | 0.00014165 | 3.489e-06 | 40.6 | 1 | 308 | Load | 74824 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001795 |  | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3731 | 833731 | 2020-01-06 19:48 | 2020-01-06 19:55 | 6.77 | 1 | 1 | 6.7667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | THE VILLAGE | 2112 CHURCHILL PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 167961 | 148168 | 5754 | 1902 | 7.8697e-06 | 1.163e-06 | 6.7667 | 1 | 320 | Customer | 7533 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | OK - 2020
J2001.001796 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_823 | 870823 | 2020-01-06 19:51 | 2020-01-06 19:58 | 7.42 | 1 | 1 | 7.4167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 832 CARDNAL-CRK BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 859842 | 158943 | 56900 | 6775 | 2380 | 8.6256e-06 | 1.163e-06 | 7.4167 | 1 | 310 | Customer | 44803 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001801 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_721 | 870721 | 2020-01-06 20:51 | 2020-01-06 21:42 | 51 | 25 | 28 | 603.3333 | 4 | DETERIORATION | 50 | CONNECTOR | NORMAN | 2121 BEAUMONT DR | CMI_PLANNED | YES | NO | NO | 859842 | 158943 | 56900 | 11826 | 1681 | 0.00070168 | 2.9075e-05 | 24.1333 | 1 | 310 | Load | 62578 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001802 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_721 | 870721 | 2020-01-06 20:51 | 2020-01-06 21:42 | 51.02 | 12 | 15 | 287.4 | 4 | DETERIORATION | 50 | CONNECTOR | NORMAN | 2100 BEAUMONT | CMI_PLANNED | YES | NO | NO | 859842 | 158943 | 56900 | 11826 | 1681 | 0.00033425 | 1.3956e-05 | 23.95 | 1 | 310 | Load | 71433 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-06 | 2020 |  | #N/A
J2001.001803 | PD-01062020-00633 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1524 | 811524 | 2020-01-06 21:16 | 2020-01-06 22:02 | 46.37 | 1 | 2 | 46.3667 | 13 | PREMATURE FAILURE | 15 | METER - SECONDARY | OKLAHOMA CITY | 1136 SW.25 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 859842 | 158943 | 102043 | 6052 | 2070 | 5.3925e-05 | 1.163e-06 | 46.3667 | 1 | 320 | Customer | 22249 | Load | TranOpenDelta | THOMAS E COLE | 405-623-9338 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-06 | 2020 |  | OK - 2022
J2001.001835 | PD-01072020-00012 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-01-07 04:22 | 2020-01-07 08:34 | 251.93 | 43 | 17 | 4671.95 | 13 | PREMATURE FAILURE | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | SLEEPY HOLLOW + SE.89 | CMI_NORMAL | NO | NO | NO | 860005 | 114193 | 71092 | 11612 | 3533 | 0.0054325 | 5e-05 | 108.65 | 1 | 310 | Mainline | 28372 | Fuse | FuseRiser | BAD ORDER PRIMARY RES COORD | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.001855 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-01-07 06:45 | 2020-01-07 08:58 | 132.95 | 7 | 7 | 441.5833 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | SLEEPY HOLLOW BLK 2 LOT 19 | CMI_NORMAL | NO | NO | NO | 860005 | 114193 | 71092 | 11612 | 3533 | 0.00051347 | 8.1395e-06 | 63.0833 | 1 | 310 | Load | 78769 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.001854 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-01-07 06:46 | 2020-01-07 08:57 | 131.12 | 6 | 6 | 370.4 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | 20000 SE 95TH ST | CMI_NORMAL | NO | NO | NO | 860005 | 114193 | 71092 | 11612 | 3533 | 0.0004307 | 6.9767e-06 | 61.7333 | 1 | 310 | Secondary | 81946 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.001857 | PD-01072020-00027 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9921 | 829921 | 2020-01-07 07:16 | 2020-01-07 08:23 | 67.2 | 1 | 1 | 35.057 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 529 N.BEACON DR. | CMI_NORMAL | NO | NO | NO | 860005 | 128550 | 115828 | 9212 | 1632 | 4.0764e-05 | 1.1628e-06 | 35.057 | 1 | 320 | Customer | 75179 | Load | Tran3phWye | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.001858 | PD-01072020-00031 | METRO EAST | EAST | 8471:NE 30TH ST | NE_30TH_ST_7123 | 847123 | 2020-01-07 07:21 | 2020-01-07 08:24 | 62.83 | 1 | 1 | 62.8333 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 2817 NE.17 | CMI_NORMAL | NO | NO | NO | 860005 | 114193 | 71092 | 2396 | 1288 | 7.3062e-05 | 1.1628e-06 | 62.8333 | 1 | 310 | Customer | 8288 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | OK - 2022
J2001.001861 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-07 07:33 | 2020-01-07 07:33 | 0.02 | 3783 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MULBERRY | 6007 EAST HWY 64 | CMI_MOMENTARY | YES | NO | NO | 860005 | 82100 | 61125 | 3779 | 1199 | 0 | 0.0043988 | 0 | 1 | 0 | Feeder | SIMMONS_3062 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-07 | 2020 |  | Ark - Series 2
J2001.001863 | PD-01072020-00034 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6922 | 846922 | 2020-01-07 07:46 | 2020-01-07 08:26 | 40.27 | 1 | 1 | 40.2667 | 11 | OVERLOAD | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 209 NW 111 | CMI_NORMAL | NO | NO | NO | 860005 | 167961 | 148168 | 7713 | 1482 | 4.6821e-05 | 1.1628e-06 | 40.2667 | 1 | 320 | Customer | 81984 | Load | TranOpenDelta | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.001871 | PD-01072020-00048 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2625 | 862625 | 2020-01-07 08:06 | 2020-01-07 08:43 | 36.58 | 11 | 9 | 383.7167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | DEL CITY | 1417 S.HAMPTON DR | CMI_NORMAL | NO | NO | NO | 860005 | 158943 | 102043 | 7408 | 1267 | 0.00044618 | 1.2791e-05 | 34.8833 | 1 | 310 | Load | 16889 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2022
J2001.001873 |  | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3721 | 913721 | 2020-01-07 08:15 | 2020-01-07 08:22 | 7.2 | 1 | 1 | 7.2 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | ROGERS + ALBERT PIKE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 82100 | 61125 | 4565 | 1497 | 8.372e-06 | 1.1628e-06 | 7.2 | 1 | 310 | Customer | 15830 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | Ark - Series 3
J2001.001878 | PD-01072020-00064 | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2169 | 892169 | 2020-01-07 08:32 | 2020-01-07 10:17 | 104.55 | 1 | 1 | 76.95 | 12 | POOR CONNECTION | 50 | CONNECTOR | CALUMET | 12724 Memorial Rd NW | CMI_NORMAL | NO | NO | NO | 860005 | 128550 | 12722 | 3171 | 428 | 8.9476e-05 | 1.1628e-06 | 76.95 | 1 | 310 | Load | 87349 | Load | TranOpenDelta | JOSH BLACK | 405-403-9382 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2020
J2001.001879 |  | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2223 | 882223 | 2020-01-07 08:34 | 2020-01-07 10:38 | 124.08 | 66 | 24 | 6376.7 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | EDMOND | SS-COVELL,E-COLTRANE | CMI_PLANNED | YES | NO | NO | 860005 | 167961 | 19793 | 5383 | 1202 | 0.0074147 | 7.6744e-05 | 96.6167 | 1 | 310 | Mainline | 6375 | Recloser | Rec3phHydralic | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.001883 | PD-01072020-00072 | METRO EAST | EAST | 8542:RENO | RENO_4224 | 854224 | 2020-01-07 08:41 | 2020-01-07 10:10 | 88.53 | 1 | 1 | 76.55 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | MIDWEST CITY | 1325 ST MATTHEWS | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860005 | 114193 | 71092 | 5209 | 1221 | 8.9011e-05 | 1.1628e-06 | 76.55 | 1 | 310 | Customer | 57332 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2022
J2001.001886 | PD-01072020-00087 | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1862 | 941862 | 2020-01-07 08:44 | 2020-01-07 10:25 | 101.43 | 3 | 4 | 309.9 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | LAMAR | 4 POLE S-64 ON CAZORT, LAMAR | CMI_NORMAL | NO | NO | NO | 860005 | 82100 | 7526 | 729 | 729 | 0.00036035 | 3.4884e-06 | 103.3 | 1 | 310 | Secondary | 4546 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | Ark - Series 2
J2001.001885 |  | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1723 | 911723 | 2020-01-07 08:44 | 2020-01-07 11:01 | 136.32 | 7 | 6 | 1275.1667 | 4 | DETERIORATION | 12 | POLE | BARLING | 804 11,2 POLE S-N.H ST,BARLING | CMI_PLANNED | YES | NO | NO | 860005 | 82100 | 61125 | 4235 | 1622 | 0.0014827 | 8.1395e-06 | 182.1667 | 1 | 308 | Load | 3256 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-07 | 2020 |  | #N/A
J2001.001889 | PD-01072020-00085 | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_523 | 320523 | 2020-01-07 08:52 | 2020-01-07 09:26 | 34.48 | 1 | 1 | 34.4833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | SAPULPA | 2341 S.POPLAR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 73898 | 40689 | 3833 | 1714 | 4.0097e-05 | 1.1628e-06 | 34.4833 | 1 | 310 | Customer | 44543 | Load | Tran1phOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | OK - 2022
J2001.001891 |  | METRO EAST | SEMINOLE | 7320:KOLACHE | KOLACHE_2042 | 732042 | 2020-01-07 08:52 | 2020-01-07 10:48 | 115.17 | 1 | 1 | 81.2333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | PRAGUE | 9008 N3570 RD | CMI_PLANNED | YES | NO | NO | 860005 | 114193 | 13583 | 583 | 224 | 9.4457e-05 | 1.1628e-06 | 81.2333 | 1 | 308 | Load | 170812 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | #N/A
J2001.001892 | PD-01072020-00106 | NORTHWEST | ENID | 4461:TURKEY CREEK | TURKEY_CREEK_6121 | 446121 | 2020-01-07 08:56 | 2020-01-07 10:46 | 110.43 | 1 | 1 | 110.4333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DOVER | 4S 1W HENN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 53482 | 37556 | 436 | 416 | 0.00012841 | 1.1628e-06 | 110.4333 | 1 | 310 | Load | 1978 | Load | Tran1phOH | STEVEN LORENZ | 580-822-3566 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | #N/A
J2001.001895 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5922 | 835922 | 2020-01-07 09:00 | 2020-01-07 10:50 | 109.73 | 5 | 5 | 190.6667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | YUKON | 509 TURTLECREEK DR | CMI_PLANNED | YES | NO | NO | 860005 | 128550 | 115828 | 6411 | 1634 | 0.0002217 | 5.8139e-06 | 38.1333 | 1 | 310 | Load | 24078 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | #N/A
J2001.001896 |  | NORTHWEST | ENID | 4109:WAUKOMIS | WAUKOMIS 23 | 410923 | 2020-01-07 09:02 | 2020-01-07 13:57 | 294.38 | 1 | 0 | 292.2833 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | 0 | 9/10M E OF REED RD AND US 81 - RURAL | CMI_PLANNED | YES | NO | NO | 860005 | 53482 | 37556 | 1556 | 572 | 0.00033986 | 1.1628e-06 | 292.2833 | 1 | 0 | Load | 412999 | Load | Tran3phWye | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.001897 |  | NORTHWEST | ENID | 4109:WAUKOMIS | WAUKOMIS 23 | 410923 | 2020-01-07 09:03 | 2020-01-07 12:44 | 221.75 | 1 | 1 | 219.0333 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | BISON | 2.5N, 1E BISON | CMI_PLANNED | YES | NO | NO | 860005 | 53482 | 37556 | 1556 | 572 | 0.00025469 | 1.1628e-06 | 219.0333 | 1 | 308 | Load | 4798 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.001899 |  | NORTHEAST | SAPULPA | 7636:GREAT PLAINS | GREAT_PLAINS_3641 | 763641 | 2020-01-07 09:07 | 2020-01-07 10:43 | 96.15 | 1 | 0 | 95.5167 | 4 | DETERIORATION | 12 | POLE | 0 | 349883 E0750 RD | CMI_PLANNED | YES | NO | NO | 860005 | 73898 | 40689 | 118 | 77 | 0.00011107 | 1.1628e-06 | 95.5167 | 1 | 0 | Mainline | 325789 | Recloser | Rec3phHydralic | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.001900 |  | NORTHWEST | ENID | 4109:WAUKOMIS | WAUKOMIS 23 | 410923 | 2020-01-07 09:07 | 2020-01-07 09:42 | 34.68 | 1 | 1 | 34.6833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BISON | 3015 W OSBORNE RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 53482 | 37556 | 1556 | 572 | 4.0329e-05 | 1.1628e-06 | 34.6833 | 1 | 310 | Load | 409337 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.001901 |  | NORTHWEST | ENID | 4109:WAUKOMIS | WAUKOMIS 23 | 410923 | 2020-01-07 09:09 | 2020-01-07 09:22 | 13.8 | 1 | 1 | 3.4167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BISON | 4S 3/4E W | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 53482 | 37556 | 1556 | 572 | 3.9728e-06 | 1.1628e-06 | 3.4167 | 1 | 310 | Load | 2039 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.001902 |  | SOUTHERN | MADILL | 5409:LITTLE CITY | LITTLE CITY 21 | 540921 | 2020-01-07 09:11 | 2020-01-07 09:49 | 37.92 | 2 | 0 | 69.55 | 4 | DETERIORATION | 2 | TRANSFORMER OH | 0 | 812 CUMBERLAND COVE RD | CMI_PLANNED | YES | NO | NO | 860005 | 77518 | 7201 | 610 | 591 | 8.0872e-05 | 2.3256e-06 | 34.775 | 1 | 0 | Load | 5323 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.001906 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6322 | 816322 | 2020-01-07 09:18 | 2020-01-07 11:38 | 140.05 | 12 | 12 | 1449.8 | 4 | DETERIORATION | 1 | TRANSFORMER UG | MOORE | 1136 NW.7 PL | CMI_PLANNED | YES | NO | NO | 860005 | 158943 | 102043 | 11809 | 1816 | 0.0016858 | 1.3953e-05 | 120.8167 | 1 | 310 | Load | 52654 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.001918 | PD-01072020-00157 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2221 | 832221 | 2020-01-07 09:23 | 2020-01-07 11:25 | 121.92 | 2 | 4 | 235.1667 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | OKLAHOMA CITY | 3936 NW.46 | CMI_NORMAL | NO | NO | NO | 860005 | 167961 | 148168 | 9168 | 1658 | 0.00027345 | 2.3256e-06 | 117.5833 | 1 | 310 | Load | 69624 | Load | Tran1phOH | PETER BILICKI | 619-726-8332 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | OK - 2022
J2001.001915 | PD-01072020-00142 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-01-07 09:25 | 2020-01-07 12:32 | 187.45 | 10 | 11 | 1844.6667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2213 SW.50 | CMI_NORMAL | NO | NO | NO | 860005 | 158943 | 102043 | 7592 | 2452 | 0.0021449 | 1.1628e-05 | 184.4667 | 1 | 310 | Load | 36540 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | #N/A
J2001.001912 | PD-01072020-00137 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2625 | 862625 | 2020-01-07 09:30 | 2020-01-07 11:33 | 123.62 | 1 | 1 | 9.8719 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 2018 SE 18TH ST | CMI_NORMAL | NO | NO | NO | 860005 | 158943 | 102043 | 7408 | 1267 | 1.1479e-05 | 1.1628e-06 | 9.8719 | 1 | 310 | Customer | 67334 | Load | Tran3phPadWye | RICHARD C PALMROSE | 405-650-1619 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2022
J2001.001917 | PD-01072020-00156 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3731 | 833731 | 2020-01-07 09:31 | 2020-01-07 11:32 | 120.72 | 1 | 3 | 114.45 | 27 | TREE:NON PREVENTABLE | 31 | CONDUCTOR SERVICE - OH | THE VILLAGE | 2112 CHURCHILL PL | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860005 | 167961 | 148168 | 5754 | 1902 | 0.00013308 | 1.1628e-06 | 114.45 | 1 | 310 | Customer | 7533 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2020
J2001.001920 |  | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_861 | 550861 | 2020-01-07 09:33 | 2020-01-07 09:46 | 13.07 | 1 | 1 | 13.0667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | COBB | 6815 FOREST LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 77518 | 15465 | 1101 | 480 | 1.5194e-05 | 1.1628e-06 | 13.0667 | 1 | 310 | Customer | 3493 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.001922 |  | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-01-07 09:39 | 2020-01-07 09:48 | 8.48 | 1 | 1 | 8.4833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DEL CITY | 3909 DEL RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 158943 | 102043 | 7408 | 2235 | 9.8643e-06 | 1.1628e-06 | 8.4833 | 1 | 310 | Customer | 9073 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2022
J2001.001923 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-07 09:43 | 2020-01-07 09:48 | 4.53 | 3281 | 51 | 12316.7 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MULBERRY | 6007 EAST HWY 64 | CMI_MOMENTARY | YES | NO | NO | 860005 | 82100 | 61125 | 3779 | 1199 | 0.014322 | 0.0038151 | 3.7539 | 1 | 310 | Feeder | SIMMONS_3062 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-07 | 2020 |  | Ark - Series 2
J2001.001925 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6322 | 816322 | 2020-01-07 09:44 | 2020-01-07 09:50 | 6.33 | 1 | 1 | 6.3333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MOORE | 1008 NW.21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 158943 | 102043 | 11809 | 1816 | 7.3643e-06 | 1.1628e-06 | 6.3333 | 1 | 310 | Customer | 46568 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.001960 | PD-01072020-00167 | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1862 | 941862 | 2020-01-07 09:51 | 2020-01-07 10:36 | 44.92 | 1 | 1 | 35.7667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | LAMAR | SHROPSHIRE ST W. OF CAZORT | CMI_NORMAL | NO | NO | NO | 860005 | 82100 | 7526 | 729 | 729 | 4.1589e-05 | 1.1628e-06 | 35.7667 | 1 | 310 | Customer | 10325 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | Ark - Series 2
J2001.001965 |  | NORTHWEST | ENID | 4518:MENO TAP | MENO TAP 22 | 451822 | 2020-01-07 09:52 | 2020-01-07 11:42 | 109.2 | 9 | 4 | 953.4 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | LAHOMA | LAHOMA SEC RD,E-PETTUS | CMI_PLANNED | YES | NO | NO | 860005 | 53482 | 37556 | 1331 | 829 | 0.0011086 | 1.0465e-05 | 105.9333 | 1 | 310 | Load | 7917 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.001970 | PD-01072020-00171 | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6223 | 866223 | 2020-01-07 09:54 | 2020-01-07 10:41 | 46.55 | 7 | 3 | 285.1333 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | OKLAHOMA CITY | .5MN SE44 .3ME WSTMNSTR | CMI_NORMAL | NO | NO | NO | 860005 | 114193 | 71092 | 7197 | 2227 | 0.00033155 | 8.1395e-06 | 40.7333 | 1 | 310 | Mainline | 13405 | Fuse | FuseRiser | STEVEN CASKEY | 405-777-8855 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.001976 |  | METRO SOUTH | SOUTH CENTRAL | 8723:INDIAN HILL | INDIAN_HILL_2321 | 872321 | 2020-01-07 10:07 | 2020-01-07 10:13 | 6.63 | 1 | 1 | 6.6333 | 1 | CANCELLED | 57 | CANCELLED | MOORE | 6571 NW 24th St. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 158943 | 102043 | 3189 | 1736 | 7.7131e-06 | 1.1628e-06 | 6.6333 | 1 | 310 | Customer | 326414 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.001977 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3822 | 913822 | 2020-01-07 10:10 | 2020-01-07 12:47 | 157.1 | 11 | 9 | 1728.1766 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 1004 S.11 | CMI_PLANNED | YES | NO | NO | 860005 | 82100 | 61125 | 2926 | 106 | 0.0020095 | 1.2791e-05 | 157.107 | 1 | 308 | Load | 1203 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-07 | 2020 |  | Ark - Series 2
J2001.001982 | PD-01072020-00195 | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 22 | 570822 | 2020-01-07 10:13 | 2020-01-07 11:03 | 49.62 | 6 | 7 | 279.25 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | DAVIS | 402 S.3RD | CMI_NORMAL | NO | NO | NO | 860005 | 77518 | 6807 | 1857 | 954 | 0.00032471 | 6.9767e-06 | 46.5417 | 1 | 310 | Load | 3793 | Load | Tran1phOH | CHAD A DOTSON | 405-488-5658 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | OK - 2021
J2001.001980 | PD-01072020-00188 | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_521 | 530521 | 2020-01-07 10:15 | 2020-01-07 10:57 | 42 | 1 | 1 | 40.8333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | HEALDTON | 17 FRANCES | CMI_NORMAL | NO | NO | NO | 860005 | 77518 | 6784 | 2125 | 1257 | 4.748e-05 | 1.1628e-06 | 40.8333 | 1 | 310 | Customer | 7488 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | OK - 2020
J2001.001985 | PD-01072020-00191 | METRO WEST | WEST | 8158:SARA | SARA_5862 | 815862 | 2020-01-07 10:18 | 2020-01-07 11:07 | 48.88 | 1 | 1 | 46.1305 | 4 | DETERIORATION | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 6801 S. Council Rd | CMI_NORMAL | NO | NO | NO | 860005 | 128550 | 115828 | 18201 | 3587 | 5.364e-05 | 1.1628e-06 | 46.1305 | 1 | 310 | Load | 323391 | Load | Tran3phWye | STEVEN GILES | 405-227-2802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2022
J2001.001986 |  | NORTHEAST | MUSKOGEE | 3326:JAMESVILLE | JAMESVILLE_2642 | 332642 | 2020-01-07 10:23 | 2020-01-07 14:12 | 228.48 | 1 | 0 | 228.4957 | 4 | DETERIORATION | 28 | CROSSARM | 0 | 2 1/4ME HWY 72 & 104 JCT | CMI_PLANNED | YES | NO | NO | 860005 | 73898 | 33209 | 1549 | 725 | 0.00026569 | 1.1628e-06 | 228.4957 | 1 | 0 | Load | 154465 | Load | Tran3phWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | #N/A
J2001.001995 | PD-01072020-00201 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_629 | 870629 | 2020-01-07 10:29 | 2020-01-07 11:15 | 46.15 | 14 | 15 | 624.1667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | NORMAN | 909 IOWA | CMI_NORMAL | NO | NO | NO | 860005 | 158943 | 56900 | 7362 | 1372 | 0.00072577 | 1.6279e-05 | 44.5833 | 1 | 310 | Load | 36638 | Load | Tran1phOH | MARK A PALMORE | 405-512-1933 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.001992 |  | SOUTHERN | MADILL | 5409:LITTLE CITY | LITTLE CITY 21 | 540921 | 2020-01-07 10:29 | 2020-01-07 11:43 | 73.65 | 7 | 1 | 472.9667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | BRIDGEVIEW | 2069 HILLTOP RD | CMI_PLANNED | YES | NO | NO | 860005 | 77518 | 7201 | 610 | 591 | 0.00054996 | 8.1395e-06 | 67.5667 | 1 | 308 | Load | 15018 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002000 | PD-01072020-00207 | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-01-07 10:37 | 2020-01-07 11:28 | 50.65 | 1 | 1 | 50.65 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 521 N.COUNCIL RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 128550 | 115828 | 3402 | 2035 | 5.8895e-05 | 1.1628e-06 | 50.65 | 1 | 310 | Customer | 34644 | Load | Tran1phPad | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002004 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6322 | 816322 | 2020-01-07 10:40 | 2020-01-07 11:37 | 56.48 | 1 | 1 | 38.5 | 4 | DETERIORATION | 1 | TRANSFORMER UG | MOORE | 733 OAKCLIFF | CMI_PLANNED | YES | NO | NO | 860005 | 158943 | 102043 | 11809 | 1816 | 4.4767e-05 | 1.1628e-06 | 38.5 | 1 | 310 | Customer | 52653 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002002 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7421 | 847421 | 2020-01-07 10:41 | 2020-01-07 10:41 | 0.03 | 405 | 0 | 13.5 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 1131 NE 33RD ST | CMI_MOMENTARY | YES | NO | NO | 860005 | 167961 | 148168 | 6148 | 405 | 1.5698e-05 | 0.00047093 | 0.033333 | 1 | 0 | Feeder | STONEWALL_7421 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-07 | 2020 |  | OK - 2022
J2001.002006 | PD-01072020-00221 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1423 | 311423 | 2020-01-07 10:43 | 2020-01-07 11:22 | 39.08 | 1 | 1 | 38.5167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MUSKOGEE | 554 N.8 | CMI_NORMAL | NO | NO | NO | 860005 | 73898 | 33209 | 4559 | 1496 | 4.4787e-05 | 1.1628e-06 | 38.5167 | 1 | 310 | Customer | 7852 | Load | Tran1phOH | REID R WILLIAMS | 512-618-8800 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | OK - 2020
J2001.002009 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-07 10:46 | 2020-01-07 10:53 | 6.38 | 1 | 1 | 6.3833 | 1 | CANCELLED | 57 | CANCELLED | ALMA | FINE RANCH-.3MN 282 ON 282LINK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 82100 | 61125 | 3779 | 1199 | 7.4224e-06 | 1.1628e-06 | 6.3833 | 1 | 310 | Customer | 17554 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-07 | 2020 |  | Ark - Series 2
J2001.002010 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5921 | 835921 | 2020-01-07 10:48 | 2020-01-07 11:49 | 61.12 | 9 | 10 | 296.7 | 4 | DETERIORATION | 2 | TRANSFORMER OH | YUKON | 401 RANCHWOOD BL | CMI_PLANNED | YES | NO | NO | 860005 | 128550 | 115828 | 6411 | 1803 | 0.000345 | 1.0465e-05 | 32.9667 | 1 | 310 | Load | 24060 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | #N/A
J2001.002011 | PD-01072020-00218 | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2161 | 892161 | 2020-01-07 10:53 | 2020-01-07 11:52 | 58.95 | 1 | 1 | 58.95 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 15200 NW 34th St | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 128550 | 12722 | 3171 | 731 | 6.8546e-05 | 1.1628e-06 | 58.95 | 1 | 310 | Load | 376738 | Load | Tran1phOH | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002021 | PD-01072020-00232 | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6223 | 866223 | 2020-01-07 10:54 | 2020-01-07 11:52 | 57.6 | 29 | 22 | 1237.8167 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | MIDWEST CITY | 2063 RIDGEVIEW RD. | CMI_NORMAL | NO | NO | NO | 860005 | 114193 | 71092 | 7197 | 2227 | 0.0014393 | 3.3721e-05 | 42.6833 | 1 | 310 | Mainline | 31567 | Fuse | FuseRiser | STEVEN CASKEY | 405-777-8855 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002012 |  | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_622 | 770622 | 2020-01-07 10:55 | 2020-01-07 14:13 | 198.45 | 3 | 3 | 110.6 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | BRISTOW | 1300 S.POPLAR PL | CMI_PLANNED | YES | NO | NO | 860005 | 73898 | 40689 | 3776 | 2006 | 0.0001286 | 3.4884e-06 | 36.8667 | 1 | 308 | Load | 46771 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | #N/A
J2001.002014 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-07 10:57 | 2020-01-07 14:10 | 193.27 | 1 | 1 | 176.7667 | 4 | DETERIORATION | 12 | POLE | COAL HILL | 1104 Carolina St | CMI_PLANNED | YES | NO | NO | 860005 | 82100 | 7526 | 1501 | 1198 | 0.00020554 | 1.1628e-06 | 176.7667 | 1 | 308 | Load | 3829 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-07 | 2020 |  | Ark - Series 2
J2001.002015 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-07 10:57 | 2020-01-07 14:10 | 192.87 | 1 | 1 | 179.4333 | 4 | DETERIORATION | 12 | POLE | COAL HILL | 1/4M S OF HWY64 ON 1ST S 500 | CMI_PLANNED | YES | NO | NO | 860005 | 82100 | 7526 | 1501 | 1198 | 0.00020864 | 1.1628e-06 | 179.4333 | 1 | 308 | Load | 15472 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-07 | 2020 |  | Ark - Series 2
J2001.002020 | PD-01072020-00238 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-01-07 11:01 | 2020-01-07 12:14 | 73.22 | 1 | 1 | 73.2167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 5720 NW.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 167961 | 148168 | 9234 | 1940 | 8.5135e-05 | 1.1628e-06 | 73.2167 | 1 | 310 | Customer | 30951 | Load | Tran1phPad | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2021
J2001.002022 | PD-01072020-00237 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3224 | 813224 | 2020-01-07 11:02 | 2020-01-07 12:51 | 109.07 | 8 | 7 | 852.9333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1605 SW.56 | CMI_NORMAL | NO | NO | NO | 860005 | 158943 | 102043 | 7592 | 1581 | 0.00099178 | 9.3023e-06 | 106.6167 | 1 | 310 | Load | 2839 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | #N/A
J2001.002027 |  | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-07 11:09 | 2020-01-07 11:31 | 22.7 | 1 | 1 | 22.7 | 1 | CANCELLED | 57 | CANCELLED | MUSTANG | 409 E.MEADOW-LN CT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 128550 | 115828 | 18201 | 4430 | 2.6395e-05 | 1.1628e-06 | 22.7 | 1 | 308 | Customer | 47171 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2022
J2001.002034 | PD-01072020-00281 | SOUTHERN | ARDMORE | 5124:BERWYN | BERWYN_2423 | 512423 | 2020-01-07 11:45 | 2020-01-07 12:30 | 45.37 | 6 | 2 | 514.8339 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | SPRINGER | 77/AIRPARK RD .25E.25N | CMI_NORMAL | NO | NO | NO | 860005 | 77518 | 23563 | 1034 | 774 | 0.00059864 | 6.9767e-06 | 85.8056 | 1 | 310 | Tap | 1448 | Fuse | FuseOH | RANDAL G CALLAWAY | 580-220-8449 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002035 |  | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-01-07 11:47 | 2020-01-07 13:50 | 123.47 | 2 | 1 | 214.2167 | 4 | DETERIORATION | 12 | POLE | EL RENO | 1/8 MW HWY 81 ON NS JONES RD | CMI_PLANNED | YES | NO | NO | 860005 | 128550 | 12722 | 6933 | 1822 | 0.00024909 | 2.3256e-06 | 107.1083 | 1 | 308 | Load | 73009 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002036 | PD-01072020-00275 | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_621 | 880621 | 2020-01-07 11:49 | 2020-01-07 14:00 | 130.92 | 1 | 1 | 130.9167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | GUTHRIE | 5322 S DIVISION | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 167961 | 19793 | 5155 | 1875 | 0.00015223 | 1.1628e-06 | 130.9167 | 1 | 310 | Load | 79434 | Load | Tran3phPadWye | JOSEPH WAYNE POOL | 405-919-2253 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002046 |  | NORTHWEST | ENID | 4219:BUNCH CREEK | BUNCH CREEK 41 | 421941 | 2020-01-07 11:57 | 2020-01-07 14:43 | 165.82 | 10 | 2 | 1638.6667 | 4 | DETERIORATION | 5 | SWITCH - AIR | GARBER | N 126th ST and E Robertson | CMI_PLANNED | YES | NO | NO | 860005 | 53482 | 37556 | 910 | 910 | 0.0019054 | 1.1628e-05 | 163.8667 | 1 | 308 | Mainline | 373735 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002051 | PD-01072020-00298 | NORTHEAST | SAPULPA | 3220:KELLYVILLE | KELLYVILLE_2024 | 322024 | 2020-01-07 12:04 | 2020-01-07 14:42 | 157.67 | 3 | 3 | 456.875 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | SAPULPA | 1+1/2W.OF HWY 66 ON HWY 33. | CMI_NORMAL | NO | NO | NO | 860005 | 73898 | 40689 | 2550 | 1580 | 0.00053125 | 3.4884e-06 | 152.2917 | 1 | 310 | Load | 18853 | Load | Tran1phOH | GREGORY R HOOVER | 918-261-6803 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2020
J2001.002056 |  | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1724 | 911724 | 2020-01-07 12:25 | 2020-01-07 18:06 | 341.2 | 1 | 1 | 341.2159 | 4 | DETERIORATION | 12 | POLE | BARLING | 1406 CHAD COLLEY BL | CMI_PLANNED | YES | NO | NO | 860005 | 82100 | 61125 | 4235 | 611 | 0.00039676 | 1.1628e-06 | 341.2159 | 1 | 308 | Load | 314641 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-07 | 2020 |  | #N/A
J2001.002059 | PD-01072020-00307 | METRO EAST | EAST | 8471:NE 30TH ST | NE_30TH_ST_7122 | 847122 | 2020-01-07 12:32 | 2020-01-07 13:05 | 32.75 | 1 | 1 | 30.3833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | FOREST PARK | 4900 N.COLTRANE RD | CMI_NORMAL | NO | NO | NO | 860005 | 114193 | 71092 | 2396 | 766 | 3.5329e-05 | 1.1628e-06 | 30.3833 | 1 | 310 | Load | 9044 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | OK - 2022
J2001.002058 |  | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3723 | 833723 | 2020-01-07 12:33 | 2020-01-07 12:33 | 0.07 | 325 | 0 | 21.6667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 8423 N CLASSEN BLVD | CMI_MOMENTARY | YES | NO | NO | 860005 | 167961 | 148168 | 5754 | 325 | 2.5194e-05 | 0.0003779 | 0.066667 | 1 | 0 | Feeder | 84th ST_3723 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002060 |  | METRO WEST | WEST | 8342:BRADEN PARK | BRADEN_PARK_4223 | 834223 | 2020-01-07 12:34 | 2020-01-07 16:42 | 248.82 | 1 | 1 | 153 | 3 | DAMAGED BY PUBLIC | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 12901 N. MACARTHUR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 128550 | 115828 | 3396 | 1781 | 0.00017791 | 1.1628e-06 | 153 | 1 | 310 | Customer | 70867 | Load | Tran1phPad | Crew | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2022
J2001.002072 |  | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1722 | 911722 | 2020-01-07 12:34 | 2020-01-07 15:25 | 170.83 | 3 | 3 | 497.9 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 9100 ROYALRIDGE DR | CMI_PLANNED | YES | NO | NO | 860005 | 82100 | 61125 | 4235 | 1473 | 0.00057895 | 3.4884e-06 | 165.9667 | 1 | 308 | Load | 568 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-07 | 2020 |  | #N/A
J2001.002063 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2263 | 852263 | 2020-01-07 12:38 | 2020-01-07 12:48 | 10.07 | 1 | 1 | 10.0667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | JONES | 12655 MONTANA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 114193 | 71092 | 11612 | 1526 | 1.1705e-05 | 1.1628e-06 | 10.0667 | 1 | 310 | Load | 325441 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2021
J2001.002064 | PD-01072020-00314 | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_622 | 770622 | 2020-01-07 12:40 | 2020-01-07 13:34 | 53.93 | 1 | 1 | 53.5024 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | BRISTOW | 3MN .5ME BRISTOW | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 73898 | 40689 | 3776 | 2006 | 6.2212e-05 | 1.1628e-06 | 53.5024 | 1 | 310 | Customer | 16405 | Load | Tran1phOH | GREGORY R HOOVER | 918-261-6803 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | #N/A
J2001.002066 | PD-01072020-00312 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-01-07 12:42 | 2020-01-07 13:39 | 56.72 | 1 | 1 | 55.2667 | 4 | DETERIORATION | 28 | CROSSARM | DEL CITY | 2321 EAGLE DR | CMI_NORMAL | NO | NO | NO | 860005 | 158943 | 102043 | 7408 | 2235 | 6.4263e-05 | 1.1628e-06 | 55.2667 | 1 | 320 | Customer | 13885 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2022
J2001.002069 |  | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_863 | 550863 | 2020-01-07 12:43 | 2020-01-07 13:54 | 71.48 | 6 | 3 | 369 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | MEAD | Hwy 69 & 75 5W NS | CMI_PLANNED | YES | NO | NO | 860005 | 77518 | 15465 | 1101 | 621 | 0.00042907 | 6.9767e-06 | 61.5 | 1 | 308 | Tap | 301887 | Fuse | FuseOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002067 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5923 | 835923 | 2020-01-07 12:45 | 2020-01-07 13:48 | 62.78 | 3 | 3 | 148.05 | 4 | DETERIORATION | 2 | TRANSFORMER OH | YUKON | 1380 W Main Street | CMI_PLANNED | YES | NO | NO | 860005 | 128550 | 115828 | 6411 | 1150 | 0.00017215 | 3.4884e-06 | 49.35 | 1 | 308 | Load | 16988 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | #N/A
J2001.002068 | PD-01072020-00318 | METRO WEST | WEST | 8222:CZECH HALL | CZECH_HALL_2229 | 822229 | 2020-01-07 12:46 | 2020-01-07 13:22 | 36.43 | 1 | 1 | 36.4333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 300 MARRGATE DR LOT 24,BLK 23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 128550 | 115828 | 8592 | 997 | 4.2364e-05 | 1.1628e-06 | 36.4333 | 1 | 320 | Customer | 76318 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002074 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6324 | 816324 | 2020-01-07 12:46 | 2020-01-07 14:08 | 82.13 | 9 | 6 | 254.1 | 4 | DETERIORATION | 2 | TRANSFORMER OH | MOORE | 1416 SUNRISE DR | CMI_PLANNED | YES | NO | NO | 860005 | 158943 | 102043 | 11809 | 2048 | 0.00029546 | 1.0465e-05 | 28.2333 | 1 | 308 | Load | 33227 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2021
J2001.002076 | PD-01072020-00317 | METRO EAST | SHAWNEE | 7409:MCLOUD | MCLOUD_922 | 740922 | 2020-01-07 12:53 | 2020-01-07 13:53 | 60.2 | 1 | 1 | 56.9167 | 4 | DETERIORATION | 20 | FUSE BARREL | MCLOUD | 1/2MW ARENA RD SS SE 15 | CMI_NORMAL | NO | NO | NO | 860005 | 114193 | 22067 | 2027 | 1208 | 6.6182e-05 | 1.1628e-06 | 56.9167 | 1 | 310 | Load | 21158 | Load | Tran1phOH | BRYAN K TATUM | 405-659-0746 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | OK - 2021
J2001.002075 | PD-01072020-00322 | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-01-07 12:54 | 2020-01-07 15:20 | 146.38 | 1 | 1 | 147.1575 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 11400 COYOTE CRK RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 158943 | 56900 | 4204 | 3066 | 0.00017111 | 1.1628e-06 | 147.1575 | 1 | 310 | Customer | 205160 | Load | Tran1phPad | CONTRACTOR 17 DAVID ELLIOT INC | 405-625-6555 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002077 | PD-01072020-00324 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4862 | 824862 | 2020-01-07 12:55 | 2020-01-07 13:43 | 47.82 | 1 | 1 | 47.8167 | 3 | DAMAGED BY PUBLIC | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 611 SW.6 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 167961 | 148168 | 4186 | 127 | 5.56e-05 | 1.1628e-06 | 47.8167 | 1 | 310 | Load | 52456 | Load | Tran1phOH | PETER BILICKI | 619-726-8332 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2022
J2001.002078 | PD-01072020-00328 | NORTHWEST | ENID | 4210:MEDFORD | MEDFORD 22 | 421022 | 2020-01-07 13:00 | 2020-01-07 16:25 | 204.5 | 1 | 1 | 204.5 | 22 | WIND | 17 | JUMPER | RENFROW | RENFROW S-ROCK ISLAND,W-RR | CMI_NORMAL | NO | NO | NO | 860005 | 53482 | 37556 | 744 | 681 | 0.00023779 | 1.1628e-06 | 204.5 | 1 | 310 | Customer | 1770 | Load | TranOH3phDelta | PATRICK LYONS | 580-395-4171 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | #N/A
J2001.002083 | PD-01072020-00345 | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1823 | 931823 | 2020-01-07 13:19 | 2020-01-07 14:03 | 44.12 | 1 | 1 | 36.55 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ALMA | RUDY RD | CMI_NORMAL | NO | NO | NO | 860005 | 82100 | 61125 | 2834 | 1227 | 4.25e-05 | 1.1628e-06 | 36.55 | 1 | 310 | Customer | 1616 | Load | Tran1phOH | KRIS L HALMES | 479-430-9447 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | Ark - Series 2
J2001.002136 | PD-01072020-00494 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1221 | 831221 | 2020-01-07 13:28 | 2020-01-07 19:32 | 363.7 | 1 | 1 | 363.7 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | NICHOLS HILLS | 6500 N.HILLCREST AV | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860005 | 167961 | 148168 | 7734 | 987 | 0.0004229 | 1.1628e-06 | 363.7 | 1 | 310 | Load | 7181 | Load | TranOpenDelta | BEAU S HUDSON | 405-306-8284 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2022
J2001.002089 | PD-01072020-00382 | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5621 | 865621 | 2020-01-07 13:34 | 2020-01-07 14:41 | 66.6 | 1 | 1 | 66.6 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2145 SE.59 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 158943 | 102043 | 2746 | 537 | 7.7441e-05 | 1.1628e-06 | 66.6 | 1 | 320 | Customer | 36108 | Load | Tran1phPad | THOMAS E COLE | 405-623-9338 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002091 | PD-01072020-00379 | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1862 | 941862 | 2020-01-07 13:41 | 2020-01-07 15:47 | 126.15 | 1 | 1 | 124.5833 | 5 | ELECTRICAL TRACKING | 20 | FUSE BARREL | LAMAR | CEDARWOOD DRIVE | CMI_NORMAL | NO | NO | NO | 860005 | 82100 | 7526 | 729 | 729 | 0.00014486 | 1.1628e-06 | 124.5833 | 1 | 310 | Customer | 18845 | Load | Tran1phOH | KRIS L HALMES | 479-430-9447 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | Ark - Series 2
J2001.002097 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-07 13:57 | 2020-01-07 17:20 | 203.58 | 2 | 2 | 376.1833 | 4 | DETERIORATION | 12 | POLE | CLARKSVILLE | COUNTY RD 16 NO. 64 HWY-HARTMA | CMI_PLANNED | YES | NO | NO | 860005 | 82100 | 7526 | 1501 | 1198 | 0.00043742 | 2.3256e-06 | 188.0917 | 1 | 308 | Load | 2172 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-07 | 2020 |  | Ark - Series 2
J2001.002098 | PD-01072020-00424 | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1722 | 911722 | 2020-01-07 13:58 | 2020-01-07 17:41 | 223.38 | 1 | 1 | 223.3833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 8405 HWY 59T | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 82100 | 61125 | 4235 | 1473 | 0.00025975 | 1.1628e-06 | 223.3833 | 1 | 310 | Customer | 2002 | Load | Tran1phOH | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-07 | 2020 |  | #N/A
J2001.002099 | PD-01072020-00396 | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4529 | 824529 | 2020-01-07 14:03 | 2020-01-07 14:42 | 39.25 | 1 | 1 | 39.25 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 8324 W RENO AVE OKLAHOMA CITY 731277204 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 128550 | 115828 | 3402 | 257 | 4.5639e-05 | 1.1628e-06 | 39.25 | 1 | 310 | Customer | 65747 | Load | Tran3phWye | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002102 | PD-01072020-00410 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6522 | 836522 | 2020-01-07 14:12 | 2020-01-07 16:00 | 107.98 | 1 | 1 | 107.9833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6819 SAXON DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 128550 | 115828 | 7416 | 1859 | 0.00012556 | 1.1628e-06 | 107.9833 | 1 | 310 | Customer | 47373 | Load | Tran1phPad | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2021
J2001.002105 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-01-07 14:16 | 2020-01-07 16:23 | 126.57 | 2 | 0 | 184.3667 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | BIXBY | 18102 S.156 E.AV | CMI_PLANNED | YES | NO | NO | 860005 | 73898 | 40689 | 2743 | 1439 | 0.00021438 | 2.3256e-06 | 92.1833 | 1 | 0 | Load | 18887 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | OK - 2021
J2001.002109 | PD-01072020-00411 | NORTHWEST | ENID | 4112:CHESTNUT | CHESTNUT_1222 | 411222 | 2020-01-07 14:21 | 2020-01-07 15:14 | 52.57 | 1 | 1 | 51.7667 | 22 | WIND | 31 | CONDUCTOR SERVICE - OH | ENID | 2010 E PINE | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860005 | 53482 | 37556 | 2857 | 1745 | 6.0193e-05 | 1.1628e-06 | 51.7667 | 1 | 310 | Customer | 333 | Load | Tran1phOH | KEVIN N PERRYMAN | 601-528-2473 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | #N/A
J2001.002113 | PD-01072020-00429 | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_621 | 880621 | 2020-01-07 14:42 | 2020-01-07 16:00 | 78.15 | 1 | 1 | 78.15 | 23 | CUSTOMER EQUIPMENT | 53 | ON UPON ARRIVAL | GUTHRIE | 4080 Lynda Ln L2 B8 GREEN ACRES 4 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 167961 | 19793 | 5155 | 1875 | 9.0872e-05 | 1.1628e-06 | 78.15 | 1 | 310 | Customer | 72748 | Load | Tran1phPad | JIM R HEIDEN | 405-501-1680 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002116 |  | NORTHWEST | ENID | 4353:OTTER | OTTER_5341 | 435341 | 2020-01-07 14:42 | 2020-01-07 15:02 | 19.23 | 1 | 1 | 19.2333 | 1 | CANCELLED | 57 | CANCELLED | COVINGTON | 404 W MAINE ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 53482 | 37556 | 960 | 792 | 2.2364e-05 | 1.1628e-06 | 19.2333 | 1 | 308 | Customer | 6419 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2021
J2001.002115 | PD-01072020-00453 | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3821 | 913821 | 2020-01-07 14:58 | 2020-01-07 16:13 | 75.5 | 2 | 2 | 151 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 23 | FUSE - PRIMARY | FORT SMITH | 9th & Carnall | CMI_NORMAL | NO | NO | NO | 860005 | 82100 | 61125 | 2926 | 209 | 0.00017558 | 2.3256e-06 | 75.5 | 1 | 310 | Tap | 179115 | Fuse | FuseRiser | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-01-07 | 2020 |  | Ark - Series 2
J2001.002114 |  | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_622 | 880622 | 2020-01-07 14:58 | 2020-01-07 18:22 | 204.28 | 3 | 3 | 478.65 | 13 | PREMATURE FAILURE | 2 | TRANSFORMER OH | GUTHRIE | DREXEL + PERKINS | CMI_NORMAL | NO | NO | NO | 860005 | 167961 | 19793 | 5155 | 1161 | 0.00055657 | 3.4884e-06 | 159.55 | 1 | 310 | Load | 57867 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002119 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2525 | 912525 | 2020-01-07 15:03 | 2020-01-07 19:26 | 262.6 | 1 | 1 | 262.601 | 4 | DETERIORATION | 1 | TRANSFORMER UG | FORT SMITH | 4304 S.PHOENIX | CMI_PLANNED | YES | NO | NO | 860005 | 82100 | 61125 | 2732 | 198 | 0.00030535 | 1.1628e-06 | 262.601 | 1 | 308 | Load | 728 | Load | Tran3phPadWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | Ark - Series 2
J2001.002124 |  | NORTHWEST | ENID | 4518:MENO TAP | MENO TAP 22 | 451822 | 2020-01-07 15:04 | 2020-01-07 15:24 | 20.05 | 1 | 1 | 20.05 | 1 | CANCELLED | 57 | CANCELLED | MENO | 2 W, 1/2 N. OF LAHOMA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 53482 | 37556 | 1331 | 829 | 2.3314e-05 | 1.1628e-06 | 20.05 | 1 | 308 | Load | 10993 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002120 |  | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1823 | 931823 | 2020-01-07 15:05 | 2020-01-07 15:14 | 9.65 | 1 | 1 | 9.65 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ALMA | RUDY RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 82100 | 61125 | 2834 | 1227 | 1.1221e-05 | 1.1628e-06 | 9.65 | 1 | 310 | Customer | 1616 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | Ark - Series 2
J2001.002122 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3822 | 913822 | 2020-01-07 15:16 | 2020-01-07 15:51 | 34.6 | 8 | 0 | 169.8667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 1505 S.10 | CMI_PLANNED | YES | NO | NO | 860005 | 82100 | 61125 | 2926 | 106 | 0.00019752 | 9.3023e-06 | 21.2333 | 1 | 0 | Load | 57 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-07 | 2020 |  | Ark - Series 2
J2001.002123 | PD-01072020-00471 | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3829 | 913829 | 2020-01-07 15:18 | 2020-01-07 16:35 | 77.37 | 1 | 1 | 77.3667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 1515 S.S | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 82100 | 61125 | 2926 | 1182 | 8.9961e-05 | 1.1628e-06 | 77.3667 | 1 | 310 | Customer | 1523 | Load | Tran1phOH | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-07 | 2020 |  | Ark - Series 2
J2001.002125 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-01-07 15:31 | 2020-01-07 15:48 | 17.07 | 1 | 2 | 17.0667 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 2109 N.MCKINLEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 167961 | 148168 | 11095 | 2036 | 1.9845e-05 | 1.1628e-06 | 17.0667 | 1 | 310 | Customer | 27446 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2021
J2001.002128 | PD-01072020-00505 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-01-07 15:35 | 2020-01-07 16:50 | 75.35 | 1 | 1 | 75.35 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 1815 N.BRAUER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 167961 | 148168 | 11095 | 2036 | 8.7616e-05 | 1.1628e-06 | 75.35 | 1 | 310 | Customer | 27447 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2021
J2001.002129 |  | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-01-07 15:44 | 2020-01-07 21:12 | 327.92 | 3 | 3 | 980.3995 | 4 | DETERIORATION | 12 | POLE | EL RENO | 1/8W-HWY 81 + JONES RD | CMI_PLANNED | YES | NO | NO | 860005 | 128550 | 12722 | 6933 | 1822 | 0.00114 | 3.4884e-06 | 326.7998 | 1 | 310 | Tap | 19403 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002131 |  | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5023 | 865023 | 2020-01-07 15:46 | 2020-01-07 15:50 | 4.57 | 1 | 1 | 4.5667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 1629 MELODY DR | CMI_MOMENTARY | YES | NO | NO | 860005 | 114193 | 71092 | 8623 | 1268 | 5.31e-06 | 1.1628e-06 | 4.5667 | 1 | 310 | Customer | 11937 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2022
J2001.002137 | PD-01072020-00510 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3923 | 833923 | 2020-01-07 15:58 | 2020-01-07 17:01 | 63.37 | 1 | 2 | 63.3667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 5117 COLFAX PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 167961 | 148168 | 7846 | 1247 | 7.3682e-05 | 1.1628e-06 | 63.3667 | 1 | 310 | Customer | 21235 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2022
J2001.002140 |  | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-01-07 16:00 | 2020-01-07 17:41 | 101.22 | 3 | 1 | 286.05 | 4 | DETERIORATION | 12 | POLE | EL RENO | 1325 N.HWY-81 | CMI_PLANNED | YES | NO | NO | 860005 | 128550 | 12722 | 6933 | 1822 | 0.00033261 | 3.4884e-06 | 95.35 | 1 | 308 | Load | 34932 | Load | Tran1phOH | Contractor | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002138 |  | NORTHEAST | MUSKOGEE | 3326:JAMESVILLE | JAMESVILLE_2642 | 332642 | 2020-01-07 16:09 | 2020-01-07 18:04 | 115.1 | 1 | 0 | 103.6167 | 4 | DETERIORATION | 28 | CROSSARM | 0 | SOUTH OF SAND PLANT | CMI_PLANNED | YES | NO | NO | 860005 | 73898 | 33209 | 1549 | 725 | 0.00012048 | 1.1628e-06 | 103.6167 | 1 | 0 | Load | 190797 | Load | Tran3phWye | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | #N/A
J2001.002139 |  | NORTHWEST | ENID | 4210:MEDFORD | MEDFORD 22 | 421022 | 2020-01-07 16:09 | 2020-01-07 16:19 | 10.1 | 52 | 1 | 502.6667 | 4 | DETERIORATION | 27 | CUTOUT | MEDFORD | .5MN-HWY 11 + FRONT ST | CMI_NORMAL | NO | NO | NO | 860005 | 53482 | 37556 | 744 | 681 | 0.00058449 | 6.0465e-05 | 9.6667 | 1 | 310 | Mainline | 1028 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | #N/A
J2001.002145 | PD-01072020-00529 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-01-07 16:21 | 2020-01-07 17:15 | 53.53 | 1 | 1 | 53.5333 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 2020 N.MINNIE LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 167961 | 148168 | 9234 | 1940 | 6.2248e-05 | 1.1628e-06 | 53.5333 | 1 | 310 | Customer | 28280 | Load | Tran1phOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2021
J2001.002152 |  | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3723 | 833723 | 2020-01-07 16:34 | 2020-01-07 22:04 | 329.93 | 12 | 8 | 2550.8 | 3 | DAMAGED BY PUBLIC | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | 7005 N.WESTERN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 167961 | 148168 | 5754 | 325 | 0.002966 | 1.3953e-05 | 212.5667 | 1 | 308 | Mainline | 24861 | Fuse | FuseRiser | Crew | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002158 |  | NORTHWEST | ENID | 4353:OTTER | OTTER_5341 | 435341 | 2020-01-07 16:54 | 2020-01-07 17:15 | 21.38 | 1 | 1 | 21.3833 | 1 | CANCELLED | 57 | CANCELLED | COVINGTON | 404 W MAINE ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 53482 | 37556 | 960 | 792 | 2.4864e-05 | 1.1628e-06 | 21.3833 | 1 | 308 | Customer | 6419 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2021
J2001.002160 |  | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_522 | 560522 | 2020-01-07 16:54 | 2020-01-07 17:13 | 18.1 | 2 | 2 | 36.2 | 1 | CANCELLED | 57 | CANCELLED | PAOLI | PAOLI SR CITIZEN S CTR-HWY 145 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 77518 | 6195 | 2450 | 825 | 4.2093e-05 | 2.3256e-06 | 18.1 | 1 | 308 | Secondary | 25339 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | OK - 2022
J2001.002159 |  | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2029 | 862029 | 2020-01-07 17:08 | 2020-01-07 17:15 | 6.32 | 1 | 1 | 6.3167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 640.5 SE.20 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 158943 | 102043 | 4736 | 980 | 7.3449e-06 | 1.1628e-06 | 6.3167 | 1 | 310 | Customer | 54701 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002172 |  | METRO SOUTH | SOUTH | 8722:MILLENNIUM | MILLENNIUM_2229 | 872229 | 2020-01-07 17:44 | 2020-01-07 17:49 | 4.7 | 1 | 1 | 4.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 1305 12 AV NE. | CMI_MOMENTARY | YES | NO | NO | 860005 | 158943 | 56900 | 4204 | 774 | 5.4651e-06 | 1.1628e-06 | 4.7 | 1 | 310 | Customer | 44392 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002173 | PD-01072020-00561 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3925 | 833925 | 2020-01-07 18:29 | 2020-01-07 20:35 | 125.73 | 1 | 1 | 125.7333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 5310 WILLOWCLF RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 167996 | 148199 | 7845 | 2182 | 0.0001462 | 1.1628e-06 | 125.7333 | 1 | 310 | Customer | 38666 | Load | Tran1phPad | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2022
J2001.002176 | PD-01072020-00563 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-01-07 19:00 | 2020-01-07 19:48 | 47.77 | 1 | 1 | 47.7667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2109 N.MCKINLEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 167996 | 148199 | 11096 | 2036 | 5.5542e-05 | 1.1628e-06 | 47.7667 | 1 | 310 | Customer | 27446 | Load | Tran1phOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2021
J2001.002177 | PD-01072020-00564 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-07 19:41 | 2020-01-07 20:33 | 52.45 | 1 | 1 | 52.45 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MOUNTAINBURG | HWY 282 1/2 M N. OF HWY 71 | CMI_NORMAL | NO | NO | NO | 860005 | 82119 | 61134 | 3783 | 1201 | 6.0988e-05 | 1.1628e-06 | 52.45 | 1 | 310 | Load | 16306 | Load | Tran1phOH | KRIS L HALMES | 479-430-9447 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-01-07 | 2020 |  | Ark - Series 2
J2001.002178 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_769 | 870769 | 2020-01-07 20:04 | 2020-01-08 01:44 | 340.07 | 10 | 0 | 534.6667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | NORMAN | 115 E.GRAY | CMI_PLANNED | YES | NO | NO | 860005 | 158971 | 56907 | 11827 | 2299 | 0.0006217 | 1.1628e-05 | 53.4667 | 1 | 0 | Load | 39018 | Load | Tran3phWye | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002189 | PD-01072020-00574 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_869 | 830869 | 2020-01-07 20:33 | 2020-01-08 02:33 | 360.17 | 15 | 13 | 4690.75 | 11 | OVERLOAD | 1 | TRANSFORMER UG | OKLAHOMA CITY | 0 | CMI_NORMAL | NO | NO | NO | 860005 | 167996 | 148199 | 19348 | 2462 | 0.0054543 | 1.7442e-05 | 312.7167 | 1 | 310 | Mainline | 89722-2 | Switch | SwitchDefault | BRIAN E WHITE | 405-642-7075 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | #N/A
J2001.002181 |  | SOUTHERN | ADA | 5809:VANOSS | VANOSS_922 | 580922 | 2020-01-07 20:34 | 2020-01-07 21:02 | 27.87 | 1 | 1 | 27.8667 | 1 | CANCELLED | 57 | CANCELLED | STRATFORD | 510 GARVIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 77534 | 11504 | 978 | 978 | 3.2403e-05 | 1.1628e-06 | 27.8667 | 1 | 308 | Customer | 2227 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-07 | 2020 |  | OK - 2021
J2001.002190 |  | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-01-07 21:56 | 2020-01-07 22:20 | 24.03 | 2 | 2 | 48.0667 | 1 | CANCELLED | 57 | CANCELLED | ADA | 1024 E.7 PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 77534 | 11504 | 2517 | 1090 | 5.5891e-05 | 2.3256e-06 | 24.0333 | 1 | 308 | Secondary | 16156 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | #N/A
J2001.002193 | PD-01072020-00583 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4124 | 814124 | 2020-01-07 22:15 | 2020-01-08 03:43 | 327.83 | 448 | 168 | 145488 | 28 | OTHER (DESCRIBE) | 23 | FUSE - PRIMARY | OKLAHOMA CITY | W OF HARVEY N OF SW 40 | CMI_NORMAL | NO | NO | NO | 860005 | 158971 | 102064 | 5800 | 2009 | 0.16917 | 0.00052093 | 324.75 | 1 | 310 | Mainline | 36236 | Fuse | FuseOH | CAMERON L ALLEN | 405-517-2208 | [5 empty] | Other | N | DISTRIBUTION | 69kV | 2020-01-07 | 2020 |  | #N/A
J2001.002191 |  | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4124 | 814124 | 2020-01-07 22:15 | 2020-01-07 22:15 | 0 | 586 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | S WALKER AV & SW 46TH ST | CMI_MOMENTARY | YES | NO | NO | 860005 | 158971 | 102064 | 5800 | 2009 | 0 | 0.00068139 | 0 | 1 | 0 | Mainline | 337580 | Recloser | Rec3phElectronic | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-07 | 2020 |  | #N/A
J2001.002205 | PD-01082020-00001 | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-01-08 00:07 | 2020-01-08 04:55 | 287.53 | 1 | 1 | 277.65 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | ADA | 1024 E.7 PL | CMI_NORMAL | NO | NO | NO | 860005 | 77534 | 11504 | 2517 | 1090 | 0.00032285 | 1.1628e-06 | 277.65 | 1 | 310 | Customer | 16156 | Load | Tran1phOH | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002217 |  | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-01-08 01:32 | 2020-01-08 05:00 | 208.33 | 7 | 3 | 1354.9667 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | ADA | 1024 E.7 PL | CMI_NORMAL | NO | NO | NO | 860005 | 77534 | 11504 | 2517 | 1090 | 0.0015755 | 8.1395e-06 | 193.5667 | 1 | 310 | Load | 16156 | Load | Tran1phOH | OGE | [6 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002220 | PD-01082020-00006 | NORTHEAST | SAPULPA | 3208:TIBBENS ROAD | TIBBENS_RD_822 | 320822 | 2020-01-08 02:21 | 2020-01-08 03:45 | 84.32 | 1 | 1 | 84.3167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | KIEFER | 1E1N 1/4W OF KIEFER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860005 | 73916 | 40701 | 3138 | 523 | 9.8042e-05 | 1.1628e-06 | 84.3167 | 1 | 310 | Load | 91137 | Load | 0 | STEPHEN BURKS | 918-639-0130 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002223 |  | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-01-08 02:50 | 2020-01-08 04:59 | 128.9 | 12 | 12 | 1384.5 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | ADA | HIGHLAND+ALY S 6TH E | CMI_NORMAL | NO | NO | NO | 860005 | 77534 | 11504 | 2517 | 1090 | 0.0016099 | 1.3953e-05 | 115.375 | 1 | 310 | Tap | 4193 | Fuse | FuseOH | OGE | [6 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002224 | PD-01082020-00007 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_866 | 830866 | 2020-01-08 02:54 | 2020-01-08 08:30 | 335.5 | 1 | 1 | 326.3167 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | Lot 8/9 Muirfield Pl | CMI_NORMAL | NO | NO | NO | 860005 | 167996 | 148199 | 19348 | 4303 | 0.00037944 | 1.1628e-06 | 326.3167 | 1 | 310 | Load | 393701 | Load | Tran1phPad | DAVID M CLEMMONS | 405-777-8355 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002232 | PD-01082020-00011 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4121 | 814121 | 2020-01-08 04:25 | 2020-01-08 07:25 | 179.77 | 1 | 1 | 169.3333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 809 SW.56 | CMI_NORMAL | NO | NO | NO | 860082 | 158971 | 102064 | 5800 | 1201 | 0.00019688 | 1.1627e-06 | 169.3333 | 1 | 310 | Customer | 17175 | Load | Tran1phOH | GERARDO D SOTO | 405-758-6334 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002241 |  | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1723 | 911723 | 2020-01-08 05:55 | 2020-01-08 08:31 | 155.85 | 5 | 6 | 588.3052 | 4 | DETERIORATION | 2 | TRANSFORMER OH | BARLING | 702 11 | CMI_PLANNED | YES | NO | NO | 860082 | 82119 | 61134 | 4234 | 1622 | 0.00068401 | 5.8134e-06 | 117.661 | 1 | 310 | Load | 7276 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-08 | 2020 |  | #N/A
J2001.002242 | PD-01082020-00014 | METRO EAST | EAST | 8417:ROUND BARN | ROUND_BARN_1723 | 841723 | 2020-01-08 05:56 | 2020-01-08 07:46 | 110.35 | 1 | 1 | 110.35 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | ARCADIA | L2 SKY RIDGE | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860082 | 114276 | 71165 | 1009 | 1009 | 0.0001283 | 1.1627e-06 | 110.35 | 1 | 320 | Customer | 72824 | Load | Tran1phPad | CONTRACTOR BHI51 DAVID ELLIOT INC | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002243 | PD-01082020-00015 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-01-08 06:03 | 2020-01-08 07:11 | 68.08 | 1 | 1 | 37.145 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2033 NW.21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 167996 | 148199 | 11096 | 2036 | 4.3188e-05 | 1.1627e-06 | 37.145 | 1 | 310 | Customer | 1117 | Load | Tran1phOH | DARREN L STOCKTON | 918-777-1697 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2021
J2001.002251 | PD-01082020-00029 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3924 | 833924 | 2020-01-08 06:47 | 2020-01-08 08:21 | 93.82 | 1 | 1 | 93.8167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 3500-3510 NW EXPRESSWAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 167996 | 148199 | 7845 | 795 | 0.00010908 | 1.1627e-06 | 93.8167 | 1 | 310 | Customer | 18709 | Load | Tran3phPadWye | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2022
J2001.002256 |  | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1821 | 931821 | 2020-01-08 06:59 | 2020-01-08 08:45 | 105.15 | 8 | 7 | 521.0667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | ALMA | 642 FAYETTEVILLE | CMI_PLANNED | YES | NO | NO | 860082 | 82119 | 61134 | 2834 | 821 | 0.00060583 | 9.3014e-06 | 65.1333 | 1 | 308 | Load | 9924 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | Ark - Series 2
J2001.002260 | PD-01082020-00044 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1422 | 311422 | 2020-01-08 07:29 | 2020-01-08 08:30 | 60.93 | 8 | 8 | 479.6 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MUSKOGEE | 2132 DENISON | CMI_NORMAL | NO | NO | NO | 860082 | 73916 | 33215 | 4560 | 1166 | 0.00055762 | 9.3014e-06 | 59.95 | 1 | 310 | Load | 9658 | Load | Tran1phOH | REID R WILLIAMS | 512-618-8800 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | OK - 2020
J2001.002262 | PD-01082020-00046 | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-01-08 07:46 | 2020-01-08 12:03 | 256.7 | 1694 | 604 | 87195.5167 | 3 | DAMAGED BY PUBLIC | 12 | POLE | OKLAHOMA CITY | East side of Westminster and 149th | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 158971 | 56907 | 4204 | 3066 | 0.10138 | 0.0019696 | 51.4732 | 1 | 310 | Mainline | 379120 | Recloser | Rec3phElectronic | DAVID M CLEMMONS | 405-777-8355 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002307 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-01-08 07:47 | 2020-01-08 09:20 | 93.65 | 3 | 2 | 127.75 | 3 | DAMAGED BY PUBLIC | 12 | POLE | OKLAHOMA CITY | 11112 S.PEEBLY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 158971 | 56907 | 4204 | 3066 | 0.00014853 | 3.488e-06 | 42.5833 | 1 | 310 | Load | 78930 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002268 | PD-01082020-00047 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1926 | 851926 | 2020-01-08 07:56 | 2020-01-08 08:45 | 49.5 | 1 | 1 | 33.65 | 3 | DAMAGED BY PUBLIC | 12 | POLE | CHOCTAW | 910 N WESTMINSTER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 114276 | 71165 | 12432 | 2125 | 3.9124e-05 | 1.1627e-06 | 33.65 | 1 | 310 | Customer | 246503 | Load | Tran1phOH | STEVEN CASKEY | 405-777-8855 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2021
J2001.002269 |  | NORTHEAST | MUSKOGEE | 3326:JAMESVILLE | JAMESVILLE_2642 | 332642 | 2020-01-08 07:58 | 2020-01-08 11:40 | 221.8 | 3 | 1 | 631.9 | 4 | DETERIORATION | 12 | POLE | HASKELL | HWY.104+ARK.RVR. | CMI_PLANNED | YES | NO | NO | 860082 | 73916 | 33215 | 1549 | 725 | 0.0007347 | 3.488e-06 | 210.6333 | 1 | 308 | Mainline | 27905 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002271 |  | METRO NORTH | NORTH | 8430:REMINGTON PARK | REMINGTON_PARK_3024 | 843024 | 2020-01-08 08:01 | 2020-01-08 16:44 | 523.17 | 2 | 0 | 319.3333 | 28 | OTHER (DESCRIBE) | 41 | OTHER | OKLAHOMA CITY | ES LAKE PK REST RMS | CMI_PLANNED | YES | NO | NO | 860082 | 167996 | 148199 | 848 | 179 | 0.00037128 | 2.3254e-06 | 159.6667 | 1 | 0 | Load | 29472 | Load | Tran1phOH | Crew | [6 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002273 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1325 | 911325 | 2020-01-08 08:02 | 2020-01-08 10:08 | 125.82 | 2 | 0 | 251.586 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 1001S ZERO | CMI_PLANNED | YES | NO | NO | 860082 | 82119 | 61134 | 1455 | 216 | 0.00029251 | 2.3254e-06 | 125.793 | 1 | 0 | Load | 10245 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | Ark - Series 2
J2001.002276 | PD-01082020-00050 | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6221 | 866221 | 2020-01-08 08:05 | 2020-01-08 09:15 | 69.72 | 1 | 1 | 69.7167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MIDWEST CITY | 10006.5 SE.15 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 114276 | 71165 | 7199 | 1292 | 8.1058e-05 | 1.1627e-06 | 69.7167 | 1 | 310 | Customer | 66414 | Load | Tran3phPadWye | STEVEN CASKEY | 405-777-8855 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002285 |  | NORTHEAST | SAPULPA | 7605:DRUMRIGHT | DRUMRIGHT_541 | 760541 | 2020-01-08 08:28 | 2020-01-08 10:58 | 150.13 | 4 | 0 | 598.9754 | 4 | DETERIORATION | 28 | CROSSARM | 0 | 2.5MS OILTON ON HWY 99 | CMI_PLANNED | YES | NO | NO | 860082 | 73916 | 40701 | 1691 | 322 | 0.00069642 | 4.6507e-06 | 149.7439 | 1 | 0 | Mainline | 5886 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002288 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-08 08:35 | 2020-01-08 10:26 | 111.38 | 9 | 6 | 684.6 | 4 | DETERIORATION | 2 | TRANSFORMER OH | COAL HILL | COAL HILL HA #3 | CMI_PLANNED | YES | NO | NO | 860082 | 82119 | 7528 | 1502 | 1199 | 0.00079597 | 1.0464e-05 | 76.0667 | 1 | 308 | Load | 12435 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-08 | 2020 |  | Ark - Series 2
J2001.002297 | PD-01082020-00193 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4823 | 824823 | 2020-01-08 08:37 | 2020-01-08 12:20 | 222.58 | 12 | 11 | 2642 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 3324 SW.21 | CMI_NORMAL | NO | NO | NO | 860082 | 167996 | 148199 | 4188 | 1795 | 0.0030718 | 1.3952e-05 | 220.1667 | 1 | 310 | Load | 5464 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2021
J2001.002292 | PD-01082020-00070 | NORTHEAST | MUSKOGEE | 3117:THREE RIVERS | THREE_RIVERS_1724 | 311724 | 2020-01-08 08:38 | 2020-01-08 09:05 | 27.02 | 1 | 1 | 24.8333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MUSKOGEE | NE46TH + EUFAULA-1850 N,840 E | CMI_NORMAL | NO | NO | NO | 860082 | 73916 | 33215 | 2831 | 170 | 2.8873e-05 | 1.1627e-06 | 24.8333 | 1 | 310 | Customer | 14358 | Load | Tran1phOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-01-08 | 2020 |  | #N/A
J2001.002304 | PD-01082020-00084 | ARKANSAS | POTEAU | 3516:TARBY | TARBY_1625 | 351625 | 2020-01-08 08:40 | 2020-01-08 09:47 | 66.78 | 1 | 2 | 64.8833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | POTEAU | .5ME ABM DR NS RD | CMI_NORMAL | NO | NO | NO | 860082 | 82119 | 13457 | 1671 | 1193 | 7.5439e-05 | 1.1627e-06 | 64.8833 | 1 | 310 | Load | 15281 | Load | Tran1phOH | TOBY C MEAD | 918-658-5596 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-01-08 | 2020 |  | #N/A
J2001.002301 |  | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2824 | 312824 | 2020-01-08 08:49 | 2020-01-08 09:21 | 32.17 | 1 | 1 | 32.1667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 312 N.L | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 73916 | 33215 | 5271 | 1609 | 3.74e-05 | 1.1627e-06 | 32.1667 | 1 | 310 | Customer | 11059 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-08 | 2020 |  | OK - 2020
J2001.002305 |  | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1621 | 581621 | 2020-01-08 08:56 | 2020-01-08 18:09 | 553.03 | 1 | 0 | 545.3333 | 3 | DAMAGED BY PUBLIC | 12 | POLE | ADA | ALLEY E CONSTANT S MAIN | CMI_PLANNED | YES | NO | NO | 860082 | 77534 | 11504 | 3457 | 1807 | 0.00063405 | 1.1627e-06 | 545.3333 | 1 | 0 | Load | 25526 | Load | Tran3phWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002306 |  | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1621 | 581621 | 2020-01-08 08:56 | 2020-01-08 18:09 | 552.63 | 9 | 10 | 4931.85 | 3 | DAMAGED BY PUBLIC | 12 | POLE | ADA | 310 E.12 | CMI_PLANNED | YES | NO | NO | 860082 | 77534 | 11504 | 3457 | 1807 | 0.0057342 | 1.0464e-05 | 547.9833 | 1 | 310 | Load | 1436 | Load | Tran3phWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002308 |  | METRO SOUTH | SOUTH | 8728:CHERRY CREEK | CHERRY_CREEK_2829 | 872829 | 2020-01-08 08:57 | 2020-01-08 12:01 | 183.48 | 7 | 6 | 783.3 | 4 | DETERIORATION | 1 | TRANSFORMER UG | NORMAN | 502 PINEY OAK | CMI_PLANNED | YES | NO | NO | 860082 | 158971 | 56907 | 7100 | 1147 | 0.00091073 | 8.1388e-06 | 111.9 | 1 | 310 | Load | 52933 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002314 |  | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2624 | 862624 | 2020-01-08 09:08 | 2020-01-08 09:25 | 17.23 | 1 | 1 | 17.2333 | 1 | CANCELLED | 57 | CANCELLED | DEL CITY | 4709 NEWPORT DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 158971 | 102064 | 7409 | 1262 | 2.0037e-05 | 1.1627e-06 | 17.2333 | 1 | 310 | Customer | 20484 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002316 | PD-01082020-00096 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2024 | 822024 | 2020-01-08 09:08 | 2020-01-08 09:47 | 38.98 | 1 | 1 | 36.3833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2204 NW.12 | CMI_NORMAL | NO | NO | NO | 860082 | 167996 | 148199 | 6031 | 1774 | 4.2302e-05 | 1.1627e-06 | 36.3833 | 1 | 310 | Customer | 2998 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | OK - 2020
J2001.002319 |  | METRO EAST | SHAWNEE | 7432:ST GREGORY | ST_GREGORY_3231 | 743231 | 2020-01-08 09:17 | 2020-01-08 10:46 | 88.23 | 6 | 1 | 299.6 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | SHAWNEE | 311 E.GEORGIA | CMI_PLANNED | YES | NO | NO | 860082 | 114276 | 22072 | 4089 | 1203 | 0.00034834 | 6.9761e-06 | 49.9333 | 1 | 308 | Load | 7893 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002326 |  | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1373 | 831373 | 2020-01-08 09:35 | 2020-01-08 11:02 | 87.33 | 1 | 1 | 42.9833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 10500 HEFNER RD | CMI_PLANNED | YES | NO | NO | 860082 | 128574 | 115850 | 7866 | 4090 | 4.9976e-05 | 1.1627e-06 | 42.9833 | 1 | 308 | Load | 18734 | Load | TranOpenDelta | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002327 |  | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_623 | 870623 | 2020-01-08 09:36 | 2020-01-08 09:41 | 5.6 | 1 | 1 | 5.6 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 538 CHAUTAUQUA AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 158971 | 56907 | 7363 | 1898 | 6.511e-06 | 1.1627e-06 | 5.6 | 1 | 310 | Customer | 48011 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2021
J2001.002330 | PD-01082020-00140 | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3421 | 843421 | 2020-01-08 09:36 | 2020-01-08 10:30 | 53.67 | 1 | 1 | 53.6667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4701 N.EVEREST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 167996 | 148199 | 1224 | 498 | 6.2397e-05 | 1.1627e-06 | 53.6667 | 1 | 310 | Customer | 10341 | Load | TranOpenDelta | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002331 | PD-01082020-00166 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6524 | 836524 | 2020-01-08 09:37 | 2020-01-08 10:30 | 53.42 | 1 | 1 | 53.4167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 6904 ST-MARYS PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 128574 | 115850 | 7416 | 1651 | 6.2106e-05 | 1.1627e-06 | 53.4167 | 1 | 310 | Customer | 24780 | Load | Tran1phOH | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002333 | PD-01082020-00129 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_623 | 870623 | 2020-01-08 09:41 | 2020-01-08 10:14 | 33.3 | 1 | 1 | 33.3 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 538 CHAUTAUQUA AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 158971 | 56907 | 7363 | 1898 | 3.8717e-05 | 1.1627e-06 | 33.3 | 1 | 310 | Customer | 48011 | Load | Tran1phOH | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2021
J2001.002337 |  | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1722 | 911722 | 2020-01-08 09:49 | 2020-01-08 12:17 | 148.13 | 6 | 4 | 854.5 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 9200 ROYALRIDGE DR | CMI_PLANNED | YES | NO | NO | 860082 | 82119 | 61134 | 4234 | 1473 | 0.00099351 | 6.9761e-06 | 142.4167 | 1 | 308 | Load | 585 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-08 | 2020 |  | #N/A
J2001.002341 | PD-01082020-00143 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1422 | 311422 | 2020-01-08 09:51 | 2020-01-08 10:06 | 15.38 | 1 | 1 | 15.3833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MUSKOGEE | 2132 DENISON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 73916 | 33215 | 4560 | 1166 | 1.7886e-05 | 1.1627e-06 | 15.3833 | 1 | 310 | Customer | 9658 | Load | Tran1phOH | REID R WILLIAMS | 512-618-8800 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | OK - 2020
J2001.002349 |  | METRO WEST | WEST | 8158:SARA | SARA_5864 | 815864 | 2020-01-08 10:07 | 2020-01-08 16:42 | 395.32 | 2 | 2 | 375.3333 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2801 N FRISCO RD | CMI_PLANNED | YES | NO | NO | 860082 | 128574 | 115850 | 18207 | 4806 | 0.00043639 | 2.3254e-06 | 187.6667 | 1 | 308 | Load | 30354 | Load | Tran1phOH | OGE | [6 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2022
J2001.002351 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-01-08 10:12 | 2020-01-08 10:40 | 28.2 | 15 | 0 | 422.8143 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | BIXBY | S SIDE MOBILE VILL | CMI_PLANNED | YES | NO | NO | 860082 | 73916 | 40701 | 2743 | 1439 | 0.0004916 | 1.744e-05 | 28.1876 | 1 | 0 | Load | 42691 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | OK - 2021
J2001.002353 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-08 10:15 | 2020-01-08 13:22 | 186.32 | 1 | 0 | 158.3833 | 4 | DETERIORATION | 12 | POLE | 0 | BETWEEN HARTMAN AND CLARKSVILE | CMI_PLANNED | YES | NO | NO | 860082 | 82119 | 7528 | 1502 | 1199 | 0.00018415 | 1.1627e-06 | 158.3833 | 1 | 0 | Load | 15788 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-08 | 2020 |  | Ark - Series 2
J2001.002357 | PD-01082020-00171 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3923 | 833923 | 2020-01-08 10:16 | 2020-01-08 10:54 | 37.72 | 1 | 1 | 37.7167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4942 N.PORTLAND | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 167996 | 148199 | 7845 | 1247 | 4.3852e-05 | 1.1627e-06 | 37.7167 | 1 | 310 | Customer | 28618 | Load | TranOpenDelta | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2022
J2001.002358 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-01-08 10:20 | 2020-01-08 15:44 | 324.68 | 1 | 1 | 100.05 | 3 | DAMAGED BY PUBLIC | 12 | POLE | OKLAHOMA CITY | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 0 | 0 | 0 | 0 | 0.00011633 | 1.1627e-06 | 100.05 | 1 | 310 | Customer |  | 0 | 0 | Crew | [5 empty] | 06/02/2020 note from burchamc. Reference J2001.002358 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Emailed Brent Miller with blank transformer and circuit #'s. Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002361 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-01-08 10:33 | 2020-01-08 11:34 | 61.08 | 1 | 1 | 61.0833 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 2109 N.MCKINLEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 167996 | 148199 | 11096 | 2036 | 7.102e-05 | 1.1627e-06 | 61.0833 | 1 | 310 | Customer | 27446 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2021
J2001.002364 | PD-01082020-00179 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3021 | 743021 | 2020-01-08 10:35 | 2020-01-08 11:13 | 38.48 | 2 | 2 | 60.1 | 22 | WIND | 34 | CONDUCTOR SECONDARY - OH | SHAWNEE | 219 N.KICKAPOO | CMI_NORMAL | NO | NO | NO | 860082 | 114276 | 22072 | 6633 | 1699 | 6.9877e-05 | 2.3254e-06 | 30.05 | 1 | 310 | Secondary | 4565 | Load | Tran1phOH | BRYAN K TATUM | 405-659-0746 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2021
J2001.002368 | PD-01082020-00188 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9923 | 829923 | 2020-01-08 10:42 | 2020-01-08 11:21 | 38.9 | 1 | 1 | 38.9 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 937 N.ROCKWELL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 128574 | 115850 | 9214 | 863 | 4.5228e-05 | 1.1627e-06 | 38.9 | 1 | 310 | Customer | 42432 | Load | Tran1phPad | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002370 | PD-01082020-00186 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1922 | 851922 | 2020-01-08 10:48 | 2020-01-08 11:34 | 46.08 | 1 | 1 | 46.0833 | 4 | DETERIORATION | 50 | CONNECTOR | MIDWEST CITY | 1109 JASMINE LN | CMI_NORMAL | NO | NO | NO | 860082 | 114276 | 71165 | 12432 | 1795 | 5.358e-05 | 1.1627e-06 | 46.0833 | 1 | 320 | Customer | 12926 | Load | Tran1phOH | STEVEN CASKEY | 405-777-8855 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002387 | PD-01082020-00216 | METRO NORTH | NORTH | 8430:REMINGTON PARK | REMINGTON_PARK_3022 | 843022 | 2020-01-08 11:20 | 2020-01-08 11:59 | 38.68 | 1 | 1 | 38.6833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6300 POST-OAK RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 167996 | 148199 | 848 | 669 | 4.4976e-05 | 1.1627e-06 | 38.6833 | 1 | 310 | Customer | 27692 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002397 | PD-01082020-00231 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6121 | 836121 | 2020-01-08 11:27 | 2020-01-08 13:45 | 138.13 | 10 | 12 | 1315.3333 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | 1602 NW.39 | CMI_NORMAL | NO | NO | NO | 860082 | 167996 | 148199 | 11096 | 1637 | 0.0015293 | 1.1627e-05 | 131.5333 | 1 | 310 | Load | 556 | Load | TranOpenDelta | JERRY CASNER | 405-620-0772 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2021
J2001.002389 | PD-01082020-00223 | METRO NORTH | NORTH | 8493:KELLEY AVE | KELLEY_AVENUE_9331 | 849331 | 2020-01-08 11:27 | 2020-01-08 12:05 | 37.53 | 1040 | 266 | 38861.3333 | 27 | TREE:NON PREVENTABLE | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | 9909 N KELLY AVE | CMI_NORMAL | NO | NO | NO | 860082 | 167996 | 148199 | 1481 | 1060 | 0.045183 | 0.0012092 | 37.3667 | 1 | 310 | Feeder | KELLY AV_9331 | Recloser | SubRecloser | [7 empty] | Vegetation | N | SUBSTATION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002398 | PD-01082020-00235 | METRO NORTH | NORTH | 8493:KELLEY AVE | KELLEY_AVENUE_9329 | 849329 | 2020-01-08 11:31 | 2020-01-08 12:18 | 46.65 | 1 | 1 | 46.65 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | NW 95TH AND E. BROADWAY EXT. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 167996 | 148199 | 1481 | 421 | 5.4239e-05 | 1.1627e-06 | 46.65 | 1 | 310 | Load | 209111 | Load | Tran3phPadWye | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002401 | PD-01082020-00226 | METRO WEST | WEST | 8222:CZECH HALL | CZECH_HALL_2224 | 822224 | 2020-01-08 11:34 | 2020-01-08 12:32 | 58.27 | 1 | 1 | 58.2667 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | YUKON | 311 BEECH AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 128574 | 115850 | 8592 | 1332 | 6.7745e-05 | 1.1627e-06 | 58.2667 | 1 | 310 | Customer | 21042 | Load | Tran1phOH | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002405 | PD-01082020-00317 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3731 | 833731 | 2020-01-08 11:36 | 2020-01-08 13:53 | 136.58 | 7 | 8 | 939.75 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1207 NW.86 | CMI_NORMAL | NO | NO | NO | 860082 | 167996 | 148199 | 5755 | 1902 | 0.0010926 | 8.1388e-06 | 134.25 | 1 | 310 | Load | 6905 | Load | TranOHDeltaSplitBank | KIRK REILLEY | 405-550-3062 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2020
J2001.002409 | PD-01082020-00253 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3731 | 833731 | 2020-01-08 11:36 | 2020-01-08 12:47 | 70.7 | 9 | 10 | 590.6333 | 22 | WIND | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1231 NW.86 | CMI_NORMAL | NO | NO | NO | 860082 | 167996 | 148199 | 5755 | 1902 | 0.00068672 | 1.0464e-05 | 65.6259 | 1 | 310 | Load | 4945 | Load | TranOpenDelta | KIRK REILLEY | 405-550-3062 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2020
J2001.002408 | PD-01082020-00241 | METRO NORTH | NORTH | 8430:REMINGTON PARK | REMINGTON_PARK_3022 | 843022 | 2020-01-08 11:41 | 2020-01-08 12:49 | 68.38 | 1 | 1 | 68.3833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 816 NE.73 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 167996 | 148199 | 848 | 669 | 7.9508e-05 | 1.1627e-06 | 68.3833 | 1 | 310 | Load | 4586 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002417 | PD-01082020-00242 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1922 | 851922 | 2020-01-08 11:46 | 2020-01-08 13:18 | 91.8 | 1 | 1 | 91.8 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MIDWEST CITY | 1285 N Air Depot Bl | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 114276 | 71165 | 12432 | 1795 | 0.00010673 | 1.1627e-06 | 91.8 | 1 | 310 | Customer | 318941 | Load | Tran3phPadWye | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002419 | PD-01082020-00247 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3925 | 833925 | 2020-01-08 11:49 | 2020-01-08 15:49 | 240.22 | 59 | 21 | 14157.05 | 22 | WIND | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | KINGSTON + NW.61 | CMI_NORMAL | NO | NO | NO | 860082 | 167996 | 148199 | 7845 | 2182 | 0.01646 | 6.8598e-05 | 239.95 | 1 | 310 | Mainline | 13046 | Fuse | FuseOH | BEAU S HUDSON | 405-306-8284 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2022
J2001.002422 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-08 12:04 | 2020-01-08 13:23 | 79.58 | 2 | 2 | 87.15 | 4 | DETERIORATION | 2 | TRANSFORMER OH | ARKOMA | 728 RIVERSIDE | CMI_PLANNED | YES | NO | NO | 860082 | 82119 | 61134 | 2928 | 872 | 0.00010133 | 2.3254e-06 | 43.575 | 1 | 308 | Load | 5221 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-08 | 2020 |  | Ark - Series 2
J2001.002423 | PD-01082020-00252 | SOUTHERN | ARDMORE | 5117:MARIETTA | MARIETTA_1721 | 511721 | 2020-01-08 12:05 | 2020-01-08 13:09 | 64.43 | 1 | 1 | 44.1 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | ARDMORE | 77 & LODGE RD 1.1S, 250'' E | CMI_NORMAL | NO | NO | NO | 860082 | 77534 | 23565 | 1594 | 637 | 5.1274e-05 | 1.1627e-06 | 44.1 | 1 | 310 | Load | 355693 | Load | Tran1phPad | GARRETT YOUNG | 580-276-6194 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002443 | PD-01082020-00283 | ARKANSAS | OZARK | 9413:RAZORBACK | RAZORBACK_1362 | 941362 | 2020-01-08 12:27 | 2020-01-08 13:36 | 68.98 | 37 | 20 | 2697.9167 | 28 | OTHER (DESCRIBE) | 23 | FUSE - PRIMARY | SCRANTON | 5TH + OLIVE | CMI_NORMAL | NO | NO | NO | 860082 | 82119 | 7528 | 396 | 396 | 0.0031368 | 4.3019e-05 | 72.9167 | 1 | 310 | Mainline | 4288 | Fuse | FuseOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Other | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | Ark - Series 2
J2001.002439 | PD-01082020-00275 | ARKANSAS | OZARK | 9413:RAZORBACK | RAZORBACK_1362 | 941362 | 2020-01-08 12:35 | 2020-01-08 14:04 | 89.63 | 1 | 1 | 65.0667 | 28 | OTHER (DESCRIBE) | 23 | FUSE - PRIMARY | SCRANTON | HWY 109 1 BLK S-HWY197SCRANTON | CMI_NORMAL | NO | NO | NO | 860082 | 82119 | 7528 | 396 | 396 | 7.5652e-05 | 1.1627e-06 | 65.0667 | 1 | 310 | Customer | 718 | Load | TranOpenDelta | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Other | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | Ark - Series 2
J2001.002449 |  | ARKANSAS | POTEAU | 3505:POTEAU | POTEAU_522 | 350522 | 2020-01-08 12:36 | 2020-01-08 13:05 | 29.08 | 13 | 6 | 362.4833 | 4 | DETERIORATION | 12 | POLE | POTEAU | AUSTIN AND WHITNEY | CMI_PLANNED | YES | NO | NO | 860082 | 82119 | 13457 | 2295 | 358 | 0.00042145 | 1.5115e-05 | 27.8833 | 1 | 310 | Tap | 27903 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002440 |  | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-01-08 12:37 | 2020-01-08 16:46 | 248.75 | 2 | 1 | 192.7333 | 28 | OTHER (DESCRIBE) | 10 | RELIABILITY | EL RENO | HWY 81-BRITTON ROAD | CMI_PLANNED | YES | NO | NO | 860082 | 128574 | 12724 | 6933 | 1822 | 0.00022409 | 2.3254e-06 | 96.3667 | 1 | 308 | Tap | 7878 | Fuse | FuseOH | Crew | [6 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002447 |  | METRO NORTH | NORTH | 8493:KELLEY AVE | KELLEY_AVENUE_9331 | 849331 | 2020-01-08 12:40 | 2020-01-08 12:51 | 10.95 | 2 | 2 | 20.5333 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1024 SHAMROCK RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 167996 | 148199 | 1481 | 1060 | 2.3874e-05 | 2.3254e-06 | 10.2667 | 1 | 310 | Customer | 24824 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002452 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5923 | 835923 | 2020-01-08 12:59 | 2020-01-08 13:42 | 42.92 | 2 | 2 | 77.5 | 4 | DETERIORATION | 2 | TRANSFORMER OH | YUKON | 402 OAK | CMI_PLANNED | YES | NO | NO | 860082 | 128574 | 115850 | 6411 | 1150 | 9.0108e-05 | 2.3254e-06 | 38.75 | 1 | 308 | Load | 58034 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002457 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6121 | 836121 | 2020-01-08 13:07 | 2020-01-08 14:20 | 73.12 | 164 | 36 | 5103.1333 | 22 | WIND | 17 | JUMPER | OKLAHOMA CITY | NW 36 & MCKINLEY | CMI_NORMAL | NO | NO | NO | 860082 | 167996 | 148199 | 11096 | 1637 | 0.0059333 | 0.00019068 | 31.1167 | 1 | 310 | Mainline | 167000 | Switch | SwitchRiser | [7 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2021
J2001.002467 |  | NORTHEAST | SAPULPA | 3218:BEGGS | BEGGS_1829 | 321829 | 2020-01-08 13:26 | 2020-01-08 14:30 | 63.88 | 3 | 1 | 184.6 | 4 | DETERIORATION | 2 | TRANSFORMER OH | MOUNDS | .5W .5S MOUNDS | CMI_PLANNED | YES | NO | NO | 860082 | 73916 | 40701 | 1831 | 895 | 0.00021463 | 3.488e-06 | 61.5333 | 1 | 308 | Load | 44178 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2020
J2001.002469 | PD-01082020-00335 | METRO NORTH | NORTH | 8493:KELLEY AVE | KELLEY_AVENUE_9331 | 849331 | 2020-01-08 13:26 | 2020-01-08 14:09 | 42.58 | 1 | 1 | 42.5833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 809 NE.81 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 167996 | 148199 | 1481 | 1060 | 4.9511e-05 | 1.1627e-06 | 42.5833 | 1 | 310 | Customer | 28937 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002471 | PD-01082020-00334 | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_622 | 730622 | 2020-01-08 13:30 | 2020-01-08 15:25 | 115.32 | 7 | 4 | 714.7 | 5 | ELECTRICAL TRACKING | 21 | FUSE - TRANSFORMER | SEMINOLE | 520 W SIMPSON | CMI_NORMAL | NO | NO | NO | 860082 | 114276 | 13584 | 4056 | 1250 | 0.00083097 | 8.1388e-06 | 102.1 | 1 | 310 | Load | 2023 | Load | Tran1phOH | KEVIN M RICH | 405-802-2121 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2020
J2001.002484 | PD-01082020-00352 | METRO EAST | EAST | 8471:NE 30TH ST | NE_30TH_ST_7121 | 847121 | 2020-01-08 13:46 | 2020-01-08 15:30 | 103.6 | 6 | 7 | 605.25 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 4236 NE.20 | CMI_NORMAL | NO | NO | NO | 860082 | 114276 | 71165 | 2396 | 342 | 0.00070371 | 6.9761e-06 | 100.875 | 1 | 310 | Load | 26098 | Load | Tran1phOH | KYLE L GOODIN | 405-426-9802 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | OK - 2022
J2001.002478 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-08 13:50 | 2020-01-08 16:57 | 186.9 | 1 | 1 | 183.4333 | 4 | DETERIORATION | 12 | POLE | HARTMAN | HARTMAN AR 72840/W. OF SCHOOL | CMI_PLANNED | YES | NO | NO | 860082 | 82119 | 7528 | 1502 | 1199 | 0.00021327 | 1.1627e-06 | 183.4333 | 1 | 308 | Load | 8616 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-08 | 2020 |  | Ark - Series 2
J2001.002485 | PD-01082020-00362 | METRO NORTH | NORTH | 8493:KELLEY AVE | KELLEY_AVENUE_9331 | 849331 | 2020-01-08 13:59 | 2020-01-08 14:22 | 22.68 | 1 | 1 | 22.6833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 729 NE.KATHERINE PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 167996 | 148199 | 1481 | 1060 | 2.6373e-05 | 1.1627e-06 | 22.6833 | 1 | 310 | Customer | 18708 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002486 | PD-01082020-00367 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2624 | 862624 | 2020-01-08 14:01 | 2020-01-08 14:42 | 41.02 | 1 | 1 | 41.0167 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | DEL CITY | 4709 NEWPORT DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 158971 | 102064 | 7409 | 1262 | 4.7689e-05 | 1.1627e-06 | 41.0167 | 1 | 310 | Customer | 20484 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002508 | PD-01082020-00395 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1922 | 851922 | 2020-01-08 14:42 | 2020-01-08 15:58 | 76.47 | 45 | 51 | 3165.75 | 22 | WIND | 17 | JUMPER | MIDWEST CITY | .1MNNE.10 .4MEAIRDEPOT | CMI_NORMAL | NO | NO | NO | 860082 | 114276 | 71165 | 12432 | 1795 | 0.0036808 | 5.2321e-05 | 70.35 | 1 | 310 | Tap | 13713 | Fuse | FuseOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002511 | PD-01082020-00398 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2224 | 832224 | 2020-01-08 14:47 | 2020-01-08 17:05 | 138.32 | 1 | 1 | 138.3167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 3512 NW.28 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 167996 | 148199 | 9168 | 1427 | 0.00016082 | 1.1627e-06 | 138.3167 | 1 | 310 | Customer | 8666 | Load | Tran1phOH | PETER BILICKI | 619-726-8332 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002514 |  | NORTHWEST | ALVA | 4705:ALVA | ALVA_522 | 470522 | 2020-01-08 14:49 | 2020-01-08 15:03 | 14.72 | 1 | 1 | 14.7167 | 1 | CANCELLED | 57 | CANCELLED | ALVA | 324 FLYNN ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 53490 | 5515 | 2437 | 1119 | 1.7111e-05 | 1.1627e-06 | 14.7167 | 1 | 310 | Customer | 9309 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002519 | PD-01082020-00436 | METRO WEST | EL RENO | 8908:ROMAN NOSE | ROMAN_NOSE_847 | 890847 | 2020-01-08 15:03 | 2020-01-08 17:01 | 118.22 | 1 | 2 | 105.5 | 22 | WIND | 31 | CONDUCTOR SERVICE - OH | WATONGA | WATONGA>1MN-33 ON LAND WSR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860082 | 128574 | 12724 | 523 | 214 | 0.00012266 | 1.1627e-06 | 105.5 | 1 | 310 | Load | 34073 | Load | Tran1phOH | MICHAEL T MAHEN | 405-210-6029 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2020
J2001.002524 | PD-01082020-00425 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6024 | 836024 | 2020-01-08 15:05 | 2020-01-08 21:46 | 401.15 | 62 | 35 | 11202.3667 | 22 | WIND | 12 | POLE | BETHANY | NW 36/ MARKWELL AVE | CMI_NORMAL | NO | NO | NO | 860082 | 128574 | 115850 | 5503 | 1343 | 0.013025 | 7.2086e-05 | 180.6833 | 1 | 310 | Mainline | 13786 | Fuse | FuseOH | VEGETATION MGMT CONTRACTOR | 405-317-6576 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | OK - 2022
J2001.002522 |  | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6024 | 836024 | 2020-01-08 15:05 | 2020-01-08 15:05 | 0.03 | 1343 | 0 | 44.7667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 4315 N COUNCIL RD | CMI_MOMENTARY | YES | NO | NO | 860082 | 128574 | 115850 | 5503 | 1343 | 5.2049e-05 | 0.0015615 | 0.033333 | 1 | 0 | Feeder | WOODLAWN_6024 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-08 | 2020 |  | OK - 2022
J2001.002531 |  | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_523 | 320523 | 2020-01-08 15:19 | 2020-01-08 15:28 | 9.28 | 1 | 1 | 9.2833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SAPULPA | SHADY GROVE M/H PK:BLK A.LOT32 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 73916 | 40701 | 3834 | 1714 | 1.0794e-05 | 1.1627e-06 | 9.2833 | 1 | 310 | Customer | 43857 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | OK - 2022
J2001.002541 |  | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3925 | 833925 | 2020-01-08 15:22 | 2020-01-08 16:22 | 60.53 | 2 | 2 | 34.9667 | 22 | WIND | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | 6120 KINGSTON RD | CMI_NORMAL | NO | NO | NO | 860082 | 167996 | 148199 | 7845 | 2182 | 4.0655e-05 | 2.3254e-06 | 17.4833 | 1 | 308 | Load | 19565 | Load | Tran1phOH | Crew | [6 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2022
J2001.002534 | PD-01082020-00458 | NORTHEAST | SAPULPA | 7605:DRUMRIGHT | DRUMRIGHT_541 | 760541 | 2020-01-08 15:23 | 2020-01-08 17:19 | 115.57 | 1 | 1 | 108.535 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DRUMRIGHT | 49801 W. 163rd St. S.(E0750RD) | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 73916 | 40701 | 1691 | 322 | 0.00012619 | 1.1627e-06 | 108.535 | 1 | 310 | Load | 407126 | Load | Tran1phOH | GREGORY R HOOVER | 918-261-6803 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002535 |  | METRO WEST | WEST | 8158:SARA | SARA_5871 | 815871 | 2020-01-08 15:24 | 2020-01-08 16:41 | 77.17 | 8 | 2 | 213.3333 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | OKLAHOMA CITY | 3605 Canton Trail | CMI_PLANNED | YES | NO | NO | 860082 | 128574 | 115850 | 18207 | 5381 | 0.00024804 | 9.3014e-06 | 26.6667 | 1 | 308 | Load | 375364 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2022
J2001.002537 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5136 | 815136 | 2020-01-08 15:30 | 2020-01-08 15:30 | 0.02 | 1299 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 8101 S PENNSYLVANIA AVE | CMI_MOMENTARY | YES | NO | NO | 860082 | 158971 | 102064 | 13933 | 1299 | 0 | 0.0015103 | 0 | 1 | 0 | Feeder | PENNSYLV_5136 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-08 | 2020 |  | OK - 2021
J2001.002540 | PD-01082020-00451 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-01-08 15:35 | 2020-01-08 16:34 | 58.77 | 1 | 1 | 58.7667 | 4 | DETERIORATION | 50 | CONNECTOR | DEL CITY | 2513 MICKEY RD | CMI_NORMAL | NO | NO | NO | 860082 | 158971 | 102064 | 7409 | 2236 | 6.8327e-05 | 1.1627e-06 | 58.7667 | 1 | 320 | Customer | 32527 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2022
J2001.002559 |  | ARKANSAS | OZARK | 9412:ALTUS | ALTUS_1229 | 941229 | 2020-01-08 15:42 | 2020-01-08 20:08 | 265.9 | 1 | 1 | 221.8667 | 4 | DETERIORATION | 12 | POLE | OZARK | 4601 River Sand Rd | CMI_PLANNED | YES | NO | NO | 860082 | 82119 | 7528 | 863 | 863 | 0.00025796 | 1.1627e-06 | 221.8667 | 1 | 308 | Load | 387047 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-08 | 2020 |  | Ark - Series 2
J2001.002550 | PD-01082020-00456 | METRO SOUTH | SOUTH | 8722:MILLENNIUM | MILLENNIUM_2231 | 872231 | 2020-01-08 15:44 | 2020-01-08 16:55 | 70.9 | 2 | 2 | 100.0667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | NORMAN | NORMAN><1908 E. ROCKCREEK ROAD | CMI_NORMAL | NO | NO | NO | 860082 | 158971 | 56907 | 4204 | 2053 | 0.00011635 | 2.3254e-06 | 50.0333 | 1 | 310 | Load | 64601 | Load | Tran1phOH | THOMAS E COLE | 405-623-9338 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002564 |  | ARKANSAS | POTEAU | 3607:ROLAND ROAD | ROLAND_RD_721 | 360721 | 2020-01-08 15:47 | 2020-01-08 16:28 | 41.38 | 1 | 1 | 33.65 | 4 | DETERIORATION | 2 | TRANSFORMER OH | ROLAND | HY 64 WOODLND HL BL | CMI_NORMAL | NO | NO | NO | 860082 | 82119 | 13457 | 1135 | 1135 | 3.9124e-05 | 1.1627e-06 | 33.65 | 1 | 308 | Load | 11512 | Load | TranOpenDelta | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002555 | PD-01082020-00463 | METRO EAST | EAST | 8416:DUNJEE | DUNJEE_1621 | 841621 | 2020-01-08 15:52 | 2020-01-08 16:34 | 42.48 | 1 | 1 | 42.4833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | CHOCTAW | 1401 N.CHOCTAW RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 114276 | 71165 | 3539 | 1552 | 4.9395e-05 | 1.1627e-06 | 42.4833 | 1 | 310 | Customer | 37813 | Load | Tran1phOH | KYLE L GOODIN | 405-426-9802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002560 |  | SOUTHERN | DURANT | 5504:BUTTERFIELD | BUTTERFIELD_429 | 550429 | 2020-01-08 15:55 | 2020-01-08 16:00 | 5 | 1 | 1 | 5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DURANT | 708 W LIVE OAK | CMI_MOMENTARY | YES | NO | NO | 860082 | 77534 | 15473 | 3481 | 1270 | 5.8134e-06 | 1.1627e-06 | 5 | 1 | 310 | Customer | 12274 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002557 |  | ARKANSAS | OZARK | 9412:ALTUS | ALTUS_1229 | 941229 | 2020-01-08 15:55 | 2020-01-08 20:07 | 251.82 | 1 | 0 | 239.45 | 4 | DETERIORATION | 12 | POLE | 0 | 1 3/4M S HWY64 1/2M W. SUB | CMI_PLANNED | YES | NO | NO | 860082 | 82119 | 7528 | 863 | 863 | 0.0002784 | 1.1627e-06 | 239.45 | 1 | 0 | Load | 16550 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-08 | 2020 |  | Ark - Series 2
J2001.002558 |  | ARKANSAS | OZARK | 9412:ALTUS | ALTUS_1229 | 941229 | 2020-01-08 15:55 | 2020-01-08 20:07 | 251.9 | 1 | 0 | 241.75 | 4 | DETERIORATION | 12 | POLE | 0 | 1 3/4M S HWY64 1/2M W. SUB | CMI_PLANNED | YES | NO | NO | 860082 | 82119 | 7528 | 863 | 863 | 0.00028108 | 1.1627e-06 | 241.75 | 1 | 0 | Load | 16703 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-08 | 2020 |  | Ark - Series 2
J2001.002561 | PD-01082020-00472 | NORTHEAST | MUSKOGEE | 3325:WELLS | WELLS_2549 | 332549 | 2020-01-08 15:56 | 2020-01-08 22:14 | 378.38 | 1 | 1 | 375.6667 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | TEXANNA | LAKEWOOD PARK | CMI_NORMAL | NO | NO | NO | 860082 | 73916 | 33215 | 2372 | 1049 | 0.00043678 | 1.1627e-06 | 375.6667 | 1 | 310 | Load | 12294 | Load | Tran1phPad | STEVE K HIGHFILL | 918-869-2785 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | OK - 2021
J2001.002562 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-01-08 15:59 | 2020-01-08 16:20 | 21.55 | 1 | 1 | 17.3833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | BIXBY | 1/4 E. LEONARD SCHOOL | CMI_PLANNED | YES | NO | NO | 860082 | 73916 | 40701 | 2743 | 1439 | 2.0211e-05 | 1.1627e-06 | 17.3833 | 1 | 308 | Load | 20158 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | OK - 2021
J2001.002568 | PD-01082020-00484 | SOUTHERN | ADA | 5813:BYNG SPA | BYNG_SPA_1322 | 581322 | 2020-01-08 16:14 | 2020-01-08 17:27 | 73.17 | 1 | 1 | 62.45 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | BYNG | NEW BETHEL SUB DIV | CMI_NORMAL | NO | NO | NO | 860082 | 77534 | 11504 | 546 | 546 | 7.2609e-05 | 1.1627e-06 | 62.45 | 1 | 310 | Load | 16791 | Load | Tran1phOH | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002569 |  | SOUTHERN | HEALDTON | 5306:COUNTY LINE | COUNTY LINE 22 | 530622 | 2020-01-08 16:14 | 2020-01-08 16:27 | 12.73 | 1 | 1 | 12.7333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | HENNEPIN | 1 MI W HWY 7, .4N, WS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 77534 | 6784 | 755 | 413 | 1.4805e-05 | 1.1627e-06 | 12.7333 | 1 | 310 | Load | 28308 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002571 |  | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1424 | 311424 | 2020-01-08 16:17 | 2020-01-08 16:52 | 34.22 | 1 | 1 | 34.2167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 2414 ELGIN ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 73916 | 33215 | 4560 | 797 | 3.9783e-05 | 1.1627e-06 | 34.2167 | 1 | 310 | Customer | 505 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | OK - 2020
J2001.002573 |  | METRO WEST | WEST | 8157:MACARTHUR | MACARTHUR_5724 | 815724 | 2020-01-08 16:24 | 2020-01-08 18:36 | 131.8 | 1 | 0 | 104.8167 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | MACARTHUR/N.SW.15TH | CMI_PLANNED | YES | NO | NO | 860082 | 128574 | 115850 | 1853 | 1252 | 0.00012187 | 1.1627e-06 | 104.8167 | 1 | 0 | Tap | 6135 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002577 |  | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3024 | 743024 | 2020-01-08 16:37 | 2020-01-08 16:44 | 7.57 | 1 | 1 | 7.5667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SHAWNEE | 321 S MARKET SHAWNEE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 114276 | 22072 | 6633 | 1639 | 8.7976e-06 | 1.1627e-06 | 7.5667 | 1 | 310 | Customer | 6768 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002576 |  | NORTHWEST | ENID | 4518:MENO TAP | MENO TAP 21 | 451821 | 2020-01-08 16:38 | 2020-01-08 16:45 | 7.42 | 1 | 1 | 7.4167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | LACEY | 1.5E 5.5S AMES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 53490 | 37561 | 1331 | 502 | 8.6232e-06 | 1.1627e-06 | 7.4167 | 1 | 320 | Load | 8894 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002591 | PD-01082020-00540 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6522 | 836522 | 2020-01-08 17:25 | 2020-01-08 19:03 | 98.18 | 1 | 1 | 98.1833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6704 LYREWOOD LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 128574 | 115850 | 7416 | 1859 | 0.00011416 | 1.1627e-06 | 98.1833 | 1 | 310 | Customer | 38962 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2021
J2001.002592 |  | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-01-08 17:27 | 2020-01-08 17:49 | 22.5 | 2 | 2 | 10.4333 | 22 | WIND | 37 | CONDUCTOR PRIMARY - OH | EL RENO | 117 N.M | CMI_NORMAL | NO | NO | NO | 860082 | 128574 | 12724 | 6933 | 1822 | 1.2131e-05 | 2.3254e-06 | 5.2167 | 1 | 310 | Secondary | 41597 | Load | Tran1phOH | Crew | [6 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002593 |  | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-01-08 17:27 | 2020-01-08 18:02 | 34.42 | 16 | 2 | 74.9333 | 22 | WIND | 37 | CONDUCTOR PRIMARY - OH | EL RENO | 1/2 B.E."K" ON ROGERS | CMI_NORMAL | NO | NO | NO | 860082 | 128574 | 12724 | 6933 | 1822 | 8.7123e-05 | 1.8603e-05 | 4.6833 | 1 | 310 | Tap | 9962 | Fuse | FuseOH | [7 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002594 |  | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-01-08 17:28 | 2020-01-08 17:47 | 19.08 | 1 | 1 | 3.7667 | 22 | WIND | 37 | CONDUCTOR PRIMARY - OH | EL RENO | 116 S.M | CMI_NORMAL | NO | NO | NO | 860082 | 128574 | 12724 | 6933 | 1822 | 4.3794e-06 | 1.1627e-06 | 3.7667 | 1 | 310 | Customer | 41616 | Load | Tran1phOH | Crew | [6 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002600 |  | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_522 | 560522 | 2020-01-08 17:31 | 2020-01-08 17:48 | 16.95 | 1 | 1 | 16.95 | 1 | CANCELLED | 57 | CANCELLED | PAOLI | PAOLI SR CITIZEN S CTR-HWY 145 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 77534 | 6198 | 2452 | 826 | 1.9707e-05 | 1.1627e-06 | 16.95 | 1 | 308 | Customer | 25339 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | OK - 2022
J2001.002595 | PD-01082020-00536 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-01-08 17:38 | 2020-01-08 17:53 | 15.33 | 1 | 1 | 14.5 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ARDMORE | 3202 S. RANCHO LANE | CMI_NORMAL | NO | NO | NO | 860082 | 77534 | 23565 | 2205 | 1001 | 1.6859e-05 | 1.1627e-06 | 14.5 | 1 | 310 | Customer | 24199 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002598 | PD-01082020-00541 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4033 | 834033 | 2020-01-08 17:44 | 2020-01-08 20:58 | 194.5 | 1 | 1 | 194.5 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 7616 NW.102 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 128574 | 115850 | 10840 | 1115 | 0.00022614 | 1.1627e-06 | 194.5 | 1 | 320 | Customer | 65544 | Load | Tran1phPad | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002601 |  | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1922 | 851922 | 2020-01-08 17:53 | 2020-01-08 17:58 | 4.93 | 1 | 1 | 4.9333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 203 SHADYBROOK PL | CMI_MOMENTARY | YES | NO | NO | 860082 | 114276 | 71165 | 12432 | 1795 | 5.7359e-06 | 1.1627e-06 | 4.9333 | 1 | 310 | Customer | 40852 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002603 | PD-01082020-00543 | METRO EAST | SHAWNEE | 7432:ST GREGORY | ST_GREGORY_3229 | 743229 | 2020-01-08 18:00 | 2020-01-08 19:11 | 71.03 | 1 | 1 | 68.5167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | SHAWNEE | 13804 COKER RD | CMI_NORMAL | NO | NO | NO | 860082 | 114276 | 22072 | 4089 | 795 | 7.9663e-05 | 1.1627e-06 | 68.5167 | 1 | 310 | Load | 23873 | Load | Tran1phOH | KYLE L GOODIN | 405-426-9802 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002608 |  | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_522 | 560522 | 2020-01-08 18:20 | 2020-01-08 18:50 | 29.9 | 2 | 2 | 59.8 | 1 | CANCELLED | 57 | CANCELLED | PAOLI | PAOLI SR CITIZEN S CTR-HWY 145 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 77538 | 6199 | 2452 | 826 | 6.9528e-05 | 2.3254e-06 | 29.9 | 1 | 308 | Secondary | 25339 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | OK - 2022
J2001.002609 |  | METRO EAST | EAST | 8417:ROUND BARN | ROUND_BARN_1723 | 841723 | 2020-01-08 18:38 | 2020-01-08 18:45 | 6.32 | 1 | 1 | 6.3167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 10017 NE 146th St | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 114299 | 71177 | 1010 | 1010 | 7.3443e-06 | 1.1627e-06 | 6.3167 | 1 | 310 | Customer | 390697 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002610 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_861 | 830861 | 2020-01-08 18:51 | 2020-01-08 19:29 | 38.42 | 315 | 11 | 2047.5 | 22 | WIND | 17 | JUMPER | EDMOND | NEC-PENN + NW.234 | CMI_PLANNED | YES | NO | NO | 860082 | 168012 | 148215 | 19351 | 3925 | 0.0023806 | 0.00036624 | 6.5 | 1 | 310 | Mainline | 29519 | Fuse | FuseOH | [7 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002623 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_629 | 460629 | 2020-01-08 18:53 | 2020-01-08 19:13 | 19.63 | 1 | 1 | 19.6333 | 1 | CANCELLED | 57 | CANCELLED | WOODWARD | 924 MAIN WOODWARD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 53495 | 10415 | 5679 | 930 | 2.2827e-05 | 1.1627e-06 | 19.6333 | 1 | 308 | Customer | 11173 | Load | Tran3phWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002626 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_631 | 460631 | 2020-01-08 18:53 | 2020-01-08 18:53 | 0 | 1 | 1 | 0 | 1 | CANCELLED | 57 | CANCELLED | WOODWARD | 2910 ESSEX-WOODWARD | CMI_MOMENTARY | YES | NO | NO | 860082 | 53495 | 10415 | 5679 | 1170 | 0 | 1.1627e-06 | 0 | 1 | 308 | Load | 10938 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002627 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_622 | 460622 | 2020-01-08 18:53 | 2020-01-08 18:53 | 0 | 1 | 1 | 0 | 1 | CANCELLED | 57 | CANCELLED | WOODWARD | 1MN-TOWN SUB, .5MW-WOODWARD | CMI_MOMENTARY | YES | NO | NO | 860082 | 53495 | 10415 | 5679 | 765 | 0 | 1.1627e-06 | 0 | 1 | 308 | Load | 10684 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002628 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_622 | 460622 | 2020-01-08 18:53 | 2020-01-08 18:53 | 0 | 1 | 1 | 0 | 1 | CANCELLED | 57 | CANCELLED | WOODWARD | 1 1/4MN-WOODWARD + HWY 34 | CMI_MOMENTARY | YES | NO | NO | 860082 | 53495 | 10415 | 5679 | 765 | 0 | 1.1627e-06 | 0 | 1 | 308 | Load | 8524 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002625 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_622 | 460622 | 2020-01-08 18:53 | 2020-01-08 18:53 | 0 | 1 | 1 | 0 | 1 | CANCELLED | 57 | CANCELLED | WOODWARD | 312 E WEBSTER-WOODWARD | CMI_MOMENTARY | YES | NO | NO | 860082 | 53495 | 10415 | 5679 | 765 | 0 | 1.1627e-06 | 0 | 1 | 308 | Load | 13213 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002614 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_622 | 460622 | 2020-01-08 18:58 | 2020-01-08 18:58 | 0 | 2 | 2 | 0 | 1 | CANCELLED | 57 | CANCELLED | WOODWARD | E-10TH,S-WEBSTER AVE -WOODWARD | CMI_MOMENTARY | YES | NO | NO | 860082 | 53495 | 10415 | 5679 | 765 | 0 | 2.3254e-06 | 0 | 1 | 308 | Load | 10713 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002619 | PD-01082020-00548 | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_622 | 460622 | 2020-01-08 18:58 | 2020-01-08 19:37 | 39.07 | 1 | 1 | 39.0667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | WOODWARD | E-10TH,S-WEBSTER AVE -WOODWARD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 53495 | 10415 | 5679 | 765 | 4.5422e-05 | 1.1627e-06 | 39.0667 | 1 | 310 | Customer | 10713 | Load | TranOpenDelta | KEVIN D PETTIGREW | 580-216-6305 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002616 | PD-01082020-00547 | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_631 | 460631 | 2020-01-08 18:58 | 2020-01-08 20:10 | 71.93 | 1 | 1 | 71.9333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | WOODWARD | 3311.5 22ND-WOODWARD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 53495 | 10415 | 5679 | 1170 | 8.3635e-05 | 1.1627e-06 | 71.9333 | 1 | 310 | Customer | 12706 | Load | Tran1phPad | KEVIN D PETTIGREW | 580-216-6305 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002630 |  | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4123 | 814123 | 2020-01-08 19:13 | 2020-01-08 19:22 | 9.12 | 1 | 1 | 9.1167 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 29 SW.59 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 158979 | 102070 | 5801 | 1320 | 1.06e-05 | 1.1627e-06 | 9.1167 | 1 | 310 | Customer | 25018 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002633 |  | METRO NORTH | NORTH | 8347:WILSHIRE | WILSHIRE_4722 | 834722 | 2020-01-08 19:30 | 2020-01-08 23:29 | 238.88 | 6 | 11 | 1332.2 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2708 CAMBRIDGE CT | CMI_PLANNED | YES | NO | NO | 860082 | 168012 | 148215 | 4620 | 1588 | 0.0015489 | 6.9761e-06 | 222.0333 | 1 | 310 | Load | 14748 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2021
J2001.002635 | PD-01082020-00551 | SOUTHERN | SULPHUR | 5707:MILL CREEK | MILL CREEK 22 | 570722 | 2020-01-08 19:47 | 2020-01-09 04:46 | 538.55 | 4 | 3 | 2114.4 | 3 | DAMAGED BY PUBLIC | 12 | POLE | MILL CREEK | .75S MER AGG,.1W HWY12 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 77538 | 6809 | 210 | 19 | 0.0024584 | 4.6507e-06 | 528.6 | 1 | 311 | Tap | 8990 | Fuse | FuseOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002640 |  | NORTHWEST | ENID | 4158:FAIRMONT | FAIRMONT_5829 | 415829 | 2020-01-08 19:59 | 2020-01-08 20:16 | 17.35 | 1 | 1 | 17.35 | 1 | CANCELLED | 57 | CANCELLED | ENID | 2S 1W BRECK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 53495 | 37564 | 1640 | 1622 | 2.0172e-05 | 1.1627e-06 | 17.35 | 1 | 308 | Load | 3007 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2021
J2001.002643 |  | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_522 | 560522 | 2020-01-08 20:16 | 2020-01-08 20:33 | 17.08 | 2 | 2 | 34.1667 | 1 | CANCELLED | 57 | CANCELLED | PAOLI | PAOLI SR CITIZEN S CTR-HWY 145 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 77538 | 6199 | 2452 | 826 | 3.9725e-05 | 2.3254e-06 | 17.0833 | 1 | 308 | Secondary | 25339 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | OK - 2022
J2001.002644 | PD-01082020-00565 | NORTHWEST | ENID | 4414:HENNESSEY | HENNESSEY_1423 | 441423 | 2020-01-08 20:53 | 2020-01-08 22:11 | 77.67 | 1 | 1 | 2.0667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | HENNESSEY | 3ME MN C.H. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 53495 | 37564 | 1952 | 286 | 2.4029e-06 | 1.1627e-06 | 2.0667 | 1 | 310 | Load | 2803 | Load | Tran1phOH | RANDY D MASON | 580-977-8823 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002651 | PD-01082020-00567 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3022 | 743022 | 2020-01-08 21:30 | 2020-01-09 01:20 | 229.93 | 1 | 1 | 218.4667 | 22 | WIND | 17 | JUMPER | SHAWNEE | 720 E.INDEPENDENCE | CMI_NORMAL | NO | NO | NO | 860082 | 114299 | 22083 | 6637 | 2163 | 0.00025401 | 1.1627e-06 | 218.4667 | 1 | 310 | Customer | 7622 | Load | TranOpenDelta | DAVID M CLEMMONS | 405-777-8355 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | OK - 2020
J2001.002654 |  | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_522 | 560522 | 2020-01-08 21:59 | 2020-01-08 22:19 | 20.55 | 2 | 2 | 41.1 | 1 | CANCELLED | 57 | CANCELLED | PAOLI | PAOLI SR CITIZEN S CTR-HWY 145 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 77538 | 6199 | 2452 | 826 | 4.7786e-05 | 2.3254e-06 | 20.55 | 1 | 308 | Secondary | 25339 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | OK - 2022
J2001.002656 | PD-01082020-00568 | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_622 | 770622 | 2020-01-08 22:11 | 2020-01-08 23:29 | 77.8 | 9 | 11 | 671.1 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | BRISTOW | 703 E.4 | CMI_NORMAL | NO | NO | NO | 860082 | 73926 | 40710 | 3781 | 2009 | 0.00078027 | 1.0464e-05 | 74.5667 | 1 | 310 | Load | 41224 | Load | Tran1phOH | STEPHEN BURKS | 918-639-0130 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | #N/A
J2001.002662 |  | METRO SOUTH | SOUTH CENTRAL | 8194:WESTMOORE | WESTMOORE_9431 | 819431 | 2020-01-08 22:46 | 2020-01-08 22:54 | 8.15 | 1 | 1 | 8.15 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 605 SW 119TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 158979 | 102070 | 8099 | 1535 | 9.4758e-06 | 1.1627e-06 | 8.15 | 1 | 310 | Customer | 363276 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-08 | 2020 |  | #N/A
J2001.002663 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-08 22:51 | 2020-01-08 23:35 | 44.58 | 1 | 1 | 44.5833 | 16 | SUBSTATION OPERATION | 16 | LINE RECLOSER | MOUNTAINBURG | RURAL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 82136 | 61142 | 3787 | 1204 | 5.1836e-05 | 1.1627e-06 | 44.5833 | 1 | 310 | Load | 945 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-08 | 2020 |  | Ark - Series 2
J2001.002674 |  | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1024 | 311024 | 2020-01-08 23:57 | 2020-01-09 00:17 | 19.93 | 1 | 1 | 19.9333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 2110 NORTH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860082 | 73926 | 33216 | 2900 | 1391 | 2.3176e-05 | 1.1627e-06 | 19.9333 | 1 | 308 | Customer | 10488 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-08 | 2020 |  | OK - 2020
J2001.002675 | PD-01092020-00002 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-09 00:26 | 2020-01-09 03:03 | 156.53 | 2 | 1 | 307.0333 | 29 | TREES : GROW IN | 37 | CONDUCTOR PRIMARY - OH | MOUNTAINBURG | .9MW HWY 71 ON CARTWRIGHT MTN RD | CMI_NORMAL | NO | NO | NO | 860082 | 82136 | 61142 | 3787 | 1204 | 0.00035698 | 2.3254e-06 | 153.5167 | 1 | 310 | Mainline | 214620 | Fuse | FuseOH | KRIS L HALMES | 479-430-9447 | [5 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.002678 | PD-01092020-00004 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-01-09 00:36 | 2020-01-09 02:35 | 118.53 | 1 | 2 | 112.2833 | 12 | POOR CONNECTION | 50 | CONNECTOR | DEL CITY | 1912 S.HAMPTON DR | CMI_NORMAL | NO | NO | NO | 860082 | 158979 | 102070 | 7410 | 2237 | 0.00013055 | 1.1627e-06 | 112.2833 | 1 | 320 | Customer | 8718 | Load | Tran1phOH | DARREN L STOCKTON | 918-777-1697 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2022
J2001.002698 | PD-01092020-00005 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4821 | 824821 | 2020-01-09 04:31 | 2020-01-09 08:54 | 263.25 | 1 | 3 | 263.25 | 3 | DAMAGED BY PUBLIC | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 2109 W. SHERIDAN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 168012 | 148215 | 4189 | 242 | 0.00030604 | 1.1625e-06 | 263.25 | 1 | 310 | Customer | 1037 | Load | TranOpenDelta | DARREN L STOCKTON | 918-777-1697 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2022
J2001.002705 | PD-01092020-00008 | METRO WEST | WEST | 8158:SARA | SARA_5864 | 815864 | 2020-01-09 05:58 | 2020-01-09 08:08 | 130.1 | 1 | 2 | 40.6667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | TORRE PINES-HWY 92,SW 15 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 128586 | 115862 | 18216 | 4810 | 4.7276e-05 | 1.1625e-06 | 40.6667 | 1 | 310 | Customer | 87411 | Load | Tran1phOH | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2022
J2001.002706 | PD-01092020-00007 | SOUTHERN | HEALDTON | 5322:DUNDEE | DUNDEE 22 | 532222 | 2020-01-09 06:15 | 2020-01-09 13:46 | 450.73 | 1 | 1 | 450.7333 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | RINGLING | FORE ADDN LOT 22 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860195 | 77538 | 6784 | 1011 | 1000 | 0.00052399 | 1.1625e-06 | 450.7333 | 1 | 310 | Customer | 19884 | Load | Tran1phPad | MICHAEL D DICKINSON | 580-229-5532 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002713 | PD-01092020-00020 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_771 | 870771 | 2020-01-09 07:14 | 2020-01-09 09:34 | 139.78 | 1 | 1 | 139.7833 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | NOBLE | 903 MAGUIRE RD | CMI_NORMAL | NO | NO | NO | 860195 | 158979 | 56909 | 11828 | 1813 | 0.0001625 | 1.1625e-06 | 139.7833 | 1 | 310 | Customer | 36805 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002717 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-09 07:19 | 2020-01-09 07:57 | 37.7 | 1 | 1 | 30.1167 | 4 | DETERIORATION | 47 | ARRESTOR OH | FORT SMITH | CHAFFEE BLVD. | CMI_PLANNED | YES | NO | NO | 860195 | 82136 | 61142 | 2732 | 2120 | 3.5011e-05 | 1.1625e-06 | 30.1167 | 1 | 308 | Load | 202405 | Load | TranOH3phDelta | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.002715 | PD-01092020-00021 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1922 | 851922 | 2020-01-09 07:22 | 2020-01-09 10:17 | 174.68 | 6 | 8 | 1007.3 | 4 | DETERIORATION | 50 | CONNECTOR | MIDWEST CITY | 1109 JASMINE LN | CMI_NORMAL | NO | NO | NO | 860195 | 114299 | 71177 | 12437 | 1795 | 0.001171 | 6.9752e-06 | 167.8833 | 1 | 310 | Load | 12926 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002716 | PD-01092020-00022 | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5431 | 865431 | 2020-01-09 07:22 | 2020-01-09 12:34 | 311.55 | 1 | 2 | 24.9463 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | MOORE | 917 CRESTMOOR DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860195 | 158979 | 102070 | 9804 | 1377 | 2.9001e-05 | 1.1625e-06 | 24.9463 | 1 | 310 | Customer | 39593 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002721 | PD-01092020-00028 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7029 | 817029 | 2020-01-09 07:27 | 2020-01-09 10:30 | 183.48 | 1 | 2 | 165.0333 | 22 | WIND | 12 | POLE | MOORE | 3200 LARKSPUR LN | CMI_NORMAL | NO | NO | NO | 860195 | 158979 | 102070 | 9938 | 1757 | 0.00019186 | 1.1625e-06 | 165.0333 | 1 | 310 | Customer | 20883 | Load | Tran1phOH | COLBY T LLOYD | 405-312-0110 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2022
J2001.002719 |  | NORTHEAST | MUSKOGEE | 3326:JAMESVILLE | JAMESVILLE_2642 | 332642 | 2020-01-09 07:36 | 2020-01-09 12:57 | 320.55 | 3 | 1 | 980.45 | 4 | DETERIORATION | 12 | POLE | HASKELL | HWY.104+ARK.RVR. | CMI_PLANNED | YES | NO | NO | 860195 | 73926 | 33216 | 1549 | 725 | 0.0011398 | 3.4876e-06 | 326.8167 | 1 | 308 | Mainline | 27905 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-09 | 2020 |  | #N/A
J2001.002722 | PD-01092020-00035 | METRO EAST | CHANDLER | 7117:JACKTOWN | JACKTOWN_1742 | 711742 | 2020-01-09 07:49 | 2020-01-09 14:13 | 384.25 | 1 | 1 | 383.55 | 5 | ELECTRICAL TRACKING | 2 | TRANSFORMER OH | MEEKER | 1 W OF HWY 18 ON 62 1/8 N WS | CMI_NORMAL | NO | NO | NO | 860195 | 114299 | 7454 | 1011 | 828 | 0.00044589 | 1.1625e-06 | 383.55 | 1 | 310 | Load | 18751 | Load | Tran1phOH | AUSTIN R BERG | 405-590-8734 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002736 | PD-01092020-00088 | NORTHEAST | SAPULPA | 3208:TIBBENS ROAD | TIBBENS_RD_824 | 320824 | 2020-01-09 08:17 | 2020-01-09 09:46 | 89.12 | 1 | 2 | 76.4 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | SAPULPA | 8700 BK S 33RD W AV | CMI_NORMAL | NO | NO | NO | 860195 | 73926 | 40710 | 3139 | 1401 | 8.8817e-05 | 1.1625e-06 | 76.4 | 1 | 310 | Customer | 47438 | Load | Tran1phOH | CGI ADMIN | 918-261-6802 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2020
J2001.002731 | PD-01092020-00055 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-01-09 08:25 | 2020-01-09 09:59 | 93.57 | 1 | 1 | 93.5667 | 22 | WIND | 17 | JUMPER | OKLAHOMA CITY | 4119 S.PENN | CMI_NORMAL | NO | NO | NO | 860195 | 158979 | 102070 | 7597 | 2455 | 0.00010877 | 1.1625e-06 | 93.5667 | 1 | 320 | Customer | 14894 | Load | TranOpenDelta | JACOB SHANDY | 918-623-6369 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-09 | 2020 |  | #N/A
J2001.002738 | PD-01092020-00070 | SOUTHERN | DURANT | 5505:DURANT | DURANT 22 | 550522 | 2020-01-09 08:34 | 2020-01-09 08:53 | 18.93 | 1 | 1 | 37.9667 | 13 | PREMATURE FAILURE | 2 | TRANSFORMER OH | DURANT | US HWY 70 | CMI_NORMAL | NO | NO | NO | 860195 | 77538 | 15474 | 1319 | 798 | 4.4137e-05 | 1.1625e-06 | 37.9667 | 1 | 310 | Load | 10195 | Load | Tran1phOH | MICHAEL N STROHL | 903-821-1619 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002739 | PD-01092020-00087 | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1021 | 311021 | 2020-01-09 08:38 | 2020-01-09 12:00 | 201.98 | 1 | 1 | 201.9833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | MUSKOGEE | 3300 GIBSON - OK SCH BLIND | CMI_NORMAL | NO | NO | NO | 860195 | 73926 | 33216 | 2900 | 299 | 0.00023481 | 1.1625e-06 | 201.9833 | 1 | 310 | Load | 90050 | Load | 0 | STEVE K HIGHFILL | 918-869-2785 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-09 | 2020 |  | #N/A
J2001.002748 | PD-01092020-00213 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1122 | 511122 | 2020-01-09 08:47 | 2020-01-09 11:15 | 148.4 | 1 | 1 | 148.4 | 28 | OTHER (DESCRIBE) | 54 | LIGHTING - SECURITY | DICKSON | 3507 OLD HWY 70 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860195 | 77538 | 23566 | 2206 | 1205 | 0.00017252 | 1.1625e-06 | 148.4 | 1 | 310 | Load | 402541 | Load | Tran1phOH | GARRID H BROWN | 405-207-3948 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002749 |  | ARKANSAS | OZARK | 9412:ALTUS | ALTUS_1229 | 941229 | 2020-01-09 08:48 | 2020-01-09 10:51 | 122.73 | 1 | 1 | 113.1 | 4 | DETERIORATION | 2 | TRANSFORMER OH | ALTUS | HWY 64 EAST OF 02 | CMI_PLANNED | YES | NO | NO | 860195 | 82136 | 7530 | 864 | 864 | 0.00013148 | 1.1625e-06 | 113.1 | 1 | 308 | Load | 14970 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.002751 |  | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2724 | 872724 | 2020-01-09 08:53 | 2020-01-09 09:17 | 24.12 | 1 | 0 | 24.0998 | 4 | DETERIORATION | 2 | TRANSFORMER OH | NORMAN | 330 N.PORTER AV | CMI_PLANNED | YES | NO | NO | 860195 | 158979 | 56909 | 6456 | 1255 | 2.8017e-05 | 1.1625e-06 | 24.0998 | 1 | 0 | Load | 31918 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002753 |  | METRO NORTH | GUTHRIE | 8819:LIBERTY LAKE | LIBERTY_LAKE_1921 | 881921 | 2020-01-09 08:55 | 2020-01-09 12:07 | 191.63 | 27 | 20 | 5173.8449 | 4 | DETERIORATION | 12 | POLE | GUTHRIE | S Coltrane Rd and W Simpson Rd | CMI_PLANNED | YES | NO | NO | 860195 | 168012 | 19797 | 3348 | 1524 | 0.0060147 | 3.1388e-05 | 191.6239 | 1 | 310 | Mainline | 354202 | Switch | SwitchOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002754 | PD-01092020-00118 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3925 | 833925 | 2020-01-09 08:56 | 2020-01-09 11:34 | 158.03 | 1 | 2 | 140.05 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | BETHANY | 4220 N.CLASSEN BL | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860195 | 168012 | 148215 | 7846 | 2182 | 0.00016281 | 1.1625e-06 | 140.05 | 1 | 310 | Customer | 372013 | Load | Tran1phOH | VEGETATION MGMT CONTRACTOR | 405-317-6576 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2022
J2001.002755 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5923 | 835923 | 2020-01-09 09:00 | 2020-01-09 10:00 | 60.37 | 8 | 7 | 405.0667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | YUKON | 825 YUKON AV | CMI_PLANNED | YES | NO | NO | 860195 | 128586 | 115862 | 6411 | 1150 | 0.0004709 | 9.3002e-06 | 50.6333 | 1 | 310 | Load | 19445 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-09 | 2020 |  | #N/A
J2001.002771 |  | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3422 | 843422 | 2020-01-09 09:06 | 2020-01-09 09:37 | 30.87 | 2 | 1 | 55.3167 | 5 | ELECTRICAL TRACKING | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 2801 NE.50 | CMI_PLANNED | YES | NO | NO | 860195 | 168012 | 148215 | 1224 | 726 | 6.4307e-05 | 2.3251e-06 | 27.6583 | 1 | 308 | Mainline | 31747 | Fuse | FuseRiser | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-09 | 2020 |  | #N/A
J2001.002764 | PD-01092020-00133 | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1621 | 581621 | 2020-01-09 09:10 | 2020-01-09 10:28 | 77.73 | 1 | 1 | 77.7333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ADA | 425 W.6 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 77538 | 11505 | 3457 | 1807 | 9.0367e-05 | 1.1625e-06 | 77.7333 | 1 | 310 | Customer | 525 | Load | Tran1phOH | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002769 | PD-01092020-00153 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3621 | 853621 | 2020-01-09 09:15 | 2020-01-09 10:12 | 57.45 | 1 | 1 | 57.45 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1739 NE.19 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 168012 | 148215 | 5917 | 2164 | 6.6787e-05 | 1.1625e-06 | 57.45 | 1 | 310 | Customer | 7558 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2022
J2001.002770 | PD-01092020-00135 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7031 | 817031 | 2020-01-09 09:16 | 2020-01-09 09:59 | 43.13 | 1 | 1 | 19.1237 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 424 SW.92 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 158979 | 102070 | 9938 | 1891 | 2.2232e-05 | 1.1625e-06 | 19.1237 | 1 | 310 | Customer | 62801 | Load | Tran1phPad | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002772 |  | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2731 | 872731 | 2020-01-09 09:21 | 2020-01-09 09:46 | 25.28 | 1 | 1 | 25.2833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 442 HIGHLAND PKWY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 158979 | 56909 | 6456 | 1349 | 2.9393e-05 | 1.1625e-06 | 25.2833 | 1 | 310 | Customer | 71850 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002774 |  | NORTHEAST | SAPULPA | 3213:BOWDEN | BOWDEN_1323 | 321323 | 2020-01-09 09:27 | 2020-01-09 12:17 | 169.68 | 3 | 2 | 495.975 | 4 | DETERIORATION | 2 | TRANSFORMER OH | SAPULPA | 801 N MISSION | CMI_PLANNED | YES | NO | NO | 860195 | 73926 | 40710 | 3367 | 908 | 0.00057658 | 3.4876e-06 | 165.325 | 1 | 308 | Load | 44052 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2020
J2001.002775 |  | NORTHEAST | SAPULPA | 3213:BOWDEN | BOWDEN_1323 | 321323 | 2020-01-09 09:27 | 2020-01-09 12:17 | 169.95 | 6 | 4 | 991 | 4 | DETERIORATION | 2 | TRANSFORMER OH | SAPULPA | 1137 E.WATCHORN | CMI_PLANNED | YES | NO | NO | 860195 | 73926 | 40710 | 3367 | 908 | 0.0011521 | 6.9752e-06 | 165.1667 | 1 | 308 | Load | 42448 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2020
J2001.002777 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-09 09:29 | 2020-01-09 11:00 | 91.38 | 1 | 1 | 49.4333 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | FORT SMITH | 1/4 MI. NO. ZERO - MASSARD RD | CMI_PLANNED | YES | NO | NO | 860195 | 82136 | 61142 | 2732 | 2120 | 5.7468e-05 | 1.1625e-06 | 49.4333 | 1 | 308 | Load | 19013 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.002786 | PD-01092020-00177 | METRO WEST | WEST | 8158:SARA | SARA_5864 | 815864 | 2020-01-09 09:53 | 2020-01-09 12:07 | 133.97 | 1 | 1 | 133.9667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | West Creek Estates | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 128586 | 115862 | 18216 | 4810 | 0.00015574 | 1.1625e-06 | 133.9667 | 1 | 310 | Customer | 210253 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2022
J2001.002787 |  | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2124 | 332124 | 2020-01-09 10:00 | 2020-01-09 12:39 | 159.38 | 14 | 4 | 2126.1333 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | FORT GIBSON | 204 MEIGS | CMI_PLANNED | YES | NO | NO | 860195 | 73926 | 33216 | 3330 | 1219 | 0.0024717 | 1.6275e-05 | 151.8667 | 1 | 308 | Load | 12482 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | #N/A
J2001.002790 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-09 10:03 | 2020-01-09 11:01 | 57.48 | 4 | 1 | 158.2 | 4 | DETERIORATION | 23 | FUSE - PRIMARY | ALMA | US 71 800 S DN SPGS RD | CMI_PLANNED | YES | NO | NO | 860195 | 82136 | 61142 | 3787 | 1204 | 0.00018391 | 4.6501e-06 | 39.55 | 1 | 308 | Tap | 6195 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.002794 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5132 | 815132 | 2020-01-09 10:21 | 2020-01-09 10:40 | 19.12 | 1 | 1 | 19.1167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2645 SW.74 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 158979 | 102070 | 13934 | 2003 | 2.2224e-05 | 1.1625e-06 | 19.1167 | 1 | 310 | Customer | 46791 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002798 | PD-01092020-00225 | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-01-09 10:25 | 2020-01-09 11:54 | 89.15 | 1 | 1 | 89.15 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 14700 OAKS CROSSING | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 158979 | 56909 | 4204 | 3066 | 0.00010364 | 1.1625e-06 | 89.15 | 1 | 310 | Customer | 89218 | Load | Tran1phOH | BRADLEY SUDBECK | 405-999-6850 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002797 | PD-01092020-00221 | METRO EAST | EAST | 8416:DUNJEE | DUNJEE_1623 | 841623 | 2020-01-09 10:25 | 2020-01-09 12:04 | 99.02 | 1 | 1 | 99.0167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SPENCER | L10 B2 COBBLESTONE HOLLOW ADDN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 114299 | 71177 | 3539 | 1987 | 0.00011511 | 1.1625e-06 | 99.0167 | 1 | 310 | Customer | 72836 | Load | Tran1phPad | STEVEN CASKEY | 405-777-8855 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002803 |  | METRO WEST | WEST | 8158:SARA | SARA_5864 | 815864 | 2020-01-09 10:34 | 2020-01-09 12:15 | 100.37 | 17 | 7 | 1148.6333 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | MUSTANG | 322 W.MAPLEBRNCH WY | CMI_PLANNED | YES | NO | NO | 860195 | 128586 | 115862 | 18216 | 4810 | 0.0013353 | 1.9763e-05 | 67.5667 | 1 | 310 | Load | 65363 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2022
J2001.002807 | PD-01092020-00235 | SOUTHERN | DURANT | 5504:BUTTERFIELD | BUTTERFIELD_429 | 550429 | 2020-01-09 10:43 | 2020-01-09 12:46 | 122.62 | 1 | 2 | 122.6167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DURANT | 126 N 8TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 77538 | 15474 | 3482 | 1272 | 0.00014255 | 1.1625e-06 | 122.6167 | 1 | 310 | Customer | 413009 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002812 | PD-01092020-00231 | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2824 | 312824 | 2020-01-09 10:49 | 2020-01-09 12:12 | 83.4 | 1 | 1 | 81.3167 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | MUSKOGEE | 853 GIBSON | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860195 | 73926 | 33216 | 5271 | 1609 | 9.4533e-05 | 1.1625e-06 | 81.3167 | 1 | 320 | Load | 252 | Load | Tran1phOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | OK - 2020
J2001.002813 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-01-09 10:50 | 2020-01-09 12:50 | 120.2 | 2 | 1 | 45 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 12900 COUNTRY LANE | CMI_PLANNED | YES | NO | NO | 860195 | 158979 | 56909 | 4204 | 3066 | 5.2314e-05 | 2.3251e-06 | 22.5 | 1 | 308 | Load | 205521 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002816 | PD-01092020-00261 | METRO EAST | SHAWNEE | 7432:ST GREGORY | ST_GREGORY_3224 | 743224 | 2020-01-09 10:53 | 2020-01-09 12:41 | 108.38 | 1 | 1 | 108.3833 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | SHAWNEE | 1900 W.MACARTHUR | CMI_NORMAL | NO | NO | NO | 860195 | 114299 | 22083 | 4089 | 1370 | 0.000126 | 1.1625e-06 | 108.3833 | 1 | 310 | Load | 90217 | Load | 0 | [7 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002819 |  | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-01-09 10:56 | 2020-01-09 15:34 | 277.67 | 2 | 0 | 553.2667 | 4 | DETERIORATION | 12 | POLE | 0 | N HWY 81 | CMI_PLANNED | YES | NO | NO | 860195 | 128586 | 12724 | 6933 | 1822 | 0.00064319 | 2.3251e-06 | 276.6333 | 1 | 0 | Load | 42335 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002822 | PD-01092020-00253 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4821 | 824821 | 2020-01-09 11:02 | 2020-01-09 11:56 | 53.78 | 1 | 1 | 53.7833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2109 W. SHERIDAN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 168012 | 148215 | 4189 | 242 | 6.2525e-05 | 1.1625e-06 | 53.7833 | 1 | 310 | Customer | 1037 | Load | TranOpenDelta | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2022
J2001.002838 |  | SOUTHERN | PAULS VALLEY | 5619:RUSH CREEK | RUSH_CREEK_1921 | 561921 | 2020-01-09 11:21 | 2020-01-09 11:26 | 4.95 | 1 | 1 | 4.95 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | PAULS VALLEY | 210 S.PAUL | CMI_MOMENTARY | YES | NO | NO | 860195 | 77538 | 6199 | 2071 | 823 | 5.7545e-06 | 1.1625e-06 | 4.95 | 1 | 310 | Customer | 18573 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-09 | 2020 |  | #N/A
J2001.002840 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5922 | 835922 | 2020-01-09 11:22 | 2020-01-09 12:27 | 64.48 | 3 | 3 | 94.85 | 4 | DETERIORATION | 1 | TRANSFORMER UG | YUKON | 400 S.RANCHWOOD BL | CMI_PLANNED | YES | NO | NO | 860195 | 128586 | 115862 | 6411 | 1634 | 0.00011027 | 3.4876e-06 | 31.6167 | 1 | 310 | Secondary | 38786 | Load | Tran1phPad | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-09 | 2020 |  | #N/A
J2001.002841 | PD-01092020-00277 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2122 | 822122 | 2020-01-09 11:23 | 2020-01-09 12:25 | 62.25 | 1 | 1 | 53.407 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3825 NW 19 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 168012 | 148215 | 9236 | 2013 | 6.2087e-05 | 1.1625e-06 | 53.407 | 1 | 320 | Customer | 2756 | Load | Tran3phPadWye | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2020
J2001.002843 | PD-01092020-00284 | NORTHEAST | SAPULPA | 7632:OAK GROVE | OAK_GROVE_3221 | 763221 | 2020-01-09 11:25 | 2020-01-09 12:19 | 54.38 | 7 | 4 | 374.9667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | DRUMRIGHT | 302 N.SKINNER | CMI_NORMAL | NO | NO | NO | 860195 | 73926 | 40710 | 1020 | 1020 | 0.00043591 | 8.1377e-06 | 53.5667 | 1 | 310 | Load | 41559 | Load | Tran1phOH | BRAD WRIGHT | 918-629-1747 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-09 | 2020 |  | OK - 2021
J2001.002848 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-09 11:33 | 2020-01-09 12:55 | 82.02 | 2 | 0 | 162.6167 | 4 | DETERIORATION | 12 | POLE | COAL HILL | 309 ARBAUGH AV | CMI_PLANNED | YES | NO | NO | 860195 | 82136 | 7530 | 1502 | 1199 | 0.00018905 | 2.3251e-06 | 81.3083 | 1 | 0 | Load | 7391 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.002856 | PD-01092020-00308 | METRO WEST | WEST | 8359:YUKON | YUKON_5922 | 835922 | 2020-01-09 12:13 | 2020-01-09 13:33 | 79.98 | 1 | 1 | 79.9833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | YUKON | 106 CORNWELL DR 7 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 128586 | 115862 | 6411 | 1634 | 9.2983e-05 | 1.1625e-06 | 79.9833 | 1 | 310 | Customer | 24536 | Load | Tran1phOH | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-09 | 2020 |  | #N/A
J2001.002863 |  | NORTHWEST | ENID | 4414:HENNESSEY | HENNESSEY_1423 | 441423 | 2020-01-09 12:36 | 2020-01-09 12:56 | 20.6 | 12 | 1 | 221.2 | 4 | DETERIORATION | 17 | JUMPER | HENNESSEY | 3ME,1MN-COLONY HOUSE | CMI_PLANNED | YES | NO | NO | 860195 | 53495 | 37564 | 1952 | 286 | 0.00025715 | 1.395e-05 | 18.4333 | 1 | 310 | Mainline | 1819 | Fuse | FuseOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002867 |  | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2163 | 892163 | 2020-01-09 12:45 | 2020-01-09 12:46 | 0.07 | 1133 | 0 | 75.5333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | EL RENO | 803 JENSEN RD | CMI_MOMENTARY | YES | NO | NO | 860195 | 128586 | 12724 | 3173 | 1132 | 8.781e-05 | 0.0013171 | 0.066667 | 1 | 0 | Feeder | JENSN RD_2163 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-09 | 2020 |  | OK - 2021
J2001.002871 | PD-01092020-00390 | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2163 | 892163 | 2020-01-09 12:49 | 2020-01-09 18:02 | 313.08 | 116 | 26 | 23430.0667 | 5 | ELECTRICAL TRACKING | 23 | FUSE - PRIMARY | UNION CITY | 0 | CMI_NORMAL | NO | NO | NO | 860195 | 128586 | 12724 | 3173 | 1132 | 0.027238 | 0.00013485 | 201.9833 | 1 | 310 | Mainline |  | 0 | 0 | JESSE PHILLER | 405-512-8086 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2021
J2001.002880 | PD-01092020-00391 | NORTHWEST | ALVA | 4707:KNOBHILL | KNOBHILL_729 | 470729 | 2020-01-09 13:02 | 2020-01-09 14:36 | 93.72 | 1 | 1 | 93.7167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | HOPETON | WESLEYAN CHURCH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 53495 | 5516 | 1740 | 427 | 0.00010895 | 1.1625e-06 | 93.7167 | 1 | 320 | Customer | 9344 | Load | TranOpenDelta | DENNIS PEARSON | 580-541-4106 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-09 | 2020 |  | #N/A
J2001.002881 |  | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2163 | 892163 | 2020-01-09 13:03 | 2020-01-09 16:47 | 223.98 | 1 | 1 | 174.4333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | UNION CITY | UNION CITY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 128586 | 12724 | 3173 | 1132 | 0.00020278 | 1.1625e-06 | 174.4333 | 1 | 310 | Customer | 47305 | Load | Tran1phOH | JOSH BLACK | 405-403-9382 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2021
J2001.002883 | PD-01092020-00413 | METRO NORTH | GUTHRIE | 8819:LIBERTY LAKE | LIBERTY_LAKE_1921 | 881921 | 2020-01-09 13:08 | 2020-01-09 14:18 | 70.02 | 1 | 1 | 65.3 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | GUTHRIE | L5+6 BF GREEN ACRES | CMI_NORMAL | NO | NO | NO | 860195 | 168012 | 19797 | 3348 | 1524 | 7.5913e-05 | 1.1625e-06 | 65.3 | 1 | 310 | Customer | 43186 | Load | Tran1phOH | JOSEPH WAYNE POOL | 405-919-2253 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002885 | PD-01092020-00400 | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8124 | 838124 | 2020-01-09 13:12 | 2020-01-09 14:11 | 59.13 | 1 | 2 | 59.1333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 8204 NW.101 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 128586 | 115862 | 8951 | 1638 | 6.8744e-05 | 1.1625e-06 | 59.1333 | 1 | 310 | Customer | 47387 | Load | Tran1phPad | BRANDON H SMITH | 405-371-4294 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002886 | PD-01092020-00404 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3627 | 833627 | 2020-01-09 13:15 | 2020-01-09 13:58 | 43.25 | 1 | 1 | 43.25 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 11225 N.PENN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 168012 | 148215 | 8782 | 1494 | 5.0279e-05 | 1.1625e-06 | 43.25 | 1 | 310 | Customer | 35375 | Load | Tran1phPad | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002889 |  | ARKANSAS | FORT SMITH | 9104:J STREET | J_STREET_424 | 910424 | 2020-01-09 13:27 | 2020-01-09 13:27 | 0.03 | 226 | 0 | 7.5333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | FT SMITH | 909 N 3RD ST | CMI_MOMENTARY | YES | NO | NO | 860195 | 82136 | 61142 | 2003 | 226 | 8.7577e-06 | 0.00026273 | 0.033333 | 1 | 0 | Feeder | J STREET_424 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-09 | 2020 |  | #N/A
J2001.002891 | PD-01092020-00418 | ARKANSAS | POTEAU | 3509:PANAMA | PANAMA 42 | 350942 | 2020-01-09 13:32 | 2020-01-09 14:38 | 66.03 | 1 | 1 | 64.5833 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 21 | FUSE - TRANSFORMER | PANAMA | 1/2 mile south of Hudson Corner and 1/2 mile east. | CMI_NORMAL | NO | NO | NO | 860195 | 82136 | 13464 | 1386 | 336 | 7.508e-05 | 1.1625e-06 | 64.5833 | 1 | 310 | Load | 222169 | Load | Tran1phOH | JOHN MEEH | 918-413-0959 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-09 | 2020 |  | #N/A
J2001.002893 | PD-01092020-00414 | METRO WEST | WEST | 8335:BETHANY | BETHANY_3526 | 833526 | 2020-01-09 13:36 | 2020-01-09 14:43 | 67.22 | 1 | 1 | 67.2167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | WARR ACRES | 5931 NW.35 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 128586 | 115862 | 7860 | 2060 | 7.8141e-05 | 1.1625e-06 | 67.2167 | 1 | 310 | Customer | 42818 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-09 | 2020 |  | #N/A
J2001.002895 | PD-01092020-00419 | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1722 | 861722 | 2020-01-09 13:39 | 2020-01-09 14:26 | 46.52 | 1 | 1 | 46.5167 | 12 | POOR CONNECTION | 50 | CONNECTOR | DEL CITY | 4427 SE.40 | CMI_NORMAL | NO | NO | NO | 860195 | 114299 | 71177 | 6938 | 1787 | 5.4077e-05 | 1.1625e-06 | 46.5167 | 1 | 320 | Customer | 17066 | Load | Tran1phOH | BRADLEY SUDBECK | 405-999-6850 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-09 | 2020 |  | #N/A
J2001.002897 | PD-01092020-00425 | ARKANSAS | FORT SMITH | 9104:J STREET | J_STREET_422 | 910422 | 2020-01-09 13:43 | 2020-01-09 14:54 | 70.75 | 1 | 1 | 70.75 | 5 | ELECTRICAL TRACKING | 47 | ARRESTOR OH | FORT SMITH | 1003 N. 3RD | CMI_NORMAL | NO | NO | NO | 860195 | 82136 | 61142 | 2003 | 529 | 8.2249e-05 | 1.1625e-06 | 70.75 | 1 | 310 | Load | 327047 | Load | Tran3phPadWye | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.002898 |  | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-01-09 13:55 | 2020-01-09 14:04 | 8.92 | 1 | 1 | 7.6649 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4314 S.BARNES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 158979 | 102070 | 7597 | 2455 | 8.9107e-06 | 1.1625e-06 | 7.6649 | 1 | 310 | Customer | 44752 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-09 | 2020 |  | #N/A
J2001.002899 | PD-01092020-00453 | SOUTHERN | DURANT | 5504:BUTTERFIELD | BUTTERFIELD_429 | 550429 | 2020-01-09 13:56 | 2020-01-09 14:44 | 48.22 | 1 | 1 | 48.2167 | 28 | OTHER (DESCRIBE) | 15 | METER - SECONDARY | DURANT | 126 N 8TH | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860195 | 77538 | 15474 | 3482 | 1272 | 5.6053e-05 | 1.1625e-06 | 48.2167 | 1 | 310 | Customer | 413009 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002907 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2173 | 862173 | 2020-01-09 14:07 | 2020-01-09 14:07 | 0.22 | 158 | 0 | 34.2333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 11406 SE 134TH ST | CMI_MOMENTARY | YES | NO | NO | 860195 | 158979 | 56909 | 4204 | 164 | 3.9797e-05 | 0.00018368 | 0.21667 | 1 | 0 | Feeder | DRAPER_2173 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002908 | PD-01092020-00457 | NORTHEAST | SAPULPA | 3213:BOWDEN | BOWDEN_1329 | 321329 | 2020-01-09 14:12 | 2020-01-09 16:01 | 109.38 | 1 | 1 | 109.3833 | 4 | DETERIORATION | 50 | CONNECTOR | SAPULPA | 3/4W OF97ONPW L RD | CMI_NORMAL | NO | NO | NO | 860195 | 73926 | 40710 | 3367 | 1516 | 0.00012716 | 1.1625e-06 | 109.3833 | 1 | 320 | Load | 48396 | Load | Tran1phOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2020
J2001.002917 | PD-01092020-00469 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6922 | 846922 | 2020-01-09 14:27 | 2020-01-09 14:50 | 23.03 | 1 | 1 | 23.0333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1025 NW.97 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 168012 | 148215 | 7716 | 1485 | 2.6777e-05 | 1.1625e-06 | 23.0333 | 1 | 310 | Customer | 24244 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002918 |  | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-09 14:30 | 2020-01-09 14:42 | 11.47 | 11 | 0 | 95.8833 | 1 | CANCELLED | 37 | CONDUCTOR PRIMARY - OH | MUSTANG | 2341 E HWY 152 | CMI_PLANNED | YES | NO | NO | 860195 | 128586 | 115862 | 18216 | 4430 | 0.00011147 | 1.2788e-05 | 8.7167 | 1 | 0 | Mainline | 14056 | Fuse | FuseOH | Crew | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2022
J2001.002921 | PD-01092020-00473 | ARKANSAS | OZARK | 9224:BRANCH | BRANCH_2462 | 922462 | 2020-01-09 14:33 | 2020-01-09 15:39 | 66.1 | 1 | 1 | 65.7833 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | CHARLESTON | 3/4M N-CHARLESTON ON GRNWD ST. | CMI_NORMAL | NO | NO | NO | 860195 | 82136 | 7530 | 1791 | 971 | 7.6475e-05 | 1.1625e-06 | 65.7833 | 1 | 310 | Load | 3506 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 3
J2001.002922 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2263 | 852263 | 2020-01-09 14:34 | 2020-01-09 14:37 | 3 | 1 | 1 | 3 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3824 DUNGEE BL | CMI_MOMENTARY | YES | NO | NO | 860195 | 114299 | 71177 | 11617 | 1526 | 3.4876e-06 | 1.1625e-06 | 3 | 1 | 310 | Customer | 32749 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2021
J2001.002927 |  | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 21 | 570821 | 2020-01-09 14:46 | 2020-01-09 15:05 | 19.88 | 1 | 1 | 19.8833 | 1 | CANCELLED | 57 | CANCELLED | DAVIS | 1003 E.ELLIS ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 77538 | 6809 | 1858 | 903 | 2.3115e-05 | 1.1625e-06 | 19.8833 | 1 | 308 | Customer | 15364 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-09 | 2020 |  | OK - 2021
J2001.002932 |  | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-09 15:05 | 2020-01-09 17:54 | 169.42 | 10 | 8 | 1487.3333 | 1 | CANCELLED | 57 | CANCELLED | MUSTANG | ES MUSTANG RD-NS SW 89 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 128586 | 115862 | 18216 | 4430 | 0.0017291 | 1.1625e-05 | 148.7333 | 1 | 310 | Mainline | 6391 | Fuse | FuseOH | Crew | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2022
J2001.002935 | PD-01092020-00534 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-09 15:19 | 2020-01-09 19:01 | 221.53 | 1 | 1 | 219.15 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MOUNTAINBURG | PIGEON CREEK RD,S-MOUNTAINBURG | CMI_NORMAL | NO | NO | NO | 860195 | 82136 | 61142 | 3787 | 1204 | 0.00025477 | 1.1625e-06 | 219.15 | 1 | 310 | Load | 5467 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.002937 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-09 15:22 | 2020-01-09 16:36 | 73.87 | 1 | 1 | 73.8667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MULBERRY | KEYSTONE ADD. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 82136 | 61142 | 3787 | 1204 | 8.5872e-05 | 1.1625e-06 | 73.8667 | 1 | 310 | Customer | 203095 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.002938 | PD-01092020-00553 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-09 15:27 | 2020-01-09 17:45 | 137.73 | 1 | 2 | 136.0833 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | ALMA | ES HWY 71 1/2MN HIDDEN OAKS RD | CMI_NORMAL | NO | NO | NO | 860195 | 82136 | 61142 | 3787 | 1204 | 0.0001582 | 1.1625e-06 | 136.0833 | 1 | 310 | Load | 214607 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.002942 | PD-01092020-00557 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-09 15:34 | 2020-01-09 18:13 | 159.4 | 1 | 1 | 158 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | ALMA | 505 cozy cove | CMI_NORMAL | NO | NO | NO | 860195 | 82136 | 61142 | 3787 | 1204 | 0.00018368 | 1.1625e-06 | 158 | 1 | 310 | Load | 363443 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.002948 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4031 | 834031 | 2020-01-09 15:54 | 2020-01-09 16:11 | 16.88 | 1 | 1 | 16.8833 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 10224 EASTLAKE DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 128586 | 115862 | 10840 | 1640 | 1.9627e-05 | 1.1625e-06 | 16.8833 | 1 | 310 | Customer | 42774 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002949 | PD-01092020-00563 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-09 15:54 | 2020-01-09 19:41 | 227.27 | 1 | 1 | 227.2667 | 25 | LIGHTNING | 2 | TRANSFORMER OH | MOUNTAINBURG | ES HWY 71 4/10THMS HWY 348 | CMI_NORMAL | NO | NO | NO | 860195 | 82136 | 61142 | 3787 | 1204 | 0.0002642 | 1.1625e-06 | 227.2667 | 1 | 310 | Customer | 186510 | Load | Tran1phOH | LANCE M BECKER | 479-883-5087 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.002951 |  | METRO NORTH | NORTH | 8430:REMINGTON PARK | REMINGTON_PARK_3024 | 843024 | 2020-01-09 15:58 | 2020-01-09 17:04 | 66.48 | 2 | 1 | 123.5 | 28 | OTHER (DESCRIBE) | 14 | PEDESTAL/J-BOX | OKLAHOMA CITY | ES LAKE PK REST RMS | CMI_PLANNED | YES | NO | NO | 860195 | 168012 | 148215 | 848 | 179 | 0.00014357 | 2.3251e-06 | 61.75 | 1 | 308 | Load | 29472 | Load | Tran1phOH | Contractor | [6 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002952 | PD-01092020-00530 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3022 | 743022 | 2020-01-09 15:58 | 2020-01-09 17:06 | 68.07 | 1 | 1 | 64.85 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | SHAWNEE | 309 N.POTTENGER | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860195 | 114299 | 22083 | 6637 | 2163 | 7.539e-05 | 1.1625e-06 | 64.85 | 1 | 310 | Customer | 4132 | Load | TranOpenDelta | KYLE L GOODIN | 405-426-9802 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2020
J2001.002955 |  | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2129 | 332129 | 2020-01-09 16:02 | 2020-01-09 16:10 | 7.82 | 1 | 1 | 7.8167 | 1 | CANCELLED | 57 | CANCELLED | FORT GIBSON | .5MS DONKEY LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 73926 | 33216 | 3330 | 939 | 9.0871e-06 | 1.1625e-06 | 7.8167 | 1 | 310 | Customer | 11406 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | #N/A
J2001.002956 | PD-01092020-00564 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-09 16:07 | 2020-01-09 18:31 | 144.22 | 2 | 2 | 282.7667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MOUNTAINBURG | RURAL | CMI_NORMAL | NO | NO | NO | 860195 | 82136 | 61142 | 3787 | 1204 | 0.00032872 | 2.3251e-06 | 141.3833 | 1 | 310 | Load | 14053 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.002957 | PD-01092020-00551 | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 21 | 570821 | 2020-01-09 16:12 | 2020-01-09 18:13 | 120.58 | 1 | 1 | 99.6667 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | DAVIS | 1003 E.ELLIS ST | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860195 | 77538 | 6809 | 1858 | 903 | 0.00011587 | 1.1625e-06 | 99.6667 | 1 | 310 | Customer | 15364 | Load | Tran1phPad | JOE LOFTIS | 918-884-5349 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-09 | 2020 |  | OK - 2021
J2001.002960 | PD-01092020-00556 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2024 | 862024 | 2020-01-09 16:22 | 2020-01-09 18:40 | 138.12 | 1 | 1 | 138.1167 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | OKLAHOMA CITY | 312 SW 25TH ST | CMI_NORMAL | NO | NO | NO | 860195 | 158979 | 102070 | 4738 | 769 | 0.00016056 | 1.1625e-06 | 138.1167 | 1 | 320 | Customer | 1130 | Load | Tran3phWye | THOMAS E COLE | 405-623-9338 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002962 | PD-01092020-00562 | METRO EAST | SHAWNEE | 7411:DALE | DALE_1129 | 741129 | 2020-01-09 16:23 | 2020-01-09 18:11 | 107.93 | 1 | 1 | 107.2833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | SHAWNEE | .5W 102-CLPD RD SECR | CMI_NORMAL | NO | NO | NO | 860195 | 114299 | 22083 | 968 | 967 | 0.00012472 | 1.1625e-06 | 107.2833 | 1 | 310 | Load | 16741 | Load | Tran1phOH | KYLE L GOODIN | 405-426-9802 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2021
J2001.003281 | PD-01102020-00303 | ARKANSAS | FORT SMITH | 9512:ADABELL ROAD | ADABELL_ROAD_1222 | 951222 | 2020-01-09 16:28 | 2020-01-10 12:51 | 1223.43 | 1 | 1 | 1208.8381 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | VAN BUREN | 1514 NORTH-HILLS BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 82136 | 61142 | 3120 | 1087 | 0.0014053 | 1.1625e-06 | 1208.8381 | 1 | 310 | Customer | 13930 | Load | Tran1phPad | LANCE M BECKER | 479-883-5087 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 1, Ark - Series 2
J2001.002971 | PD-01092020-00577 | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2822 | 312822 | 2020-01-09 16:33 | 2020-01-09 17:50 | 77.22 | 1 | 1 | 32.4833 | 4 | DETERIORATION | 50 | CONNECTOR | MUSKOGEE | 215 GRANDVIEW BL | CMI_NORMAL | NO | NO | NO | 860195 | 73926 | 33216 | 5271 | 1107 | 3.7763e-05 | 1.1625e-06 | 32.4833 | 1 | 310 | Customer | 6530 | Load | Tran1phOH | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | OK - 2020
J2001.002974 | PD-01092020-00592 | METRO NORTH | GUTHRIE | 8807:CRESCENT | CRESCENT_723 | 880723 | 2020-01-09 16:51 | 2020-01-09 18:47 | 116.42 | 2 | 2 | 220.1333 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 21 | FUSE - TRANSFORMER | CASHION | 504 W BROADWAY | CMI_NORMAL | NO | NO | NO | 860195 | 168012 | 19797 | 1763 | 890 | 0.00025591 | 2.3251e-06 | 110.0667 | 1 | 310 | Load | 242797 | Load | Tran1phOH | SCOTT C PERRY | 405-258-6044 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002983 |  | ARKANSAS | POTEAU | 3505:POTEAU | POTEAU_522 | 350522 | 2020-01-09 17:04 | 2020-01-09 19:48 | 163.78 | 1 | 2 | 38.1 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | POTEAU | 611 CRUCE | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860195 | 82136 | 13464 | 2296 | 358 | 4.4292e-05 | 1.1625e-06 | 38.1 | 1 | 310 | Customer | 9084 | Load | Tran1phOH | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-09 | 2020 |  | #N/A
J2001.002984 | PD-01092020-00601 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-09 17:08 | 2020-01-09 19:32 | 143.65 | 2 | 2 | 285.1167 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MOUNTAINBURG | ES HWY 71 4/10THMS HWY 348 | CMI_NORMAL | NO | NO | NO | 860195 | 82136 | 61142 | 3787 | 1204 | 0.00033146 | 2.3251e-06 | 142.5583 | 1 | 310 | Secondary | 186509 | Load | Tran1phOH | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.002987 | PD-01092020-00602 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-09 17:17 | 2020-01-09 19:45 | 147.8 | 1 | 1 | 104.1667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MOUNTAINBURG | HWY 71 NW OF HL17/6 500 | CMI_NORMAL | NO | NO | NO | 860195 | 82136 | 61142 | 3787 | 1204 | 0.0001211 | 1.1625e-06 | 104.1667 | 1 | 310 | Customer | 16542 | Load | Tran3phWye | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.002988 |  | METRO WEST | WEST | 8297:MORGAN ROAD | MORGAN_ROAD_9724 | 829724 | 2020-01-09 17:27 | 2020-01-09 17:40 | 13.27 | 1 | 1 | 13.2667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 300 S. MUSTANG | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 128586 | 115862 | 2496 | 1134 | 1.5423e-05 | 1.1625e-06 | 13.2667 | 1 | 310 | Customer | 170816 | Load | Tran3phPadWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002990 | PD-01092020-00605 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-09 17:30 | 2020-01-09 20:10 | 159.75 | 1 | 1 | 157.1667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MOUNTAINBURG | HWY 71,1/4M N-CAIN SCH RD,ALMA | CMI_NORMAL | NO | NO | NO | 860195 | 82136 | 61142 | 3787 | 1204 | 0.00018271 | 1.1625e-06 | 157.1667 | 1 | 310 | Customer | 3684 | Load | Tran1phOH | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.002992 | PD-01092020-00606 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6922 | 846922 | 2020-01-09 17:33 | 2020-01-09 19:14 | 100.58 | 1 | 1 | 87.3333 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 609 NW 109TH | CMI_NORMAL | NO | NO | NO | 860195 | 168012 | 148215 | 7716 | 1485 | 0.00010153 | 1.1625e-06 | 87.3333 | 1 | 320 | Customer | 21318 | Load | Tran1phOH | PETER BILICKI | 619-726-8332 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.002993 |  | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-09 17:36 | 2020-01-09 17:56 | 20.28 | 1 | 1 | 20.2833 | 1 | CANCELLED | 57 | CANCELLED | MUSTANG | 300 E PEBBLE CREEK TE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 128586 | 115862 | 18216 | 4430 | 2.358e-05 | 1.1625e-06 | 20.2833 | 1 | 310 | Customer | 255534 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2022
J2001.002994 |  | ARKANSAS | POTEAU | 3505:POTEAU | POTEAU_522 | 350522 | 2020-01-09 17:42 | 2020-01-09 17:42 | 0 | 357 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | POTEAU | 1100 SOUTH MCKENNA | CMI_MOMENTARY | YES | NO | NO | 860195 | 82136 | 13464 | 2296 | 358 | 0 | 0.00041502 | 0 | 1 | 0 | Feeder | POTEAU_522 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-09 | 2020 |  | #N/A
J2001.003000 | PD-01092020-00610 | SOUTHERN | DURANT | 5512:COLBERT | COLBERT_1222 | 551222 | 2020-01-09 18:23 | 2020-01-09 23:12 | 288.63 | 1 | 2 | 288.6333 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | COLBERT | 1ST + MAIN | CMI_NORMAL | NO | NO | NO | 860195 | 77550 | 15475 | 2165 | 1270 | 0.00033554 | 1.1625e-06 | 288.6333 | 1 | 320 | Customer | 6146 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.003009 | PD-01092020-00616 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-01-09 19:00 | 2020-01-09 19:52 | 51.87 | 1 | 1 | 51.8667 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 2606 N.SHARTEL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 168032 | 148231 | 11097 | 2335 | 6.0296e-05 | 1.1625e-06 | 51.8667 | 1 | 310 | Customer | 49976 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2020
J2001.003045 |  | ARKANSAS | FORT SMITH | 9512:ADABELL ROAD | ADABELL_ROAD_1221 | 951221 | 2020-01-09 19:01 | 2020-01-09 19:01 | 0 | 1 | 1 | 0 | 17 | TRANSMISSION OPERATION | 55 | SCADA - CIRCUIT TRIP | VAN BUREN | 1611 CEDAR, VAN BUREN | CMI_MOMENTARY | YES | NO | NO | 860195 | 82148 | 61149 | 3120 | 1094 | 0 | 1.1625e-06 | 0 | 1 | 308 | Load | 4636 | Load | Tran1phOH | [7 empty] | Equipment | N | TRANSMISSION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 1
J2001.003043 |  | ARKANSAS | OZARK | 9230:SHORT MTN | SHORT_MOUNTAIN_3061 | 923061 | 2020-01-09 19:01 | 2020-01-09 19:01 | 0 | 1 | 1 | 0 | 17 | TRANSMISSION OPERATION | 56 | SCADA - LOCKOUT | SUBIACO | RURAL | CMI_MOMENTARY | YES | NO | NO | 860195 | 82148 | 7532 | 367 | 367 | 0 | 1.1625e-06 | 0 | 1 | 308 | Load | 13213 | Load | Tran1phOH | [7 empty] | Equipment | N | TRANSMISSION | 69kV | 2020-01-09 | 2020 |  | #N/A
J2001.003042 |  | ARKANSAS | OZARK | 9412:ALTUS | ALTUS_1229 | 941229 | 2020-01-09 19:01 | 2020-01-09 19:01 | 0 | 3 | 3 | 0 | 17 | TRANSMISSION OPERATION | 56 | SCADA - LOCKOUT | OZARK | RURAL ALTUS | CMI_MOMENTARY | YES | NO | NO | 860195 | 82148 | 7532 | 864 | 864 | 0 | 3.4876e-06 | 0 | 1 | 308 | Load | 1664 | Load | Tran1phOH | [7 empty] | Equipment | N | TRANSMISSION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.003048 |  | ARKANSAS | OZARK | 9224:BRANCH | BRANCH_2463 | 922463 | 2020-01-09 19:01 | 2020-01-09 19:01 | 0 | 2 | 2 | 0 | 17 | TRANSMISSION OPERATION | 56 | SCADA - LOCKOUT | PARIS | 1748 CARON CITY RD. | CMI_MOMENTARY | YES | NO | NO | 860195 | 82148 | 7532 | 1791 | 820 | 0 | 2.3251e-06 | 0 | 1 | 308 | Load | 214419 | Load | Tran1phOH | [7 empty] | Equipment | N | TRANSMISSION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 3
J2001.003044 |  | ARKANSAS | OZARK | 9406:HELBERG | HELBERG_622 | 940622 | 2020-01-09 19:01 | 2020-01-09 19:01 | 0 | 1 | 1 | 0 | 17 | TRANSMISSION OPERATION | 45 | SUBSTATION CIRCUIT | OZARK | 107 SO 10TH ST + COMMERCIAL ST | CMI_MOMENTARY | YES | NO | NO | 860195 | 82148 | 7532 | 1719 | 886 | 0 | 1.1625e-06 | 0 | 1 | 308 | Load | 5143 | Load | Tran1phOH | [7 empty] | Equipment | N | TRANSMISSION | 69kV | 2020-01-09 | 2020 |  | Ark - Series 3
J2001.003011 | PD-01092020-00617 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3622 | 853622 | 2020-01-09 19:03 | 2020-01-09 22:56 | 232.77 | 1 | 1 | 214.3 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | 2412 SE 8TH ST | CMI_NORMAL | NO | NO | NO | 860195 | 168032 | 148231 | 5918 | 962 | 0.00024913 | 1.1625e-06 | 214.3 | 1 | 310 | Load | 61944 | Load | Tran3phWye | TOMMY D ROBERTSON | 405-696-6476 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.003013 |  | ARKANSAS | POTEAU | 3516:TARBY | TARBY_1625 | 351625 | 2020-01-09 19:05 | 2020-01-09 19:14 | 9.02 | 1 | 1 | 9.0167 | 1 | CANCELLED | 57 | CANCELLED | SHADY POINT | SHADY PT OK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 82148 | 13467 | 1674 | 1194 | 1.0482e-05 | 1.1625e-06 | 9.0167 | 1 | 310 | Customer | 10604 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | #N/A
J2001.003057 | PD-01092020-00622 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-09 19:34 | 2020-01-09 20:21 | 46.6 | 1 | 1 | 46.6 | 25 | LIGHTNING | 47 | ARRESTOR OH | MOUNTAINBURG | RURAL | CMI_NORMAL | NO | NO | NO | 860195 | 82148 | 61149 | 3787 | 1204 | 5.4174e-05 | 1.1625e-06 | 46.6 | 1 | 310 | Load | 17375 | Load | Tran1phOH | TRAVIS EARNHART | 479-462-5659 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.003062 | PD-01092020-00638 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_723 | 870723 | 2020-01-09 20:28 | 2020-01-09 21:33 | 65.48 | 1 | 1 | 65.4833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | NORMAN | 1808 E LINDSEY ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 158988 | 56911 | 11830 | 2043 | 7.6126e-05 | 1.1625e-06 | 65.4833 | 1 | 320 | Customer | 36030 | Load | Tran1phPad | THOMAS E COLE | 405-623-9338 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | #N/A
J2001.003066 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-09 20:48 | 2020-01-09 20:56 | 8.43 | 1 | 1 | 8.4333 | 25 | LIGHTNING | 2 | TRANSFORMER OH | MOUNTAINBURG | RURAL | CMI_NORMAL | NO | NO | NO | 860195 | 82148 | 61149 | 3787 | 1204 | 9.804e-06 | 1.1625e-06 | 8.4333 | 1 | 315 | Load | 17375 | Load | Tran1phOH | Ties | [6 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.003068 | PD-01092020-00652 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2123 | 822123 | 2020-01-09 21:13 | 2020-01-09 22:30 | 77.13 | 1 | 1 | 77.1333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3634 NW 15TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 168032 | 148231 | 9235 | 1488 | 8.967e-05 | 1.1625e-06 | 77.1333 | 1 | 310 | Customer | 49975 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2020
J2001.003069 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-09 21:22 | 2020-01-10 01:37 | 255.08 | 1 | 1 | 207.5333 | 25 | LIGHTNING | 2 | TRANSFORMER OH | MOUNTAINBURG | ES HWY 71 4/10THMS HWY 348 | CMI_NORMAL | NO | NO | NO | 860195 | 82148 | 61149 | 3787 | 1204 | 0.00024126 | 1.1625e-06 | 207.5333 | 1 | 310 | Customer | 186510 | Load | Tran1phOH | Ties | [6 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-09 | 2020 |  | Ark - Series 2
J2001.003074 | PD-01092020-00656 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4821 | 824821 | 2020-01-09 22:20 | 2020-01-09 23:00 | 40.47 | 1 | 1 | 40.4667 | 3 | DAMAGED BY PUBLIC | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 2109 W. SHERIDAN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 168032 | 148231 | 4189 | 242 | 4.7044e-05 | 1.1625e-06 | 40.4667 | 1 | 310 | Customer | 1037 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-09 | 2020 |  | OK - 2022
J2001.003085 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-10 00:19 | 2020-01-10 01:37 | 78.42 | 5 | 2 | 151.6667 | 25 | LIGHTNING | 2 | TRANSFORMER OH | MOUNTAINBURG | 11091 N HWY 71 | CMI_NORMAL | NO | NO | NO | 860195 | 82148 | 61149 | 3787 | 1204 | 0.00017632 | 5.8126e-06 | 30.3333 | 1 | 310 | Tap | 423957 | Fuse | FuseOH | OGE | [6 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003089 |  | ARKANSAS | OZARK | 9223:SUBIACO | SUBIACO_2321 | 922321 | 2020-01-10 01:37 | 2020-01-10 01:57 | 19.53 | 1 | 1 | 19.5333 | 1 | CANCELLED | 57 | CANCELLED | SUBIACO | RURAL PARIS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860195 | 82148 | 7532 | 156 | 155 | 2.2708e-05 | 1.1625e-06 | 19.5333 | 1 | 310 | Load | 1466 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 34.5/19.9kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003091 |  | METRO WEST | EL RENO | 8910:OKARCHE | OKARCHE_1021 | 891021 | 2020-01-10 02:06 | 2020-01-10 02:07 | 0.28 | 315 | 0 | 89.25 | 28 | OTHER (DESCRIBE) | 4 | SWITCH - OIL | 0 | Okarche Substation | CMI_MOMENTARY | YES | NO | NO | 860195 | 128607 | 12729 | 725 | 725 | 0.00010376 | 0.0003662 | 0.28333 | 1 | 0 | Mainline | 412820 | Recloser | Rec3phElectronic | [7 empty] | Other | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003092 |  | METRO WEST | EL RENO | 8910:OKARCHE | OKARCHE_1021 | 891021 | 2020-01-10 02:06 | 2020-01-10 02:07 | 0.28 | 210 | 0 | 59.5 | 28 | OTHER (DESCRIBE) | 4 | SWITCH - OIL | 0 | Okarche Substation | CMI_MOMENTARY | YES | NO | NO | 860195 | 128607 | 12729 | 725 | 725 | 6.917e-05 | 0.00024413 | 0.28333 | 1 | 0 | Mainline | 412820 | Recloser | Rec3phElectronic | [7 empty] | Other | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003093 |  | METRO WEST | EL RENO | 8910:OKARCHE | OKARCHE_1021 | 891021 | 2020-01-10 02:06 | 2020-01-10 02:07 | 0.28 | 182 | 0 | 51.5667 | 28 | OTHER (DESCRIBE) | 4 | SWITCH - OIL | 0 | Okarche Substation | CMI_MOMENTARY | YES | NO | NO | 860195 | 128607 | 12729 | 725 | 725 | 5.9948e-05 | 0.00021158 | 0.28333 | 1 | 0 | Mainline | 412820 | Recloser | Rec3phElectronic | [7 empty] | Other | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003094 | PD-01102020-00001 | METRO WEST | EL RENO | 8910:OKARCHE | OKARCHE_1021 | 891021 | 2020-01-10 02:12 | 2020-01-10 04:03 | 110.53 | 14 | 4 | 1252.0667 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKARCHE | SW-LAWRENCE + RUETER | CMI_NORMAL | NO | NO | NO | 860195 | 128607 | 12729 | 725 | 725 | 0.0014556 | 1.6275e-05 | 89.4333 | 1 | 310 | Mainline | 20343 | Fuse | FuseRiser | BAD ORDER PRIMARY RES COORD | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003099 |  | METRO WEST | EL RENO | 8910:OKARCHE | OKARCHE_1021 | 891021 | 2020-01-10 02:59 | 2020-01-10 02:59 | 0 | 283 | 0 | 0 | 28 | OTHER (DESCRIBE) | 4 | SWITCH - OIL | 0 | Okarche Substation | CMI_MOMENTARY | YES | NO | NO | 860195 | 128607 | 12729 | 725 | 725 | 0 | 0.000329 | 0 | 1 | 0 | Mainline | 412820 | Recloser | Rec3phElectronic | [7 empty] | Other | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003106 | PD-01102020-00004 | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-10 05:30 | 2020-01-10 07:50 | 140.47 | 1 | 1 | 140.4667 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | FORT SMITH | MAIN LINE FT CHAFFEE | CMI_NORMAL | NO | NO | NO | 860257 | 82148 | 61149 | 2732 | 2120 | 0.00016328 | 1.1624e-06 | 140.4667 | 1 | 310 | Customer | 90174 | Load | 0 | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003108 | PD-01102020-00008 | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-10 05:54 | 2020-01-10 07:17 | 82.5 | 1 | 1 | 82.5 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | FORT SMITH | 7712 Taylor Ave | CMI_NORMAL | NO | NO | NO | 860257 | 82148 | 61149 | 2732 | 2120 | 9.5902e-05 | 1.1624e-06 | 82.5 | 1 | 320 | Customer | 362471 | Load | Tran3phWye | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003112 | PD-01102020-00024 | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9871 | 839871 | 2020-01-10 07:01 | 2020-01-10 08:24 | 83.05 | 1 | 1 | 83.05 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | SHEFFIELD GLENN III BLK1, LOT 17 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 168032 | 148231 | 10651 | 2047 | 9.6541e-05 | 1.1624e-06 | 83.05 | 1 | 320 | Customer | 221354 | Load | Tran1phPad | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003114 | PD-01102020-00027 | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-10 07:35 | 2020-01-10 08:15 | 39.57 | 1 | 1 | 39.5667 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | FORT SMITH | ELLIS ST. | CMI_NORMAL | NO | NO | NO | 860257 | 82148 | 61149 | 2732 | 2120 | 4.5994e-05 | 1.1624e-06 | 39.5667 | 1 | 310 | Customer | 201650 | Load | Tran3phWye | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003115 | PD-01102020-00092 | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2161 | 892161 | 2020-01-10 07:47 | 2020-01-10 10:14 | 147.17 | 1 | 1 | 147.1667 | 12 | POOR CONNECTION | 50 | CONNECTOR | EL RENO | 1MS .5MW 81+66Y #2 | CMI_NORMAL | NO | NO | NO | 860257 | 128607 | 12729 | 3175 | 731 | 0.00017107 | 1.1624e-06 | 147.1667 | 1 | 320 | Load | 34229 | Load | TranOpenDelta | JOSH BLACK | 405-403-9382 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003118 |  | NORTHWEST | WOODWARD | 4611:DEWEY | DEWEY_1143 | 461143 | 2020-01-10 07:59 | 2020-01-10 07:59 | 0.05 | 677 | 0 | 33.85 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | SEILING | N2290 RD AND E0610 RD | CMI_MOMENTARY | YES | NO | NO | 860257 | 53499 | 10416 | 1319 | 677 | 3.9349e-05 | 0.00078697 | 0.05 | 1 | 0 | Feeder | DEWEY_1143 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003126 | PD-01102020-00117 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4033 | 834033 | 2020-01-10 08:12 | 2020-01-10 10:46 | 153.82 | 8 | 13 | 1218.4 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 10521 CONDOR TR | CMI_NORMAL | NO | NO | NO | 860257 | 128607 | 115878 | 10840 | 1115 | 0.0014163 | 9.2995e-06 | 152.3 | 1 | 310 | Load | 63035 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003122 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_624 | 460624 | 2020-01-10 08:14 | 2020-01-10 08:25 | 10.62 | 1 | 1 | 10.6167 | 1 | CANCELLED | 57 | CANCELLED | WOODWARD | 3305 WHEAT RIDGE-WOODWARD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 53499 | 10416 | 5680 | 488 | 1.2341e-05 | 1.1624e-06 | 10.6167 | 1 | 310 | Customer | 12425 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003132 | PD-01102020-00122 | NORTHWEST | WOODWARD | 4611:DEWEY | DEWEY_1141 | 461141 | 2020-01-10 08:17 | 2020-01-10 14:14 | 357.43 | 48 | 32 | 15992.8 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MUTUAL | .5ME,2 SPANS N-MUTUAL | CMI_NORMAL | NO | NO | NO | 860257 | 53499 | 10416 | 1319 | 614 | 0.018591 | 5.5797e-05 | 333.1833 | 1 | 310 | Mainline | 3155 | Recloser | Rec1phHydralic | HAYDEN BIERIG | 580-748-0538 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003138 |  | NORTHWEST | WOODWARD | 4611:DEWEY | DEWEY_1141 | 461141 | 2020-01-10 08:17 | 2020-01-10 10:15 | 117.97 | 1 | 2 | 91.9667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MUTUAL | .5E, 3-1/4S OF MUTUAL | CMI_NORMAL | NO | NO | NO | 860257 | 53499 | 10416 | 1319 | 614 | 0.00010691 | 1.1624e-06 | 91.9667 | 1 | 310 | Load | 10272 | Load | Tran1phOH | [7 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003134 | PD-01102020-00136 | NORTHWEST | WOODWARD | 4611:DEWEY | DEWEY_1141 | 461141 | 2020-01-10 08:17 | 2020-01-10 14:01 | 344.3 | 17 | 5 | 1563.15 | 25 | LIGHTNING | 2 | TRANSFORMER OH | MUTUAL | ALLY S-MIN,WEST-BDWY | CMI_NORMAL | NO | NO | NO | 860257 | 53499 | 10416 | 1319 | 614 | 0.0018171 | 1.9762e-05 | 91.95 | 1 | 310 | Mainline | 3317 | Fuse | FuseOH | HAYDEN BIERIG | 580-748-0538 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003124 |  | NORTHWEST | WOODWARD | 4611:DEWEY | DEWEY_1141 | 461141 | 2020-01-10 08:20 | 2020-01-10 14:39 | 379.2 | 1 | 1 | 89.1 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MUTUAL | 1-1/2E OF MUTUAL | CMI_NORMAL | NO | NO | NO | 860257 | 53499 | 10416 | 1319 | 614 | 0.00010357 | 1.1624e-06 | 89.1 | 1 | 310 | Customer | 10517 | Load | Tran1phOH | [7 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003129 | PD-01102020-00120 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6922 | 846922 | 2020-01-10 08:23 | 2020-01-10 09:21 | 57.82 | 1 | 1 | 57.8167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1120 NW.98 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 168032 | 148231 | 7716 | 1485 | 6.7209e-05 | 1.1624e-06 | 57.8167 | 1 | 310 | Customer | 1818 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003130 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-01-10 08:27 | 2020-01-10 12:50 | 262.95 | 2 | 0 | 45.9833 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | NOF SE 104 EOF MDWEST | CMI_PLANNED | YES | NO | NO | 860257 | 158988 | 56911 | 4204 | 3066 | 5.3453e-05 | 2.3249e-06 | 22.9917 | 1 | 0 | Mainline | 1896 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003229 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-10 08:29 | 2020-01-10 14:09 | 339.7 | 3 | 0 | 0.325 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MULBERRY | 6007 EAST HWY 64 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 82148 | 61149 | 3787 | 1204 | 3.7779e-07 | 3.4873e-06 | 0.10833 | 1 | 0 | Feeder | SIMMONS_3062 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003140 | PD-01102020-00137 | METRO WEST | WEST | 8158:SARA | SARA_5862 | 815862 | 2020-01-10 08:38 | 2020-01-10 12:29 | 230.72 | 1 | 1 | 227.35 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | CEDAR RIDGE | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860257 | 128607 | 115878 | 18216 | 3596 | 0.00026428 | 1.1624e-06 | 227.35 | 1 | 320 | Customer | 234889 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003145 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_863 | 830863 | 2020-01-10 08:45 | 2020-01-10 13:18 | 273 | 2 | 0 | 546.0067 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | 0 | 0 | CMI_PLANNED | YES | NO | NO | 860257 | 168032 | 148231 | 19354 | 1672 | 0.0006347 | 2.3249e-06 | 273.0034 | 1 | 0 | Mainline | 75592-1 | Switch | SwitchDefault | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003147 | PD-01102020-00142 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5024 | 865024 | 2020-01-10 08:48 | 2020-01-10 09:34 | 45.55 | 1 | 1 | 45.55 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 7201 SE 29st | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 114304 | 71179 | 8623 | 1072 | 5.2949e-05 | 1.1624e-06 | 45.55 | 1 | 310 | Customer | 209136 | Load | Tran3phPadWye | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003146 | PD-01102020-00139 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-10 08:48 | 2020-01-10 10:38 | 109.55 | 1 | 1 | 109.55 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MOUNTAINBURG | OLD SHEPHERD SPRINGS RD | CMI_NORMAL | NO | NO | NO | 860257 | 82148 | 61149 | 3787 | 1204 | 0.00012735 | 1.1624e-06 | 109.55 | 1 | 310 | Load | 220489 | Load | TranOH3phDelta | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003153 | PD-01102020-00154 | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-01-10 08:59 | 2020-01-10 14:46 | 346.6 | 1 | 1 | 346.6 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 6500 SE. 164HT ST. | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860257 | 158988 | 56911 | 4204 | 3066 | 0.0004029 | 1.1624e-06 | 346.6 | 1 | 310 | Load | 12556 | Load | Tran1phOH | JUSTIN C TAYLOR | 405-534-1006 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003154 |  | NORTHWEST | WOODWARD | 4608:WOODWARD DISTR | WOODWARD_DIST_846 | 460846 | 2020-01-10 09:02 | 2020-01-10 09:02 | 0 | 652 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | WOODWARD | 204079 E COUNTY RD 44 | CMI_MOMENTARY | YES | NO | NO | 860257 | 53499 | 10416 | 1213 | 652 | 0 | 0.00075791 | 0 | 1 | 0 | Feeder | WOODWD DIS_846 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003160 |  | NORTHWEST | WOODWARD | 4611:DEWEY | DEWEY_1141 | 461141 | 2020-01-10 09:04 | 2020-01-10 10:52 | 107.88 | 1 | 1 | 44.4167 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | CAMARGO | 5S-MUTUAL,1 E | CMI_NORMAL | NO | NO | NO | 860257 | 53499 | 10416 | 1319 | 614 | 5.1632e-05 | 1.1624e-06 | 44.4167 | 1 | 310 | Customer | 10271 | Load | Tran1phOH | [7 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003159 |  | NORTHWEST | ALVA | 4705:ALVA | ALVA_523 | 470523 | 2020-01-10 09:05 | 2020-01-10 09:05 | 0 | 581 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ALVA | 418 MILL ST | CMI_MOMENTARY | YES | NO | NO | 860257 | 53499 | 5517 | 2438 | 581 | 0 | 0.00067538 | 0 | 1 | 0 | Feeder | ALVA_523 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003161 |  | NORTHWEST | WOODWARD | 4611:DEWEY | DEWEY_1141 | 461141 | 2020-01-10 09:05 | 2020-01-10 10:52 | 106.82 | 1 | 1 | 43.1667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MUTUAL | 2 3/4ME OF MUTUAL ON E0540 RD./MAIN ST. | CMI_NORMAL | NO | NO | NO | 860257 | 53499 | 10416 | 1319 | 614 | 5.0179e-05 | 1.1624e-06 | 43.1667 | 1 | 310 | Load | 399697 | Load | Tran3phWye | [7 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003162 | PD-01102020-00165 | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2824 | 312824 | 2020-01-10 09:06 | 2020-01-10 10:02 | 56.02 | 1 | 1 | 36.9333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MUSKOGEE | 715 N.J | CMI_NORMAL | NO | NO | NO | 860257 | 73936 | 33220 | 5271 | 1609 | 4.2933e-05 | 1.1624e-06 | 36.9333 | 1 | 310 | Customer | 1462 | Load | Tran3phWye | JOSH CHENEY | 918-619-3590 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003165 | PD-01102020-00166 | ARKANSAS | POTEAU | 3514:HEAVENER | HEAVENER 22 | 351422 | 2020-01-10 09:16 | 2020-01-10 10:10 | 53.92 | 1 | 1 | 53.9167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | HEAVENER | 507 EAST 6 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 82148 | 13467 | 1766 | 1303 | 6.2675e-05 | 1.1624e-06 | 53.9167 | 1 | 310 | Customer | 2862 | Load | Tran1phOH | TOBY C MEAD | 918-658-5596 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003168 | PD-01102020-00174 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6961 | 846961 | 2020-01-10 09:19 | 2020-01-10 10:36 | 76.63 | 2 | 2 | 153.2667 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 24 W.MEMORIAL RD B8 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 168032 | 148231 | 7716 | 1387 | 0.00017816 | 2.3249e-06 | 76.6333 | 1 | 310 | Secondary | 69038 | Load | Tran3phPadWye | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003173 |  | NORTHEAST | SAPULPA | 3216:BEELINE | BEELINE_1626 | 321626 | 2020-01-10 09:33 | 2020-01-10 10:35 | 62.23 | 1 | 0 | 52.85 | 4 | DETERIORATION | 12 | POLE | 0 | 3 MW BIXBY | CMI_PLANNED | YES | NO | NO | 860257 | 73936 | 40716 | 5556 | 919 | 6.1435e-05 | 1.1624e-06 | 52.85 | 1 | 0 | Load | 45130 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003174 | PD-01102020-00188 | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-01-10 09:37 | 2020-01-10 11:17 | 100.22 | 1 | 1 | 27.4363 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 517 GREENVALE RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 128607 | 115878 | 3405 | 2036 | 3.1893e-05 | 1.1624e-06 | 27.4363 | 1 | 310 | Customer | 30777 | Load | Tran1phPad | BRANDON H SMITH | 405-371-4294 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003176 |  | NORTHEAST | MUSKOGEE | 3312:CHECOTAH | CHECOTAH 22 | 331222 | 2020-01-10 09:42 | 2020-01-10 09:53 | 11.75 | 4 | 0 | 47.0199 | 4 | DETERIORATION | 12 | POLE | 0 | S.OF WATER PLANT | CMI_PLANNED | YES | NO | NO | 860257 | 73936 | 33220 | 2881 | 1526 | 5.4658e-05 | 4.6498e-06 | 11.755 | 1 | 0 | Tap | 190660 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003178 | PD-01102020-00200 | METRO EAST | CHANDLER | 7119:WARWICK | WARWICK_1942 | 711942 | 2020-01-10 09:45 | 2020-01-10 11:36 | 110.87 | 1 | 1 | 110.8667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | CARNEY | 614 W.CENTRAL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 114304 | 7454 | 2415 | 956 | 0.00012888 | 1.1624e-06 | 110.8667 | 1 | 310 | Customer | 13530 | Load | Tran1phOH | SCOTT C PERRY | 405-258-6044 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003184 | PD-01102020-00198 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_526 | 510526 | 2020-01-10 09:47 | 2020-01-10 12:51 | 184.43 | 167 | 132 | 28056 | 25 | LIGHTNING | 37 | CONDUCTOR PRIMARY - OH | ARDMORE | N OF CAMPBELL-MT WASH | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 23570 | 4769 | 1619 | 0.032614 | 0.00019413 | 168 | 1 | 310 | Mainline | 3932 | Fuse | FuseOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003179 |  | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_429 | 580429 | 2020-01-10 09:50 | 2020-01-10 10:51 | 61.25 | 1 | 2 | 61.2352 | 23 | CUSTOMER EQUIPMENT | 39 | BUSHING | ADA | S OF ST HWY 1 N OF ARLNGTN BVD | CMI_PLANNED | YES | NO | NO | 860257 | 77550 | 11505 | 3411 | 1343 | 7.1182e-05 | 1.1624e-06 | 61.2352 | 1 | 310 | Customer | 21594 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003181 |  | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_526 | 510526 | 2020-01-10 09:50 | 2020-01-10 12:57 | 186.6 | 1 | 1 | 186.6 | 25 | LIGHTNING | 37 | CONDUCTOR PRIMARY - OH | ARDMORE | 1213 N.WASHINGTON | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 23570 | 4769 | 1619 | 0.00021691 | 1.1624e-06 | 186.6 | 1 | 310 | Customer | 2949 | Load | TranOH3phDelta | [7 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003187 |  | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_526 | 510526 | 2020-01-10 09:53 | 2020-01-10 12:58 | 184.4 | 1 | 1 | 184.4 | 25 | LIGHTNING | 37 | CONDUCTOR PRIMARY - OH | ARDMORE | 106 FREEMAN | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 23570 | 4769 | 1619 | 0.00021435 | 1.1624e-06 | 184.4 | 1 | 320 | Customer | 7425 | Load | Tran1phOH | [7 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003188 |  | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_526 | 510526 | 2020-01-10 09:54 | 2020-01-10 12:59 | 185.35 | 1 | 1 | 185.35 | 25 | LIGHTNING | 37 | CONDUCTOR PRIMARY - OH | ARDMORE | 7 10 NW. TEMP | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 23570 | 4769 | 1619 | 0.00021546 | 1.1624e-06 | 185.35 | 1 | 310 | Customer | 3128 | Load | Tran1phOH | [7 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003193 |  | NORTHEAST | SAPULPA | 3216:BEELINE | BEELINE_1633 | 321633 | 2020-01-10 09:58 | 2020-01-10 10:51 | 52.87 | 43 | 44 | 2180.8167 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | GLENPOOL | ROLLING MEADOWS 2 | CMI_PLANNED | YES | NO | NO | 860257 | 73936 | 40716 | 5556 | 1946 | 0.0025351 | 4.9985e-05 | 50.7167 | 1 | 310 | Mainline | 62500 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003194 |  | NORTHEAST | SAPULPA | 3216:BEELINE | BEELINE_1633 | 321633 | 2020-01-10 09:58 | 2020-01-10 10:52 | 53.05 | 10 | 11 | 497.1667 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | GLENPOOL | 14749 S VANCOUVER AV | CMI_PLANNED | YES | NO | NO | 860257 | 73936 | 40716 | 5556 | 1946 | 0.00057793 | 1.1624e-05 | 49.7167 | 1 | 310 | Load | 20071 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003199 | PD-01102020-00219 | ARKANSAS | POTEAU | 3505:POTEAU | POTEAU_529 | 350529 | 2020-01-10 09:59 | 2020-01-10 11:16 | 76.83 | 63 | 27 | 4377.45 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | POTEAU | CLAYTON & SADDLER ST | CMI_NORMAL | NO | NO | NO | 860257 | 82148 | 13467 | 2296 | 439 | 0.0050885 | 7.3234e-05 | 69.4833 | 1 | 310 | Mainline | 17857 | Fuse | FuseOH | JOHN MEEH | 918-413-0959 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003195 |  | ARKANSAS | POTEAU | 3505:POTEAU | POTEAU_529 | 350529 | 2020-01-10 09:59 | 2020-01-10 09:59 | 0 | 439 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | POTEAU | 1100 SOUTH MCKENNA | CMI_MOMENTARY | YES | NO | NO | 860257 | 82148 | 13467 | 2296 | 439 | 0 | 0.00051031 | 0 | 1 | 0 | Feeder | POTEAU_529 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003198 |  | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_526 | 510526 | 2020-01-10 10:04 | 2020-01-10 12:58 | 174.35 | 1 | 1 | 174.35 | 25 | LIGHTNING | 37 | CONDUCTOR PRIMARY - OH | ARDMORE | 313 11 NE. | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 23570 | 4769 | 1619 | 0.00020267 | 1.1624e-06 | 174.35 | 1 | 310 | Customer | 21824 | Load | Tran1phOH | [7 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003200 | PD-01102020-00224 | ARKANSAS | POTEAU | 3505:POTEAU | POTEAU_529 | 350529 | 2020-01-10 10:11 | 2020-01-10 11:25 | 73.78 | 1 | 1 | 73.7833 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | POTEAU | 1001 DEWEY | CMI_NORMAL | NO | NO | NO | 860257 | 82148 | 13467 | 2296 | 439 | 8.5769e-05 | 1.1624e-06 | 73.7833 | 1 | 310 | Load | 9990 | Load | Tran1phOH | JOHN MEEH | 918-413-0959 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003203 | PD-01102020-00222 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2221 | 832221 | 2020-01-10 10:12 | 2020-01-10 10:53 | 40.88 | 1 | 1 | 40.8833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 4904 N.STEANSON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 168032 | 148231 | 9168 | 1658 | 4.7525e-05 | 1.1624e-06 | 40.8833 | 1 | 310 | Customer | 15396 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003208 | PD-01102020-00238 | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 21 | 570821 | 2020-01-10 10:18 | 2020-01-10 11:58 | 99.75 | 1 | 1 | 99.75 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | DAVIS | 1E-.7N OF DAVIS | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 6809 | 1857 | 902 | 0.00011595 | 1.1624e-06 | 99.75 | 1 | 310 | Load | 22304 | Load | Tran1phOH | BRUCE E BEAM | 405-626-0490 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003209 | PD-01102020-00236 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5024 | 865024 | 2020-01-10 10:20 | 2020-01-10 11:48 | 87.8 | 1 | 1 | 87.8 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 539 E.HARMON DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 114304 | 71179 | 8623 | 1072 | 0.00010206 | 1.1624e-06 | 87.8 | 1 | 310 | Customer | 7167 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003210 |  | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6224 | 866224 | 2020-01-10 10:21 | 2020-01-10 10:31 | 9.45 | 1 | 1 | 9.45 | 1 | CANCELLED | 57 | CANCELLED | MIDWEST CITY | 108 GOLDSBOROUGH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 114304 | 71179 | 7201 | 1779 | 1.0985e-05 | 1.1624e-06 | 9.45 | 1 | 310 | Customer | 61621 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003211 | PD-01102020-00228 | ARKANSAS | POTEAU | 3505:POTEAU | POTEAU_531 | 350531 | 2020-01-10 10:24 | 2020-01-10 11:50 | 86.17 | 1 | 1 | 44.7 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | POTEAU | ROGERS + HARPER ST | CMI_NORMAL | NO | NO | NO | 860257 | 82148 | 13467 | 2296 | 778 | 5.1961e-05 | 1.1624e-06 | 44.7 | 1 | 310 | Load | 20654 | Load | TranOpenDelta | JOHN MEEH | 918-413-0959 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003213 | PD-01102020-00232 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2022 | 822022 | 2020-01-10 10:25 | 2020-01-10 11:07 | 41.82 | 1 | 1 | 22.506 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2737 NW 19TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 168032 | 148231 | 6035 | 2119 | 2.6162e-05 | 1.1624e-06 | 22.506 | 1 | 310 | Customer | 15279 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003232 | PD-01102020-00261 | NORTHEAST | MUSKOGEE | 3136:EUCLID | EUCLID_3629 | 313629 | 2020-01-10 10:54 | 2020-01-10 12:29 | 95.1 | 37 | 33 | 2929.1667 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | MUSKOGEE | DAYTON W.OF "G" | CMI_NORMAL | NO | NO | NO | 860257 | 73936 | 33220 | 980 | 615 | 0.003405 | 4.301e-05 | 79.1667 | 1 | 310 | Tap | 14914 | Fuse | FuseOH | REID R WILLIAMS | 512-618-8800 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | #N/A
J2001.003236 | PD-01102020-00265 | NORTHEAST | MUSKOGEE | 3136:EUCLID | EUCLID_3631 | 313631 | 2020-01-10 10:55 | 2020-01-10 13:13 | 137.77 | 4 | 3 | 530.0667 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | MUSKOGEE | ENID-ALLEY E OF SUMMIT | CMI_NORMAL | NO | NO | NO | 860257 | 73936 | 33220 | 980 | 348 | 0.00061617 | 4.6498e-06 | 132.5167 | 1 | 310 | Tap | 7497 | Fuse | FuseOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | #N/A
J2001.003228 |  | NORTHEAST | MUSKOGEE | 3136:EUCLID | EUCLID_3631 | 313631 | 2020-01-10 10:55 | 2020-01-10 10:55 | 0 | 348 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MUSKOGEE | 2513 EUCLID AVE | CMI_MOMENTARY | YES | NO | NO | 860257 | 73936 | 33220 | 980 | 348 | 0 | 0.00040453 | 0 | 1 | 0 | Feeder | EUCLID_3631 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-10 | 2020 |  | #N/A
J2001.003234 |  | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2824 | 312824 | 2020-01-10 11:02 | 2020-01-10 11:02 | 0.02 | 1609 | 0 | 26.8167 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MUSKOGEE | 2431 INDIANA | CMI_MOMENTARY | YES | NO | NO | 860257 | 73936 | 33220 | 5271 | 1609 | 3.1173e-05 | 0.0018704 | 0.016667 | 1 | 0 | Feeder | HANCOCK_2824 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003243 | PD-01102020-00275 | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2824 | 312824 | 2020-01-10 11:09 | 2020-01-10 11:52 | 43.03 | 29 | 10 | 1247.9667 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | MUSKOGEE | HOUSTON E OF "K" | CMI_NORMAL | NO | NO | NO | 860257 | 73936 | 33220 | 5271 | 1609 | 0.0014507 | 3.3711e-05 | 43.0333 | 1 | 310 | Tap | 10187 | Fuse | FuseOH | REID R WILLIAMS | 512-618-8800 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003324 | PD-01102020-00340 | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2824 | 312824 | 2020-01-10 11:09 | 2020-01-10 13:58 | 169.17 | 8 | 3 | 1290 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MUSKOGEE | 1111 GALVESTON | CMI_NORMAL | NO | NO | NO | 860257 | 73936 | 33220 | 5271 | 1609 | 0.0014996 | 9.2995e-06 | 161.25 | 1 | 310 | Load | 4444 | Load | Tran1phOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003237 |  | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2824 | 312824 | 2020-01-10 11:09 | 2020-01-10 11:09 | 0 | 1609 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MUSKOGEE | 2431 INDIANA | CMI_MOMENTARY | YES | NO | NO | 860257 | 73936 | 33220 | 5271 | 1609 | 0 | 0.0018704 | 0 | 1 | 0 | Feeder | HANCOCK_2824 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003238 |  | NORTHEAST | SAPULPA | 3216:BEELINE | BEELINE_1633 | 321633 | 2020-01-10 11:10 | 2020-01-10 11:45 | 34.93 | 27 | 5 | 249.1833 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | GLENPOOL | 14797 S VANCOUVER AV | CMI_PLANNED | YES | NO | NO | 860257 | 73936 | 40716 | 5556 | 1946 | 0.00028966 | 3.1386e-05 | 9.229 | 1 | 310 | Mainline | 62501 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003241 |  | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_863 | 550863 | 2020-01-10 11:12 | 2020-01-10 11:12 | 0.02 | 622 | 0 | 10.3667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | BROWN | WEST OF N3670 RD ON E2020RD | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 15475 | 1103 | 622 | 1.2051e-05 | 0.00072304 | 0.016667 | 1 | 0 | Feeder | BROW OGE_863 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003242 |  | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_621 | 550621 | 2020-01-10 11:12 | 2020-01-10 11:12 | 0 | 900 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | DURANT | 1400 BRYAN DR | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 15475 | 6732 | 899 | 0 | 0.0010462 | 0 | 1 | 0 | Feeder | BODLE ST_621 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003246 | PD-01102020-00276 | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-01-10 11:15 | 2020-01-10 12:06 | 51.25 | 1 | 1 | 52.4 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | BRANCH | 1300BLK OF CAMMILL ST | CMI_NORMAL | NO | NO | NO | 860257 | 82148 | 61149 | 959 | 490 | 6.0912e-05 | 1.1624e-06 | 52.4 | 1 | 310 | Load | 177890 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Weather | N | DISTRIBUTION | 34.5/19.9kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003245 | PD-01102020-00272 | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_523 | 530523 | 2020-01-10 11:15 | 2020-01-10 12:09 | 54.03 | 1 | 1 | 29.0276 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | WILSON | LONGEST OAKS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 77550 | 6787 | 2126 | 868 | 3.3743e-05 | 1.1624e-06 | 29.0276 | 1 | 310 | Customer | 8957 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003252 | PD-01102020-00288 | METRO WEST | WEST | 8158:SARA | SARA_5862 | 815862 | 2020-01-10 11:25 | 2020-01-10 12:38 | 72.77 | 1 | 1 | 72.7667 | 22 | WIND | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | Tpk.1/4E of 4915 S.Morgan Rd. | CMI_NORMAL | NO | NO | NO | 860257 | 128607 | 115878 | 18216 | 3596 | 8.4587e-05 | 1.1624e-06 | 72.7667 | 1 | 310 | Load | 419158 | Load | Tran1phOH | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003256 | PD-01102020-00289 | METRO NORTH | NORTH | 8209:CLASSEN | CLASSEN_923 | 820923 | 2020-01-10 11:26 | 2020-01-10 15:32 | 246.08 | 1 | 1 | 9.7213 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1312 NW.11 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 168032 | 148231 | 3880 | 1146 | 1.13e-05 | 1.1624e-06 | 9.7213 | 1 | 310 | Customer | 16324 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003335 | PD-01102020-00294 | NORTHEAST | MUSKOGEE | 3109:HONOR HEIGHTS | HONOR_HEIGHTS_921 | 310921 | 2020-01-10 11:28 | 2020-01-10 13:32 | 123.9 | 117 | 25 | 14517.75 | 25 | LIGHTNING | 37 | CONDUCTOR PRIMARY - OH | MUSKOGEE | 59TH + W.OKMULGEE | CMI_NORMAL | NO | NO | NO | 860257 | 73936 | 33220 | 1176 | 1154 | 0.016876 | 0.00013601 | 124.0833 | 1 | 310 | Mainline | 1417 | Fuse | FuseOH | STEVE K HIGHFILL | 918-869-2785 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003261 |  | ARKANSAS | FORT SMITH | 9104:J STREET | J_STREET_431 | 910431 | 2020-01-10 11:30 | 2020-01-10 11:36 | 5.25 | 1 | 1 | 5.25 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | DEBBIE ADDN 2 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 82148 | 61149 | 2004 | 845 | 6.1028e-06 | 1.1624e-06 | 5.25 | 1 | 310 | Customer | 256128 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003259 | PD-01102020-00292 | METRO EAST | SHAWNEE | 7417:TRIBBEY | TRIBBEY_1721 | 741721 | 2020-01-10 11:32 | 2020-01-10 12:54 | 82.5 | 1 | 2 | 80.9667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MACOMB | 1.5N .5W .5N WS | CMI_NORMAL | NO | NO | NO | 860257 | 114304 | 22083 | 241 | 241 | 9.4119e-05 | 1.1624e-06 | 80.9667 | 1 | 310 | Load | 13126 | Load | Tran1phOH | ADAM CLARK | 580-310-8924 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003268 | PD-01102020-00302 | SOUTHERN | MADILL | 5906:TISHOMINGO | TISHOMINGO_621 | 590621 | 2020-01-10 11:41 | 2020-01-10 13:15 | 93.82 | 1 | 1 | 93.8167 | 25 | LIGHTNING | 2 | TRANSFORMER OH | TISHOMINGO | MURRAY COLLEGE TISHOMINGO,OK | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 7202 | 967 | 916 | 0.00010906 | 1.1624e-06 | 93.8167 | 1 | 320 | Load | 90069 | Load | 0 | ROBERT J BEARDSLEE | 580-618-2506 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003270 |  | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1521 | 811521 | 2020-01-10 11:45 | 2020-01-10 11:45 | 0.02 | 1239 | 0 | 20.65 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 2101 SW 22ND ST | CMI_MOMENTARY | YES | NO | NO | 860257 | 158988 | 102077 | 6054 | 1239 | 2.4004e-05 | 0.0014403 | 0.016667 | 1 | 0 | Feeder | SW 22ND_1521 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003272 |  | NORTHWEST | WOODWARD | 4611:DEWEY | DEWEY_1141 | 461141 | 2020-01-10 11:47 | 2020-01-10 11:47 | 0 | 545 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | SEILING | N2290 RD AND E0610 RD | CMI_MOMENTARY | YES | NO | NO | 860257 | 53499 | 10416 | 1319 | 614 | 0 | 0.00063353 | 0 | 1 | 0 | Feeder | DEWEY_1141 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003301 | PD-01102020-00312 | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_861 | 550861 | 2020-01-10 11:49 | 2020-01-10 16:01 | 251.68 | 361 | 119 | 43817.9167 | 25 | LIGHTNING | 37 | CONDUCTOR PRIMARY - OH | COBB | 0 | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 15475 | 1103 | 481 | 0.050936 | 0.00041964 | 121.3793 | 1 | 310 | Mainline |  | 0 | 0 | JEREMY L MULLENS | 580-775-3134 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003275 |  | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_861 | 550861 | 2020-01-10 11:50 | 2020-01-10 11:50 | 0.25 | 481 | 0 | 120.25 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | BROWN | WEST OF N3670 RD ON E2020RD | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 15475 | 1103 | 481 | 0.00013978 | 0.00055914 | 0.25 | 1 | 0 | Feeder | BROW OGE_861 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003279 | PD-01102020-00338 | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_861 | 550861 | 2020-01-10 11:53 | 2020-01-10 16:01 | 248.17 | 2 | 1 | 331.5833 | 25 | LIGHTNING | 37 | CONDUCTOR PRIMARY - OH | DURANT | 3006 BRYAN RD | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 15475 | 1103 | 481 | 0.00038545 | 2.3249e-06 | 165.7917 | 1 | 310 | Load | 360862 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003323 | PD-01102020-00336 | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_861 | 550861 | 2020-01-10 11:54 | 2020-01-10 13:47 | 112.88 | 1 | 1 | 112.8833 | 25 | LIGHTNING | 37 | CONDUCTOR PRIMARY - OH | DURANT | 213 E FOREST LN | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 15475 | 1103 | 481 | 0.00013122 | 1.1624e-06 | 112.8833 | 1 | 310 | Load | 366898 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003314 | PD-01102020-00324 | NORTHEAST | MUSKOGEE | 3326:JAMESVILLE | JAMESVILLE_2623 | 332623 | 2020-01-10 12:06 | 2020-01-10 14:13 | 127.27 | 2 | 2 | 254.4667 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | HASKELL | .75MEOF HY64 ON SKELLY | CMI_NORMAL | NO | NO | NO | 860257 | 73936 | 33220 | 1549 | 403 | 0.0002958 | 2.3249e-06 | 127.2333 | 1 | 310 | Tap | 14167 | Fuse | FuseOH | REID R WILLIAMS | 512-618-8800 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003311 | PD-01102020-00346 | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_723 | 510723 | 2020-01-10 12:10 | 2020-01-10 13:50 | 99.53 | 1 | 2 | 90.9167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ARDMORE | 320 D NW | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 23570 | 4509 | 1215 | 0.00010569 | 1.1624e-06 | 90.9167 | 1 | 310 | Customer | 23220 | Load | TranOpenDelta | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003322 | PD-01102020-00337 | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_861 | 550861 | 2020-01-10 12:16 | 2020-01-10 13:51 | 95.02 | 1 | 1 | 95.0167 | 25 | LIGHTNING | 37 | CONDUCTOR PRIMARY - OH | DURANT | 3000 Bryan Rd | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 15475 | 1103 | 481 | 0.00011045 | 1.1624e-06 | 95.0167 | 1 | 310 | Load | 352322 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003315 | PD-01102020-00347 | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 21 | 570821 | 2020-01-10 12:22 | 2020-01-10 13:37 | 75.17 | 1 | 1 | 62.3167 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | DAVIS | 348 SUNSHINE RD. | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 6809 | 1857 | 902 | 7.244e-05 | 1.1624e-06 | 62.3167 | 1 | 310 | Load | 383619 | Load | Tran1phPad | CHAD A DOTSON | 405-488-5658 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003316 | PD-01102020-00372 | METRO WEST | WEST | 8335:BETHANY | BETHANY_3526 | 833526 | 2020-01-10 12:24 | 2020-01-10 13:53 | 89.38 | 1 | 1 | 38.6742 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | BETHANY | 6412 NW.30 TR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 128607 | 115878 | 7861 | 2061 | 4.4957e-05 | 1.1624e-06 | 38.6742 | 1 | 310 | Customer | 50656 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003317 | PD-01102020-00348 | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_861 | 550861 | 2020-01-10 12:25 | 2020-01-10 13:28 | 62.7 | 1 | 1 | 60.0833 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | DURANT | .5 WEST OF HWY22 AND HWY 199 | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 15475 | 1103 | 481 | 6.9843e-05 | 1.1624e-06 | 60.0833 | 1 | 310 | Load | 24842 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003325 |  | SOUTHERN | DURANT | 5512:COLBERT | COLBERT_1221 | 551221 | 2020-01-10 12:44 | 2020-01-10 12:44 | 0 | 895 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | COLBERT | 45 STIDEHAM RD | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 15475 | 2165 | 895 | 0 | 0.0010404 | 0 | 1 | 0 | Feeder | COLBERT_1221 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003328 |  | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2824 | 312824 | 2020-01-10 12:45 | 2020-01-10 12:59 | 14.02 | 1 | 1 | 14.0167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 617 LEXINGTON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 73936 | 33220 | 5271 | 1609 | 1.6294e-05 | 1.1624e-06 | 14.0167 | 1 | 310 | Customer | 4234 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003327 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1024 | 541024 | 2020-01-10 12:46 | 2020-01-10 12:47 | 1.2 | 661 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MADILL | 12537 HIGHWAY 199 | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 7202 | 2379 | 661 | 0 | 0.00076838 | 0 | 1 | 0 | Feeder | GLASSES_1024 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003346 | PD-01102020-00383 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2222 | 852222 | 2020-01-10 12:51 | 2020-01-10 14:16 | 84.58 | 1 | 2 | 82.2 | 22 | WIND | 21 | FUSE - TRANSFORMER | HARRAH | 1210 SECOND ST | CMI_NORMAL | NO | NO | NO | 860257 | 114304 | 71179 | 11621 | 2211 | 9.5553e-05 | 1.1624e-06 | 82.2 | 1 | 310 | Load | 2708 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003329 | PD-01102020-00528 | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_861 | 550861 | 2020-01-10 12:52 | 2020-01-10 16:52 | 240.27 | 1 | 1 | 135.3167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DURANT | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 0 | 0 | 0 | 0 | 0.0001573 | 1.1624e-06 | 135.3167 | 1 | 310 | Customer |  | 0 | 0 | JUSTIN DUVAL | 580-380-5747 |  |  |  |  | 06/02/2020 note from burchamc. Reference J2001.003329 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003347 | PD-01102020-00488 | SOUTHERN | MADILL | 5408:CANEY CREEK | CANEY_CREEK_831 | 540831 | 2020-01-10 12:53 | 2020-01-10 15:44 | 171.45 | 3 | 6 | 509.8 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | KINGSTON | S.KEMP + 2ND ST | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 7202 | 1053 | 629 | 0.00059261 | 3.4873e-06 | 169.9333 | 1 | 310 | Load | 16635 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003339 | PD-01102020-00377 | SOUTHERN | MADILL | 5408:CANEY CREEK | CANEY_CREEK_831 | 540831 | 2020-01-10 12:53 | 2020-01-10 14:38 | 105.43 | 6 | 7 | 1320.4 | 25 | LIGHTNING | 2 | TRANSFORMER OH | KINGSTON | ALLEY W WILLIS AT 5TH-KINGSTON | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 7202 | 1053 | 629 | 0.0015349 | 6.9747e-06 | 220.0667 | 1 | 310 | Load | 11513 | Load | Tran1phOH | ROBERT J BEARDSLEE | 580-618-2506 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003331 |  | METRO WEST | WEST | 8266:MUSTANG STA | MUSTANG_STA_6629 | 826629 | 2020-01-10 12:56 | 2020-01-10 12:56 | 0.23 | 5 | 0 | 1.1667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | 0 | 0 | CMI_MOMENTARY | YES | NO | NO | 860257 | 128607 | 115878 | 5 | 5 | 1.3562e-06 | 5.8122e-06 | 0.23333 | 1 | 0 | Feeder | MUSTANG_STA_6629 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003344 | PD-01102020-00386 | NORTHEAST | MUSKOGEE | 3109:HONOR HEIGHTS | HONOR_HEIGHTS_921 | 310921 | 2020-01-10 13:04 | 2020-01-10 14:21 | 77.43 | 1 | 1 | 28.55 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MUSKOGEE | 411 N.48 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 73936 | 33220 | 1176 | 1154 | 3.3188e-05 | 1.1624e-06 | 28.55 | 1 | 310 | Customer | 8123 | Load | Tran1phOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003345 | PD-01102020-00387 | NORTHEAST | MUSKOGEE | 3136:EUCLID | EUCLID_3631 | 313631 | 2020-01-10 13:06 | 2020-01-10 15:12 | 126.38 | 1 | 1 | 2.1333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MUSKOGEE | 1700 beacon | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 73936 | 33220 | 980 | 348 | 2.4799e-06 | 1.1624e-06 | 2.1333 | 1 | 320 | Load | 370494 | Load | Tran3phWye | JAMES C EVANS | 918-869-1174 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | #N/A
J2001.003352 | PD-01102020-00393 | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-01-10 13:19 | 2020-01-10 15:30 | 131.38 | 1 | 1 | 127.6167 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MILBURN | HWY 78/WILLARD RD .3 N ES | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 7202 | 2191 | 1673 | 0.00014835 | 1.1624e-06 | 127.6167 | 1 | 310 | Load | 209233 | Load | Tran1phOH | DAVID TAYLOR | 580-574-4517 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003366 |  | NORTHWEST | ENID | 4354:BRONCO ROAD | BRONCO ROAD 01 | 435401 | 2020-01-10 13:21 | 2020-01-10 21:52 | 510.45 | 1 | 2 | 468.7667 | 17 | TRANSMISSION OPERATION | 56 | SCADA - LOCKOUT | ORLANDO | 1 mile North and 3 1/2 miles West of Orlando Oklahoma, just West of intersection of E 0580 Rd and N 3130 Rd | CMI_NORMAL | NO | NO | NO | 860257 | 53499 | 37566 | 1 | 1 | 0.00054491 | 1.1624e-06 | 468.7667 | 1 | 310 | Feeder | BRONCO ROAD 01 | Breaker | SubBreaker | [7 empty] | Equipment | N | TRANSMISSION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003358 | PD-01102020-00418 | SOUTHERN | MADILL | 5408:CANEY CREEK | CANEY_CREEK_831 | 540831 | 2020-01-10 13:22 | 2020-01-10 15:15 | 113.67 | 36 | 17 | 4254.3 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | KINGSTON | 7TH BTW MYTBBY + KEMP | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 7202 | 1053 | 629 | 0.0049454 | 4.1848e-05 | 118.175 | 1 | 310 | Mainline | 3445 | Fuse | FuseOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003363 | PD-01102020-00420 | SOUTHERN | MADILL | 5408:CANEY CREEK | CANEY_CREEK_831 | 540831 | 2020-01-10 13:22 | 2020-01-10 15:29 | 127.33 | 4 | 5 | 472.7333 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | KINGSTON | 1ST + MAYTUBBY KINGSTON OK | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 7202 | 1053 | 629 | 0.00054953 | 4.6498e-06 | 118.1833 | 1 | 310 | Load | 6705 | Load | TranOH3phDelta | GARRETT YOUNG | 580-276-6194 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003360 | PD-01102020-00397 | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_622 | 550622 | 2020-01-10 13:27 | 2020-01-10 13:56 | 29.38 | 1 | 1 | 29.3833 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | DURANT | 301 GERLACH DR. | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 15475 | 6732 | 556 | 3.4156e-05 | 1.1624e-06 | 29.3833 | 1 | 321 | Load | 17956 | Load | Tran3phWye | MICHAEL N STROHL | 903-821-1619 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003441 | PD-01102020-00402 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1424 | 311424 | 2020-01-10 13:28 | 2020-01-10 15:57 | 148.73 | 13 | 2 | 1197.7333 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | MUSKOGEE | MILITARY BLVD AND N 32ND ST US HWY 69 | CMI_NORMAL | NO | NO | NO | 860257 | 73936 | 33220 | 4561 | 798 | 0.0013923 | 1.5112e-05 | 92.1333 | 1 | 310 | Mainline | 353639 | Fuse | FuseOH | REID R WILLIAMS | 512-618-8800 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003361 | PD-01102020-00401 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_863 | 830863 | 2020-01-10 13:28 | 2020-01-10 14:01 | 32.9 | 1 | 1 | 20.3833 | 28 | OTHER (DESCRIBE) | 41 | OTHER | OKLAHOMA CITY | NW140TH + PENN-HOBBY LOBBY | CMI_NORMAL | NO | NO | NO | 860257 | 168032 | 148231 | 19354 | 1672 | 2.3694e-05 | 1.1624e-06 | 20.3833 | 1 | 310 | Load | 81206 | Load | Tran3phPadWye | JERRY CASNER | 405-620-0772 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003371 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1024 | 541024 | 2020-01-10 13:39 | 2020-01-10 13:39 | 0 | 661 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MADILL | 12537 HIGHWAY 199 | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 7202 | 2379 | 661 | 0 | 0.00076838 | 0 | 1 | 0 | Feeder | GLASSES_1024 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003373 | PD-01102020-00415 | ARKANSAS | POTEAU | 3505:POTEAU | POTEAU_522 | 350522 | 2020-01-10 13:44 | 2020-01-10 14:35 | 50.63 | 1 | 1 | 18.6058 | 12 | POOR CONNECTION | 50 | CONNECTOR | POTEAU | 512 ROANOKE | CMI_NORMAL | NO | NO | NO | 860257 | 82148 | 13467 | 2296 | 358 | 2.1628e-05 | 1.1624e-06 | 18.6058 | 1 | 310 | Customer | 494 | Load | Tran1phOH | TOBY C MEAD | 918-658-5596 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003374 | PD-01102020-00492 | NORTHWEST | ENID | 4135:SO 4TH ST | SO_4TH_ST_3524 | 413524 | 2020-01-10 13:46 | 2020-01-10 16:58 | 192.43 | 2 | 2 | 384.8667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ENID | 1405 INDIAN DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 53499 | 37566 | 3094 | 1611 | 0.00044739 | 2.3249e-06 | 192.4333 | 1 | 310 | Secondary | 6939 | Load | Tran1phOH | JOSH SHEPHERD | 580-583-5632 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003378 |  | METRO NORTH | GUTHRIE | 8810:ORLANDO | ORLANDO 03 | 881003 | 2020-01-10 13:49 | 2020-01-10 21:46 | 477.3 | 1 | 0 | 465.2167 | 17 | TRANSMISSION OPERATION | 56 | SCADA - LOCKOUT | ORLANDO | FROM I-35 AND HWY 81, GO 3 MILES WEST ON HWY 51, 2.5 MILES NORTH ON HWY 77 TO MAIN ST, GO 1/2 MILE EAST PAST HIGH SCHOOL. SUB ON EAST SIDE | CMI_NORMAL | NO | NO | NO | 860257 | 168032 | 19801 | 3 | 2 | 0.00054079 | 1.1624e-06 | 465.2167 | 1 | 0 | Feeder | ORLANDO 03 | Breaker | SubBreaker | [7 empty] | Equipment | N | TRANSMISSION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003379 |  | METRO NORTH | GUTHRIE | 8810:ORLANDO | ORLANDO 01 | 881001 | 2020-01-10 13:49 | 2020-01-10 21:45 | 476.33 | 1 | 0 | 465.05 | 17 | TRANSMISSION OPERATION | 56 | SCADA - LOCKOUT | ORLANDO | FROM I-35 AND HWY 81, GO 3 MILES WEST ON HWY 51, 2.5 MILES NORTH ON HWY 77 TO MAIN ST, GO 1/2 MILE EAST PAST HIGH SCHOOL. SUB ON EAST SIDE | CMI_NORMAL | NO | NO | NO | 860257 | 168032 | 19801 | 3 | 1 | 0.00054059 | 1.1624e-06 | 465.05 | 1 | 0 | Feeder | ORLANDO 01 | Breaker | SubBreaker | [7 empty] | Equipment | N | TRANSMISSION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003380 |  | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1722 | 861722 | 2020-01-10 13:51 | 2020-01-10 14:29 | 38.25 | 10 | 3 | 345.6667 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 4522 SUNNYVIEW DR | CMI_PLANNED | YES | NO | NO | 860257 | 114304 | 71179 | 6938 | 1787 | 0.00040182 | 1.1624e-05 | 34.5667 | 1 | 310 | Load | 52740 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003382 | PD-01102020-00421 | METRO SOUTH | SOUTH | 8709:LITTLE R LAKE | LITTLE_RIVER_L_921 | 870921 | 2020-01-10 13:52 | 2020-01-10 14:16 | 23.57 | 1 | 1 | 23.5667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | NORMAN | 8908 BROWNFIELD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 158988 | 56911 | 672 | 672 | 2.7395e-05 | 1.1624e-06 | 23.5667 | 1 | 310 | Load | 54200 | Load | Tran1phOH | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003407 | PD-01102020-00453 | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-01-10 14:09 | 2020-01-10 16:34 | 145.45 | 15 | 8 | 1746.75 | 25 | LIGHTNING | 47 | ARRESTOR OH | MILBURN | E OF MAIN ON GRAND | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 7202 | 2191 | 1673 | 0.0020305 | 1.7437e-05 | 116.45 | 1 | 310 | Mainline | 4868 | Fuse | FuseOH | DAVID TAYLOR | 580-574-4517 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003403 |  | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-01-10 14:16 | 2020-01-10 14:16 | 0 | 1000 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 3623 RED CEDAR RD | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 23570 | 2205 | 1000 | 0 | 0.0011624 | 0 | 1 | 0 | Feeder | DRIPPING_SPRI_1129 | Recloser | 0 | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003410 | PD-01102020-00456 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2024 | 822024 | 2020-01-10 14:23 | 2020-01-10 18:31 | 247.57 | 8 | 11 | 1865.8667 | 22 | WIND | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2741 NW.25 | CMI_NORMAL | NO | NO | NO | 860257 | 168032 | 148231 | 6035 | 1775 | 0.002169 | 9.2995e-06 | 233.2333 | 1 | 310 | Load | 12125 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003408 |  | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-10 14:28 | 2020-01-10 14:37 | 8.8 | 9 | 0 | 78.1869 | 1 | CANCELLED | 57 | CANCELLED | 0 | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 128607 | 115878 | 18216 | 4429 | 9.0888e-05 | 1.0462e-05 | 8.6874 | 1 | 0 | Mainline | 73440-1 | Switch | SwitchDefault | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003415 | PD-01102020-00441 | NORTHEAST | MUSKOGEE | 3111:FIVE TRIBES | FIVE_TRIBES_1129 | 311129 | 2020-01-10 14:29 | 2020-01-10 16:45 | 136.37 | 40 | 20 | 5357.3333 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | MUSKOGEE | OLD PRAIRIE VIEW SCH. | CMI_NORMAL | NO | NO | NO | 860257 | 73936 | 33220 | 1680 | 864 | 0.0062276 | 4.6498e-05 | 133.9333 | 1 | 310 | Mainline | 26696 | Fuse | FuseOH | STEVE K HIGHFILL | 918-869-2785 | [5 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | #N/A
J2001.003409 |  | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1421 | 311421 | 2020-01-10 14:29 | 2020-01-10 14:29 | 0.22 | 1101 | 0 | 238.55 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MUSKOGEE | 2612 TENNYSON | CMI_MOMENTARY | YES | NO | NO | 860257 | 73936 | 33220 | 4561 | 1101 | 0.0002773 | 0.0012799 | 0.21667 | 1 | 0 | Feeder | TENNYSON_1421 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003412 |  | NORTHEAST | MUSKOGEE | 3137:AGENCY | AGENCY_3769 | 313769 | 2020-01-10 14:31 | 2020-01-10 14:32 | 0.1 | 136 | 0 | 9.0667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MUSKOGEE | 4224 PALM AVE | CMI_MOMENTARY | YES | NO | NO | 860257 | 73936 | 33220 | 136 | 136 | 1.0539e-05 | 0.00015809 | 0.066667 | 1 | 0 | Feeder | AGENCY_3769 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-10 | 2020 |  | #N/A
J2001.003418 | PD-01102020-00464 | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_521 | 890521 | 2020-01-10 14:34 | 2020-01-10 17:09 | 155.25 | 1 | 1 | 155.25 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | EL RENO | 219 S MACOMB | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 128607 | 12729 | 6934 | 2210 | 0.00018047 | 1.1624e-06 | 155.25 | 1 | 310 | Customer | 50871 | Load | Tran1phOH | BRANDON H SMITH | 405-371-4294 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003419 | PD-01102020-00461 | NORTHEAST | MUSKOGEE | 3111:FIVE TRIBES | FIVE_TRIBES_1129 | 311129 | 2020-01-10 14:35 | 2020-01-10 16:48 | 133.05 | 1 | 1 | 127.6167 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | MUSKOGEE | EAST OF DAVIS FIELD | CMI_NORMAL | NO | NO | NO | 860257 | 73936 | 33220 | 1680 | 864 | 0.00014835 | 1.1624e-06 | 127.6167 | 1 | 310 | Load | 15487 | Load | TranOpenDelta | STEVE K HIGHFILL | 918-869-2785 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | #N/A
J2001.003423 | PD-01102020-00459 | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4529 | 824529 | 2020-01-10 14:39 | 2020-01-10 17:12 | 153.45 | 3 | 3 | 460.35 | 22 | WIND | 17 | JUMPER | OKLAHOMA CITY | 8031 W. Reno Ave. | CMI_NORMAL | NO | NO | NO | 860257 | 128607 | 115878 | 3405 | 257 | 0.00053513 | 3.4873e-06 | 153.45 | 1 | 320 | Secondary | 311146 | Load | Tran3phPadWye | JESSE PHILLER | 405-512-8086 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003422 |  | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1023 | 311023 | 2020-01-10 14:39 | 2020-01-10 14:39 | 0 | 273 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MUSKOGEE | 1541 COUNTRY CLUB PLACE | CMI_MOMENTARY | YES | NO | NO | 860257 | 73936 | 33220 | 2900 | 114 | 0 | 0.00031735 | 0 | 1 | 0 | Feeder | RIVERSIDE_1023 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003448 | PD-01102020-00471 | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1024 | 311024 | 2020-01-10 14:42 | 2020-01-10 20:35 | 353.58 | 65 | 55 | 19995.0833 | 27 | TREE:NON PREVENTABLE | 34 | CONDUCTOR SECONDARY - OH | MUSKOGEE | VIRGINIA S OF HOUSTON | CMI_NORMAL | NO | NO | NO | 860257 | 73936 | 33220 | 2900 | 1391 | 0.023243 | 7.5559e-05 | 307.6167 | 1 | 310 | Tap | 2827 | Fuse | FuseOH | BRUCE A PAULUS | 479-220-7661 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003424 |  | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1024 | 311024 | 2020-01-10 14:42 | 2020-01-10 14:42 | 0.03 | 1390 | 0 | 46.3333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MUSKOGEE | 1541 COUNTRY CLUB PLACE | CMI_MOMENTARY | YES | NO | NO | 860257 | 73936 | 33220 | 2900 | 1391 | 5.386e-05 | 0.0016158 | 0.033333 | 1 | 0 | Feeder | RIVERSIDE_1024 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003425 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1023 | 541023 | 2020-01-10 14:42 | 2020-01-10 14:42 | 0 | 844 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MADILL | 12537 HIGHWAY 199 | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 7202 | 2379 | 844 | 0 | 0.0009811 | 0 | 1 | 0 | Feeder | GLASSES_1023 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003435 | PD-01102020-00465 | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2824 | 312824 | 2020-01-10 14:42 | 2020-01-10 17:27 | 164.72 | 8 | 7 | 1287.8667 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | MUSKOGEE | 906 FREDONIA | CMI_NORMAL | NO | NO | NO | 860257 | 73936 | 33220 | 5271 | 1609 | 0.0014971 | 9.2995e-06 | 160.9833 | 1 | 310 | Load | 4672 | Load | Tran1phOH | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003427 |  | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-01-10 14:44 | 2020-01-10 14:45 | 0.97 | 1000 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 3623 RED CEDAR RD | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 23570 | 2205 | 1000 | 0 | 0.0011624 | 0 | 1 | 0 | Feeder | DRIPPING_SPRI_1129 | Recloser | 0 | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003446 |  | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_721 | 590721 | 2020-01-10 14:46 | 2020-01-10 14:46 | 0 | 1 | 1 | 0 | 1 | CANCELLED | 57 | CANCELLED | MANNSVILLE | 14TH AVENUE-MANNSVILLE | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 7202 | 2191 | 504 | 0 | 1.1624e-06 | 0 | 1 | 308 | Load | 6133 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003449 |  | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_721 | 590721 | 2020-01-10 14:46 | 2020-01-10 14:46 | 0 | 1 | 1 | 0 | 1 | CANCELLED | 57 | CANCELLED | MANNSVILLE | .25SE MANNSVILLE(70/CHICKASAW) | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 7202 | 2191 | 504 | 0 | 1.1624e-06 | 0 | 1 | 308 | Load | 24293 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003429 |  | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_422 | 510422 | 2020-01-10 14:46 | 2020-01-10 14:46 | 0.07 | 1057 | 0 | 70.4667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 2510 SAM NOBLE PARKWAY | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 23570 | 2316 | 1057 | 8.1914e-05 | 0.0012287 | 0.066667 | 1 | 0 | Feeder | FOUNDATION_422 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003430 | PD-01102020-00503 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-01-10 14:47 | 2020-01-10 16:44 | 117.1 | 1 | 1 | 117.1 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | ARDMORE | HARVEY + SPRNGDL RD,.2E,150 N | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 23570 | 2205 | 1000 | 0.00013612 | 1.1624e-06 | 117.1 | 1 | 310 | Customer | 27768 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003434 | PD-01102020-00498 | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_422 | 510422 | 2020-01-10 14:47 | 2020-01-10 16:20 | 92.98 | 27 | 6 | 2360.25 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | ARDMORE | CHICKLAKE RD 1/2M N 70 | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 23570 | 2316 | 1057 | 0.0027437 | 3.1386e-05 | 87.4167 | 1 | 310 | Mainline | 4977 | Fuse | FuseOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003431 |  | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_422 | 510422 | 2020-01-10 14:47 | 2020-01-10 14:47 | 0.05 | 1057 | 0 | 52.85 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 2510 SAM NOBLE PARKWAY | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 23570 | 2316 | 1057 | 6.1435e-05 | 0.0012287 | 0.05 | 1 | 0 | Feeder | FOUNDATION_422 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003439 | PD-01102020-00460 | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2131 | 332131 | 2020-01-10 14:48 | 2020-01-11 00:53 | 605.4 | 7 | 9 | 4100.0167 | 27 | TREE:NON PREVENTABLE | 23 | FUSE - PRIMARY | OKAY | .5 MI W OF 3 RIVER CEM | CMI_NORMAL | NO | NO | NO | 860257 | 73936 | 33220 | 3331 | 1172 | 0.004766 | 8.1371e-06 | 585.7167 | 1 | 310 | Tap | 25926 | Fuse | FuseOH | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | #N/A
J2001.003432 | PD-01102020-00504 | SOUTHERN | HEALDTON | 5309:POOLEVILLE | POOLEVILLE_927 | 530927 | 2020-01-10 14:51 | 2020-01-10 16:29 | 98.07 | 1 | 1 | 98.0667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SPRINGER | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 0 | 0 | 0 | 0 | 0.000114 | 1.1624e-06 | 98.0667 | 1 | 310 | Customer |  | 0 | 0 | BLAKE TAYLOR | 580-504-2901 |  |  |  |  | 06/02/2020 note from burchamc. Reference J2001.003432 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003445 | PD-01102020-00469 | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_924 | 910924 | 2020-01-10 15:01 | 2020-01-10 15:40 | 39.32 | 1 | 1 | 39.3167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 2817 S.14 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 82148 | 61149 | 5008 | 1723 | 4.5703e-05 | 1.1624e-06 | 39.3167 | 1 | 310 | Customer | 4461 | Load | Tran1phOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | Ark - Series 3
J2001.003455 | PD-01102020-00562 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-01-10 15:08 | 2020-01-10 17:14 | 126.33 | 1 | 1 | 37.2667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ARDMORE | 1\4N + 1\4W OF CONCORD CHURCH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 77550 | 23570 | 2205 | 1000 | 4.332e-05 | 1.1624e-06 | 37.2667 | 1 | 310 | Customer | 25011 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003456 |  | NORTHEAST | MUSKOGEE | 3325:WELLS | WELLS_2549 | 332549 | 2020-01-10 15:08 | 2020-01-10 15:17 | 9.02 | 1 | 1 | 9.0167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | TEXANNA | RUNAWAY BAY LYNN LANE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 73936 | 33220 | 2373 | 1050 | 1.0481e-05 | 1.1624e-06 | 9.0167 | 1 | 310 | Customer | 16264 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003459 | PD-01102020-00481 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1421 | 311421 | 2020-01-10 15:10 | 2020-01-10 22:31 | 440.87 | 1 | 1 | 440.8667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MUSKOGEE | 4311 W OKLMULGEE AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 73936 | 33220 | 4561 | 1101 | 0.00051248 | 1.1624e-06 | 440.8667 | 1 | 310 | Customer | 322523 | Load | Tran1phPad | GARY MICHAEL KNUPP | 918-577-8564 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003458 | PD-01102020-00499 | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-01-10 15:10 | 2020-01-10 17:10 | 119.73 | 1 | 1 | 115.35 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | TISHOMINGO | 2823 E OK HWY 22 | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 7202 | 2191 | 1673 | 0.00013409 | 1.1624e-06 | 115.35 | 1 | 310 | Load | 10120 | Load | Tran1phOH | DAVID TAYLOR | 580-574-4517 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003461 |  | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1122 | 511122 | 2020-01-10 15:12 | 2020-01-10 15:12 | 0.03 | 1204 | 0 | 40.1333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 3623 RED CEDAR RD | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 23570 | 2205 | 1205 | 4.6653e-05 | 0.0013996 | 0.033333 | 1 | 0 | Feeder | DRIPPING_SPRI_1122 | Recloser | 0 | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003463 |  | SOUTHERN | ADA | 5808:HARDEN CITY | HARDEN_CITY_822 | 580822 | 2020-01-10 15:15 | 2020-01-10 15:15 | 0 | 1 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | HARDEN CITY | 25747 CR 3600 | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 11505 | 105 | 1 | 0 | 1.1624e-06 | 0 | 1 | 0 | Feeder | HARDEN_CITY_822 | Recloser | 0 | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003468 |  | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_524 | 510524 | 2020-01-10 15:16 | 2020-01-10 15:16 | 0 | 1434 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 228 C ST | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 23570 | 4769 | 1434 | 0 | 0.0016669 | 0 | 1 | 0 | Feeder | ARDMORE_524 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003469 | PD-01102020-00483 | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1373 | 831373 | 2020-01-10 15:19 | 2020-01-10 22:40 | 440.82 | 1 | 1 | 440.8167 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 4301 N Sara | CMI_NORMAL | NO | NO | NO | 860257 | 128607 | 115878 | 7870 | 4096 | 0.00051242 | 1.1624e-06 | 440.8167 | 1 | 310 | Customer | 403705 | Load | Tran3phPadWye | JESSE PHILLER | 405-512-8086 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003473 |  | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6223 | 866223 | 2020-01-10 15:20 | 2020-01-10 15:34 | 14.08 | 1 | 1 | 14.0833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 13237 SE 40 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 114304 | 71179 | 7201 | 2229 | 1.6371e-05 | 1.1624e-06 | 14.0833 | 1 | 310 | Load | 82491 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003470 | PD-01102020-00484 | ARKANSAS | FORT SMITH | 9512:ADABELL ROAD | ADABELL_ROAD_1221 | 951221 | 2020-01-10 15:20 | 2020-01-10 16:39 | 78.87 | 1 | 1 | 78.8667 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | VAN BUREN | 810 MAIN ST. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 82148 | 61149 | 3120 | 1094 | 9.1678e-05 | 1.1624e-06 | 78.8667 | 1 | 310 | Customer | 412667 | Load | Tran3phPadWye | MARK A. SAWYER | 479-462-4457 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | Ark - Series 1
J2001.003472 | PD-01102020-00506 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_524 | 510524 | 2020-01-10 15:22 | 2020-01-10 16:51 | 89.37 | 1 | 1 | 89.2667 | 25 | LIGHTNING | 47 | ARRESTOR OH | ARDMORE | CARTER AV 2S | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 23570 | 4769 | 1434 | 0.00010377 | 1.1624e-06 | 89.2667 | 1 | 310 | Load | 30464 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003474 | PD-01102020-00489 | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2721 | 872721 | 2020-01-10 15:23 | 2020-01-10 16:12 | 48.63 | 1 | 1 | 48.6333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | 405 MIMOSA DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 158988 | 56911 | 6457 | 934 | 5.6533e-05 | 1.1624e-06 | 48.6333 | 1 | 320 | Customer | 54039 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003475 |  | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6223 | 866223 | 2020-01-10 15:24 | 2020-01-10 15:33 | 8.33 | 1 | 1 | 8.3333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3901 Hazel Ave. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 114304 | 71179 | 7201 | 2229 | 9.687e-06 | 1.1624e-06 | 8.3333 | 1 | 310 | Load | 391088 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003480 | PD-01102020-00571 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_526 | 510526 | 2020-01-10 15:32 | 2020-01-10 17:42 | 130.22 | 1 | 1 | 130.2167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ARDMORE | 1610 MT-WASH RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 77550 | 23570 | 4769 | 1619 | 0.00015137 | 1.1624e-06 | 130.2167 | 1 | 310 | Customer | 2450 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003484 | PD-01102020-00497 | NORTHEAST | MUSKOGEE | 3314:PORUM | PORUM_1421 | 331421 | 2020-01-10 15:35 | 2020-01-10 21:02 | 326.72 | 6 | 3 | 1894.3 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | WARNER | 1MW HWY 2 & HWY 266 | CMI_NORMAL | NO | NO | NO | 860257 | 73936 | 33220 | 596 | 596 | 0.002202 | 6.9747e-06 | 315.7167 | 1 | 310 | Tap | 28285 | Fuse | FuseOH | JAMES MCDONALD | 405-361-7186 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003488 | PD-01102020-00501 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-01-10 15:40 | 2020-01-10 16:40 | 59.78 | 1 | 1 | 57.9167 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | ARDMORE | 2404 SPDLE RD | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 23570 | 2205 | 1000 | 6.7325e-05 | 1.1624e-06 | 57.9167 | 1 | 310 | Customer | 17965 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003487 |  | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_622 | 870622 | 2020-01-10 15:40 | 2020-01-10 15:49 | 8.12 | 1 | 1 | 8.1167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 2408 W.BROOKS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 158988 | 56911 | 7362 | 1260 | 9.4352e-06 | 1.1624e-06 | 8.1167 | 1 | 310 | Customer | 39025 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003486 |  | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1122 | 511122 | 2020-01-10 15:42 | 2020-01-10 15:42 | 0 | 1202 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 3623 RED CEDAR RD | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 23570 | 2205 | 1205 | 0 | 0.0013973 | 0 | 1 | 0 | Feeder | DRIPPING_SPRI_1122 | Recloser | 0 | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003490 |  | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-01-10 15:45 | 2020-01-10 15:45 | 0 | 997 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 3623 RED CEDAR RD | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 23570 | 2205 | 1000 | 0 | 0.001159 | 0 | 1 | 0 | Feeder | DRIPPING_SPRI_1129 | Recloser | 0 | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003491 | PD-01102020-00575 | SOUTHERN | MADILL | 5408:CANEY CREEK | CANEY_CREEK_831 | 540831 | 2020-01-10 15:46 | 2020-01-10 19:22 | 216.12 | 1 | 1 | 214.1667 | 25 | LIGHTNING | 47 | ARRESTOR OH | KINGSTON | ALLEY W MAYTUBBY S 4TH-KINGSTO | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 7202 | 1053 | 629 | 0.00024896 | 1.1624e-06 | 214.1667 | 1 | 310 | Customer | 11084 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003521 | PD-01102020-00511 | NORTHEAST | MUSKOGEE | 3111:FIVE TRIBES | FIVE_TRIBES_1129 | 311129 | 2020-01-10 15:46 | 2020-01-10 16:50 | 63.57 | 1 | 1 | 56.15 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | MUSKOGEE | EAST OF DAVIS FIELD | CMI_NORMAL | NO | NO | NO | 860257 | 73936 | 33220 | 1680 | 864 | 6.5271e-05 | 1.1624e-06 | 56.15 | 1 | 310 | Load | 15486 | Load | Tran1phOH | STEVE K HIGHFILL | 918-869-2785 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | #N/A
J2001.003529 | PD-01102020-00509 | NORTHEAST | MUSKOGEE | 3325:WELLS | WELLS_2542 | 332542 | 2020-01-10 15:50 | 2020-01-10 18:16 | 145.95 | 1 | 1 | 145.95 | 25 | LIGHTNING | 2 | TRANSFORMER OH | EUFAULA | 416 HARRISON EUFAULA,OK | CMI_NORMAL | NO | NO | NO | 860257 | 73936 | 33220 | 2373 | 1319 | 0.00016966 | 1.1624e-06 | 145.95 | 1 | 310 | Customer | 9941 | Load | Tran1phOH | [7 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003532 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2126 | 822126 | 2020-01-10 15:53 | 2020-01-10 15:53 | 0 | 672 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 4431 NW 10TH ST | CMI_MOMENTARY | YES | NO | NO | 860257 | 168032 | 148231 | 9235 | 672 | 0 | 0.00078116 | 0 | 1 | 0 | Feeder | MERIDIAN_2126 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003535 | PD-01102020-00510 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_771 | 870771 | 2020-01-10 15:54 | 2020-01-10 17:53 | 118.57 | 1 | 1 | 105.0333 | 3 | DAMAGED BY PUBLIC | 30 | CONDUCTOR SERVICE - UG | NOBLE | 303 CRESTDALE LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 158988 | 56911 | 11830 | 1814 | 0.0001221 | 1.1624e-06 | 105.0333 | 1 | 310 | Customer | 64893 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003540 | PD-01102020-00529 | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_721 | 590721 | 2020-01-10 16:01 | 2020-01-10 18:24 | 142.9 | 1 | 1 | 138.2167 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | MANNSVILLE | SHERRY LAKE ADDN-MANNSVILLE | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 7202 | 2191 | 504 | 0.00016067 | 1.1624e-06 | 138.2167 | 1 | 310 | Load | 16102 | Load | Tran1phPad | JOE LOFTIS | 918-884-5349 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003541 | PD-01102020-00519 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6324 | 816324 | 2020-01-10 16:04 | 2020-01-10 16:27 | 23.37 | 1 | 1 | 23.3667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MOORE | 1313 NAIL PARKWAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 158988 | 102077 | 11814 | 2048 | 2.7162e-05 | 1.1624e-06 | 23.3667 | 1 | 310 | Customer | 36833 | Load | Tran1phOH | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003544 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7422 | 847422 | 2020-01-10 16:04 | 2020-01-10 16:14 | 9.3 | 1 | 1 | 9.3 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 709 NE.24 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 168032 | 148231 | 6152 | 1211 | 1.0811e-05 | 1.1624e-06 | 9.3 | 1 | 310 | Customer | 6936 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003632 |  | METRO EAST | CHANDLER | 7119:WARWICK | WARWICK_1942 | 711942 | 2020-01-10 16:08 | 2020-01-10 17:56 | 107.58 | 1 | 2 | 107.5833 | 1 | CANCELLED | 57 | CANCELLED | CARNEY | 807 S BRADLEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 114304 | 7454 | 2415 | 956 | 0.00012506 | 1.1624e-06 | 107.5833 | 1 | 310 | Load | 355559 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003555 | PD-01102020-00540 | METRO EAST | CHANDLER | 7119:WARWICK | WARWICK_1942 | 711942 | 2020-01-10 16:08 | 2020-01-10 17:40 | 92.07 | 1 | 2 | 86.95 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | CARNEY | 807 S BRADLEY | CMI_NORMAL | NO | NO | NO | 860257 | 114304 | 7454 | 2415 | 956 | 0.00010107 | 1.1624e-06 | 86.95 | 1 | 310 | Load | 355559 | Load | Tran1phOH | SCOTT C PERRY | 405-258-6044 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003549 | PD-01102020-00530 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2126 | 822126 | 2020-01-10 16:14 | 2020-01-10 20:34 | 260.35 | 1 | 2 | 60.7667 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | 3839 W.RENO | CMI_NORMAL | NO | NO | NO | 860257 | 168032 | 148231 | 9235 | 672 | 7.0638e-05 | 1.1624e-06 | 60.7667 | 1 | 310 | Customer | 56630 | Load | Tran3phPadWye | TOMMY D ROBERTSON | 405-696-6476 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003550 | PD-01102020-00527 | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1522 | 921522 | 2020-01-10 16:14 | 2020-01-10 16:46 | 32.2 | 1 | 1 | 11.5742 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | CHARLESTON | BLOOMER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 82148 | 61149 | 959 | 469 | 1.3454e-05 | 1.1624e-06 | 11.5742 | 1 | 310 | Customer | 7261 | Load | Tran1phOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 34.5/19.9kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003551 |  | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1024 | 311024 | 2020-01-10 16:18 | 2020-01-10 16:18 | 0 | 1325 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MUSKOGEE | 1541 COUNTRY CLUB PLACE | CMI_MOMENTARY | YES | NO | NO | 860257 | 73936 | 33220 | 2900 | 1391 | 0 | 0.0015402 | 0 | 1 | 0 | Feeder | RIVERSIDE_1024 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003556 | PD-01102020-00541 | NORTHEAST | MUSKOGEE | 3325:WELLS | WELLS_2542 | 332542 | 2020-01-10 16:20 | 2020-01-11 01:25 | 544.82 | 1 | 1 | 544.8167 | 25 | LIGHTNING | 2 | TRANSFORMER OH | EUFAULA | EUFAULA COVE MARINA | CMI_NORMAL | NO | NO | NO | 860257 | 73936 | 33220 | 2373 | 1319 | 0.00063332 | 1.1624e-06 | 544.8167 | 1 | 310 | Customer | 244597 | Load | Tran3phWye | BRUCE A PAULUS | 479-220-7661 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003557 | PD-01102020-00565 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1122 | 511122 | 2020-01-10 16:23 | 2020-01-10 17:20 | 57.43 | 1 | 1 | 57.4333 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | DICKSON | .2E GENE AUTRY RD .2N .1E | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 23570 | 2205 | 1205 | 6.6763e-05 | 1.1624e-06 | 57.4333 | 1 | 310 | Customer | 29623 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003558 | PD-01102020-00552 | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1022 | 541022 | 2020-01-10 16:23 | 2020-01-10 19:39 | 196.32 | 1 | 1 | 196.3167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MADILL | 410 W.BURNEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 77550 | 7202 | 2379 | 873 | 0.00022821 | 1.1624e-06 | 196.3167 | 1 | 310 | Customer | 17933 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003560 | PD-01102020-00547 | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_424 | 580424 | 2020-01-10 16:28 | 2020-01-10 17:44 | 76.15 | 1 | 1 | 76.15 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | STONEWALL | % BOX 146 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 77550 | 11505 | 3411 | 436 | 8.852e-05 | 1.1624e-06 | 76.15 | 1 | 320 | Customer | 13419 | Load | Tran1phOH | JORDAN HERBERT-BLUE | 918-839-1152 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003566 | PD-01102020-00568 | METRO EAST | SEMINOLE | 7512:CROMWELL | CROMWELL 47 | 751247 | 2020-01-10 16:40 | 2020-01-10 21:37 | 296.62 | 2 | 2 | 577.2333 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | WEWOKA | 1MS I-40 3/4ME HWY 56 | CMI_NORMAL | NO | NO | NO | 860257 | 114304 | 13588 | 308 | 308 | 0.000671 | 2.3249e-06 | 288.6167 | 1 | 310 | Tap | 7479 | Fuse | FuseOH | BRADY A HUFF | 405-519-0701 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003565 | PD-01102020-00581 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2122 | 822122 | 2020-01-10 16:44 | 2020-01-10 18:23 | 99 | 11 | 15 | 1068.65 | 22 | WIND | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 3841 NW.22 | CMI_NORMAL | NO | NO | NO | 860257 | 168032 | 148231 | 9235 | 2014 | 0.0012422 | 1.2787e-05 | 97.15 | 1 | 310 | Load | 11879 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003574 | PD-01102020-00579 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7021 | 817021 | 2020-01-10 16:45 | 2020-01-10 21:37 | 291.68 | 89 | 53 | 25884.1667 | 22 | WIND | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | N/SW.62 + WALKER | CMI_NORMAL | NO | NO | NO | 860257 | 158988 | 102077 | 9939 | 1789 | 0.030089 | 0.00010346 | 290.8333 | 1 | 310 | Mainline | 17597 | Fuse | FuseOH | JUSTIN C TAYLOR | 405-534-1006 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003571 | PD-01102020-00577 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5029 | 865029 | 2020-01-10 16:56 | 2020-01-10 21:35 | 278.97 | 1 | 2 | 64.8 | 4 | DETERIORATION | 50 | CONNECTOR | MIDWEST CITY | 104 E.MYRTLE DR | CMI_NORMAL | NO | NO | NO | 860257 | 114304 | 71179 | 8623 | 1735 | 7.5326e-05 | 1.1624e-06 | 64.8 | 1 | 310 | Customer | 16058 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003577 |  | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_621 | 550621 | 2020-01-10 17:03 | 2020-01-10 17:03 | 0.02 | 900 | 0 | 15 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | DURANT | 1400 BRYAN DR | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 15475 | 6732 | 899 | 1.7437e-05 | 0.0010462 | 0.016667 | 1 | 0 | Feeder | BODLE ST_621 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003578 |  | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_863 | 550863 | 2020-01-10 17:03 | 2020-01-10 17:03 | 0 | 622 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | BROWN | WEST OF N3670 RD ON E2020RD | CMI_MOMENTARY | YES | NO | NO | 860257 | 77550 | 15475 | 1103 | 622 | 0 | 0.00072304 | 0 | 1 | 0 | Feeder | BROW OGE_863 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003585 | PD-01102020-00588 | METRO EAST | SEMINOLE | 7312:JUMPER CREEK | JUMPER_CREEK_1227 | 731227 | 2020-01-10 17:07 | 2020-01-10 22:33 | 325.75 | 885 | 191 | 93958.9 | 25 | LIGHTNING | 37 | CONDUCTOR PRIMARY - OH | KONAWA | 0 | CMI_NORMAL | NO | NO | NO | 860257 | 114304 | 13588 | 1216 | 885 | 0.10922 | 0.0010288 | 106.1682 | 1 | 310 | Mainline | 731227 | Switch | 0 | Circuit Operation | [6 empty] | Weather | N | SUBSTATION | 69kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003583 | PD-01102020-00590 | NORTHWEST | ENID | 4219:BUNCH CREEK | BUNCH CREEK 41 | 421941 | 2020-01-10 17:07 | 2020-01-10 19:57 | 169.67 | 4 | 4 | 654.4333 | 11 | OVERLOAD | 2 | TRANSFORMER OH | GARBER | 607 ANDY DR | CMI_NORMAL | NO | NO | NO | 860257 | 53499 | 37566 | 911 | 911 | 0.00076074 | 4.6498e-06 | 163.6083 | 1 | 310 | Load | 1771 | Load | Tran1phOH | JOSH SHEPHERD | 580-583-5632 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003604 | PD-01102020-00596 | METRO WEST | WEST | 8335:BETHANY | BETHANY_3526 | 833526 | 2020-01-10 17:12 | 2020-01-10 23:47 | 395 | 9 | 11 | 3339.75 | 4 | DETERIORATION | 39 | BUSHING | BETHANY | 6503.5 NW.32 | CMI_NORMAL | NO | NO | NO | 860257 | 128607 | 115878 | 7861 | 2061 | 0.0038823 | 1.0462e-05 | 371.0833 | 1 | 310 | Load | 24296 | Load | Tran1phOH | DENNY J MORGAN | 405-501-1556 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003584 |  | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_721 | 590721 | 2020-01-10 17:13 | 2020-01-10 19:36 | 142.87 | 1 | 1 | 66.6167 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | MANNSVILLE | SHERRY LAKE ADDN-MANNSVILLE | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 7202 | 2191 | 504 | 7.7438e-05 | 1.1624e-06 | 66.6167 | 1 | 310 | Customer | 15636 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003586 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2126 | 822126 | 2020-01-10 17:14 | 2020-01-10 17:14 | 0 | 671 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 4431 NW 10TH ST | CMI_MOMENTARY | YES | NO | NO | 860257 | 168032 | 148231 | 9235 | 672 | 0 | 0.00078 | 0 | 1 | 0 | Feeder | MERIDIAN_2126 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003589 | PD-01102020-00585 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-01-10 17:15 | 2020-01-10 17:41 | 26.25 | 2 | 2 | 47.75 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | ARDMORE | HARVEY + SPRNGDL RD,.2E,150 N | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 23570 | 2205 | 1000 | 5.5507e-05 | 2.3249e-06 | 23.875 | 1 | 310 | Load | 27768 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003590 | PD-01102020-00586 | METRO WEST | WEST | 8158:SARA | SARA_5862 | 815862 | 2020-01-10 17:16 | 2020-01-10 20:16 | 180.4 | 1 | 1 | 180.4 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1/I0 MS-74TH + WS-MACAUTHUR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 128607 | 115878 | 18216 | 3596 | 0.0002097 | 1.1624e-06 | 180.4 | 1 | 311 | Load | 79032 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003595 | PD-01102020-00587 | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_422 | 510422 | 2020-01-10 17:19 | 2020-01-10 18:05 | 46.4 | 1 | 1 | 41.7333 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | ARDMORE | HWY 70 1.9 E SS | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 23570 | 2316 | 1057 | 4.8513e-05 | 1.1624e-06 | 41.7333 | 1 | 310 | Customer | 10986 | Load | Tran1phPad | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003625 | PD-01102020-00598 | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_649 | 890649 | 2020-01-10 17:27 | 2020-01-10 22:28 | 301.17 | 31 | 27 | 14773.05 | 5 | ELECTRICAL TRACKING | 27 | CUTOUT | OAKWOOD | N MAIN + W MISSOURI | CMI_NORMAL | NO | NO | NO | 860257 | 128607 | 12729 | 1364 | 278 | 0.017173 | 3.6036e-05 | 476.55 | 1 | 310 | Mainline | 13627 | Fuse | FuseOH | JOSH SHEPHERD | 580-583-5632 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003619 | PD-01102020-00594 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-01-10 17:31 | 2020-01-10 18:40 | 69.33 | 9 | 10 | 596.1 | 22 | WIND | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 222 NW.30 | CMI_NORMAL | NO | NO | NO | 860257 | 168032 | 148231 | 11097 | 2335 | 0.00069293 | 1.0462e-05 | 66.2333 | 1 | 310 | Load | 7399 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003616 | PD-01102020-00593 | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2131 | 332131 | 2020-01-10 17:31 | 2020-01-10 21:31 | 239.48 | 1 | 1 | 213.8667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | FORT GIBSON | % ROUTE 1 | CMI_NORMAL | NO | NO | NO | 860257 | 73936 | 33220 | 3331 | 1172 | 0.00024861 | 1.1624e-06 | 213.8667 | 1 | 310 | Load | 5708 | Load | Tran1phOH | [7 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | #N/A
J2001.003622 | PD-01102020-00597 | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_721 | 590721 | 2020-01-10 17:40 | 2020-01-10 19:27 | 107.43 | 1 | 1 | 102.8667 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | MANNSVILLE | JESTER-RUSSETT | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 7202 | 2191 | 504 | 0.00011958 | 1.1624e-06 | 102.8667 | 1 | 310 | Load | 3760 | Load | Tran1phOH | ROBERT J BEARDSLEE | 580-618-2506 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003630 | PD-01102020-00600 | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-01-10 17:52 | 2020-01-10 22:16 | 263.95 | 24 | 6 | 3670.4 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | LEONARD | 161 E AV,1/2 S OF 171S | CMI_NORMAL | NO | NO | NO | 860257 | 73936 | 40716 | 2743 | 1439 | 0.0042666 | 2.7899e-05 | 152.9333 | 1 | 310 | Mainline | 60719 | Fuse | FuseOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003638 | PD-01102020-00601 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5125 | 815125 | 2020-01-10 17:54 | 2020-01-10 22:46 | 291.9 | 67 | 59 | 19255.8 | 22 | WIND | 17 | JUMPER | OKLAHOMA CITY | N:PENN./72ND | CMI_NORMAL | NO | NO | NO | 860257 | 158988 | 102077 | 13935 | 1432 | 0.022384 | 7.7884e-05 | 287.4 | 1 | 310 | Mainline | 12184 | Fuse | FuseOH | DENNY J MORGAN | 405-501-1556 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003633 | PD-01102020-00602 | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_631 | 730631 | 2020-01-10 17:55 | 2020-01-10 20:34 | 158.78 | 1 | 1 | 158.7833 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | SEMINOLE | 1.5MN 9 ON HARVY RD | CMI_NORMAL | NO | NO | NO | 860257 | 114304 | 13588 | 4057 | 665 | 0.00018458 | 1.1624e-06 | 158.7833 | 1 | 310 | Load | 90241 | Load | 0 | BRADY A HUFF | 405-519-0701 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003637 | PD-01102020-00603 | SOUTHERN | PAULS VALLEY | 5619:RUSH CREEK | RUSH_CREEK_1922 | 561922 | 2020-01-10 17:56 | 2020-01-10 18:46 | 49.63 | 1 | 1 | 47.15 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | PAULS VALLEY | PAULS VALLEY ST SCH | CMI_NORMAL | NO | NO | NO | 860257 | 77550 | 6202 | 2073 | 1193 | 5.4809e-05 | 1.1624e-06 | 47.15 | 1 | 310 | Load | 90164 | Load | 0 | CHAD A DOTSON | 405-488-5658 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003648 | PD-01102020-00605 | NORTHEAST | MUSKOGEE | 3325:WELLS | WELLS_2549 | 332549 | 2020-01-10 18:02 | 2020-01-10 23:45 | 342.53 | 1 | 1 | 331.4333 | 25 | LIGHTNING | 2 | TRANSFORMER OH | CHECOTAH | 1N OF WATER TOWER ON OLD69 | CMI_NORMAL | NO | NO | NO | 860257 | 73957 | 33231 | 2373 | 1050 | 0.00038527 | 1.1624e-06 | 331.4333 | 1 | 310 | Customer | 179937 | Load | Tran1phOH | BRUCE A PAULUS | 479-220-7661 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003651 | PD-01102020-00604 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1122 | 511122 | 2020-01-10 18:04 | 2020-01-10 18:29 | 24.63 | 1 | 1 | 21.1167 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | DICKSON | 199 + GANT RD,1.3N,ES | CMI_NORMAL | NO | NO | NO | 860257 | 77559 | 23571 | 2205 | 1205 | 2.4547e-05 | 1.1624e-06 | 21.1167 | 1 | 310 | Load | 27644 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003658 |  | SOUTHERN | SULPHUR | 5705:SULPHUR | SULPHUR_531 | 570531 | 2020-01-10 18:14 | 2020-01-10 22:55 | 281.47 | 602 | 0 | 281.2292 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | SULPHUR | 300 W OKLAHOMA ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 77559 | 6809 | 3630 | 602 | 0.00032691 | 0.00069979 | 0.46716 | 1 | 0 | Feeder | SULPHUR_531 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003662 | PD-01102020-00608 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-01-10 18:18 | 2020-01-10 19:01 | 42.78 | 1 | 1 | 36.2167 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | ARDMORE | MOCKINGBIRD/EXPRESS RD .4E .2N | CMI_NORMAL | NO | NO | NO | 860257 | 77559 | 23571 | 2205 | 1000 | 4.21e-05 | 1.1624e-06 | 36.2167 | 1 | 310 | Customer | 320084 | Load | Tran1phPad | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003664 | PD-01102020-00610 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-01-10 18:19 | 2020-01-10 21:49 | 209.87 | 11 | 17 | 2222.3667 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 1431 NW 104TH ST | CMI_NORMAL | NO | NO | NO | 860257 | 168043 | 148241 | 8784 | 1951 | 0.0025834 | 1.2787e-05 | 202.0333 | 1 | 310 | Load | 19173 | Load | Tran1phOH | TOMMY D ROBERTSON | 405-696-6476 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003667 | PD-01102020-00609 | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_523 | 320523 | 2020-01-10 18:26 | 2020-01-11 04:00 | 574.35 | 4 | 17 | 161.6667 | 12 | POOR CONNECTION | 50 | CONNECTOR | SAPULPA | 121 E.GOODYKOONTZ | CMI_NORMAL | NO | NO | NO | 860257 | 73957 | 40726 | 3836 | 1715 | 0.00018793 | 4.6498e-06 | 40.4167 | 1 | 310 | Secondary | 44489 | Load | Tran1phOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003670 | PD-01102020-00611 | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_523 | 320523 | 2020-01-10 18:28 | 2020-01-11 08:40 | 852.28 | 11 | 16 | 9476.3167 | 5 | ELECTRICAL TRACKING | 27 | CUTOUT | SAPULPA | 66 W.MOCKINGBIRD | CMI_NORMAL | NO | NO | NO | 860257 | 73957 | 40726 | 3836 | 1715 | 0.011016 | 1.2787e-05 | 861.4833 | 1 | 310 | Load | 45045 | Load | Tran1phOH | NORRIS L CARRIER | 918-740-9618 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003673 |  | METRO EAST | SHAWNEE | 7407:REMINGTON | REMINGTON 22 | 740722 | 2020-01-10 18:32 | 2020-01-10 18:44 | 11.38 | 1 | 1 | 11.3833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SHAWNEE | 5 OAK-HILL RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 114316 | 22090 | 3662 | 1645 | 1.3232e-05 | 1.1624e-06 | 11.3833 | 1 | 310 | Customer | 10370 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003674 |  | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-01-10 18:39 | 2020-01-10 18:39 | 0.03 | 999 | 0 | 33.3 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 3623 RED CEDAR RD | CMI_MOMENTARY | YES | NO | NO | 860257 | 77559 | 23571 | 2205 | 1000 | 3.8709e-05 | 0.0011613 | 0.033333 | 1 | 0 | Feeder | DRIPPING_SPRI_1129 | Recloser | 0 | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003677 |  | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1523 | 811523 | 2020-01-10 18:44 | 2020-01-10 18:44 | 0 | 148 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 2200 SW 15TH ST | CMI_MOMENTARY | YES | NO | NO | 860257 | 158998 | 102083 | 6054 | 804 | 0 | 0.00017204 | 0 | 1 | 0 | Mainline | 338460 | Recloser | Rec3phElectronic | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003678 |  | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1523 | 811523 | 2020-01-10 18:44 | 2020-01-10 18:44 | 0 | 18 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 2200 SW 15TH ST | CMI_MOMENTARY | YES | NO | NO | 860257 | 158998 | 102083 | 6054 | 804 | 0 | 2.0924e-05 | 0 | 1 | 0 | Mainline | 338460 | Recloser | Rec3phElectronic | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003679 |  | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1523 | 811523 | 2020-01-10 18:44 | 2020-01-10 18:44 | 0 | 6 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 2200 SW 15TH ST | CMI_MOMENTARY | YES | NO | NO | 860257 | 158998 | 102083 | 6054 | 804 | 0 | 6.9747e-06 | 0 | 1 | 0 | Mainline | 338460 | Recloser | Rec3phElectronic | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003682 |  | ARKANSAS | POTEAU | 3516:TARBY | TARBY_1625 | 351625 | 2020-01-10 18:55 | 2020-01-10 18:55 | 0 | 1194 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | POTEAU | 82845 N 470TH ST | CMI_MOMENTARY | YES | NO | NO | 860257 | 82157 | 13469 | 1674 | 1194 | 0 | 0.001388 | 0 | 1 | 0 | Feeder | TARBY_1625 | Breaker | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-10 | 2020 |  | #N/A
J2001.003684 | PD-01102020-00612 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6333 | 816333 | 2020-01-10 18:55 | 2020-01-10 20:50 | 114.8 | 1 | 1 | 66.0667 | 12 | POOR CONNECTION | 50 | CONNECTOR | MOORE | 915 W.MAIN | CMI_NORMAL | NO | NO | NO | 860257 | 158998 | 102083 | 11814 | 1229 | 7.6799e-05 | 1.1624e-06 | 66.0667 | 1 | 320 | Customer | 20800 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003691 | PD-01102020-00615 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4124 | 814124 | 2020-01-10 19:03 | 2020-01-10 22:15 | 191.78 | 30 | 25 | 5720 | 4 | DETERIORATION | 13 | PIN | OKLAHOMA CITY | W OF HARVEY N OF SW39 | CMI_NORMAL | NO | NO | NO | 860257 | 158998 | 102083 | 5802 | 2010 | 0.0066492 | 3.4873e-05 | 190.6667 | 1 | 310 | Tap | 17930 | Fuse | FuseOH | JUSTIN C TAYLOR | 405-534-1006 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003687 |  | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4124 | 814124 | 2020-01-10 19:03 | 2020-01-10 19:03 | 0 | 518 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | S WALKER AV & SW 46TH ST | CMI_MOMENTARY | YES | NO | NO | 860257 | 158998 | 102083 | 5802 | 2010 | 0 | 0.00060215 | 0 | 1 | 0 | Mainline | 337580 | Recloser | Rec3phElectronic | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003689 | PD-01102020-00616 | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_523 | 320523 | 2020-01-10 19:07 | 2020-01-11 08:40 | 813.15 | 1 | 2 | 822.3667 | 5 | ELECTRICAL TRACKING | 27 | CUTOUT | SAPULPA | 34 W.MOCKINGBIRD | CMI_NORMAL | NO | NO | NO | 860257 | 73957 | 40726 | 3836 | 1715 | 0.00095595 | 1.1624e-06 | 822.3667 | 1 | 310 | Customer | 42681 | Load | Tran1phOH | NORRIS L CARRIER | 918-740-9618 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003692 | PD-01102020-00614 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-01-10 19:10 | 2020-01-10 22:57 | 227.45 | 1 | 1 | 227.45 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 1915 NW.12 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860257 | 168043 | 148241 | 11099 | 2036 | 0.0002644 | 1.1624e-06 | 227.45 | 1 | 310 | Customer | 16192 | Load | TranOpenDelta | PETER BILICKI | 619-726-8332 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003702 | PD-01102020-00624 | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1024 | 541024 | 2020-01-10 19:23 | 2020-01-10 22:18 | 174.95 | 5 | 2 | 874.75 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | LITTLE CITY | HWY 199/ N 10TH 2.6 E .1N | CMI_NORMAL | NO | NO | NO | 860257 | 77559 | 7203 | 2379 | 661 | 0.0010168 | 5.8122e-06 | 174.95 | 1 | 310 | Mainline | 351454 | Fuse | FuseOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003695 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1024 | 541024 | 2020-01-10 19:23 | 2020-01-10 19:23 | 0.02 | 661 | 0 | 11.0167 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MADILL | 12537 HIGHWAY 199 | CMI_MOMENTARY | YES | NO | NO | 860257 | 77559 | 7203 | 2379 | 661 | 1.2806e-05 | 0.00076838 | 0.016667 | 1 | 0 | Feeder | GLASSES_1024 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003704 | PD-01102020-00619 | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_924 | 910924 | 2020-01-10 19:25 | 2020-01-10 23:00 | 214.78 | 3 | 5 | 636.15 | 25 | LIGHTNING | 47 | ARRESTOR OH | FORT SMITH | 2122 S.CARTHAGE | CMI_NORMAL | NO | NO | NO | 860257 | 82157 | 61153 | 5008 | 1723 | 0.00073949 | 3.4873e-06 | 212.05 | 1 | 310 | Secondary | 7524 | Load | Tran1phOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | Ark - Series 3
J2001.003701 | PD-01102020-00618 | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2521 | 912521 | 2020-01-10 19:26 | 2020-01-10 20:15 | 49.37 | 23 | 22 | 1060.6833 | 4 | DETERIORATION | 20 | FUSE BARREL | FORT SMITH | 5042 S.32 | CMI_NORMAL | NO | NO | NO | 860257 | 82157 | 61153 | 2732 | 410 | 0.001233 | 2.6736e-05 | 46.1167 | 1 | 310 | Load | 12855 | Load | Tran1phOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003698 | PD-01102020-00627 | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 21 | 570821 | 2020-01-10 19:27 | 2020-01-10 20:30 | 62.83 | 1 | 1 | 59.95 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | DAVIS | 2 MI E OF DAVIS.51/4 N SUNSHINE | CMI_NORMAL | NO | NO | NO | 860257 | 77559 | 6809 | 1857 | 902 | 6.9688e-05 | 1.1624e-06 | 59.95 | 1 | 310 | Load | 15250 | Load | Tran1phOH | CHAD A DOTSON | 405-488-5658 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003699 |  | METRO EAST | SHAWNEE | 7410:MAUD TAP | MAUD_TAP_1021 | 741021 | 2020-01-10 19:30 | 2020-01-10 19:30 | 0 | 759 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | 0 | 0 | CMI_MOMENTARY | YES | NO | NO | 860257 | 114316 | 22090 | 1015 | 759 | 0 | 0.00088229 | 0 | 1 | 0 | Feeder | MAUD_TAP_1021 | Breaker | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003706 | PD-01102020-00626 | SOUTHERN | MADILL | 5906:TISHOMINGO | TISHOMINGO_621 | 590621 | 2020-01-10 19:38 | 2020-01-10 21:22 | 104.18 | 1 | 1 | 29.5279 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | TISHOMINGO | OHIO + WILSON - TISH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 77559 | 7203 | 967 | 916 | 3.4325e-05 | 1.1624e-06 | 29.5279 | 1 | 310 | Customer | 11233 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003709 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6124 | 836124 | 2020-01-10 19:48 | 2020-01-10 20:54 | 66.28 | 12 | 13 | 795.4 | 22 | WIND | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 710 NW.23 | CMI_NORMAL | NO | NO | NO | 860257 | 168043 | 148241 | 11099 | 1765 | 0.00092461 | 1.3949e-05 | 66.2833 | 1 | 310 | Load | 1254 | Load | TranOH3phDelta | Ties | [6 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003711 | PD-01102020-00631 | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-01-10 19:51 | 2020-01-11 05:27 | 575.7 | 1 | 2 | 572.3667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | BRANCH | BRANCH AR 72928 | CMI_NORMAL | NO | NO | NO | 860257 | 82157 | 61153 | 959 | 490 | 0.00066534 | 1.1624e-06 | 572.3667 | 1 | 310 | Customer | 9355 | Load | Tran1phOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Weather | N | DISTRIBUTION | 34.5/19.9kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003712 |  | ARKANSAS | OZARK | 9412:ALTUS | ALTUS_1229 | 941229 | 2020-01-10 19:53 | 2020-01-10 19:53 | 0.33 | 865 | 0 | 14.4167 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OZARK | 6007 GRAVEL RD | CMI_MOMENTARY | YES | NO | NO | 860257 | 82157 | 7535 | 865 | 865 | 1.6759e-05 | 0.0010055 | 0.016667 | 1 | 0 | Feeder | ALTUS_1229 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003715 | PD-01102020-00630 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-01-10 19:53 | 2020-01-10 22:11 | 138.2 | 1 | 1 | 135.4167 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | ARDMORE | SPDL RD BEHIND GDNTTEMP | CMI_NORMAL | NO | NO | NO | 860257 | 77559 | 23571 | 2205 | 1000 | 0.00015741 | 1.1624e-06 | 135.4167 | 1 | 310 | Load | 20982 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003713 | PD-01102020-00629 | ARKANSAS | OZARK | 9413:RAZORBACK | RAZORBACK_1362 | 941362 | 2020-01-10 19:53 | 2020-01-11 02:36 | 402.87 | 396 | 130 | 38841.6 | 22 | WIND | 12 | POLE | SUBIACO | 2426 E STATE HWY 288 | CMI_NORMAL | NO | NO | NO | 860257 | 82157 | 7535 | 396 | 396 | 0.045151 | 0.00046033 | 98.0848 | 1 | 310 | Feeder | RAZORBCK_1362 | Recloser | SubRecloser | [7 empty] | Weather | N | SUBSTATION | 69kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003717 | PD-01102020-00632 | ARKANSAS | OZARK | 9412:ALTUS | ALTUS_1229 | 941229 | 2020-01-10 19:58 | 2020-01-10 22:41 | 163.13 | 6 | 4 | 951.1 | 5 | ELECTRICAL TRACKING | 23 | FUSE - PRIMARY | OZARK | LEISURE EST 2000 S 64 | CMI_NORMAL | NO | NO | NO | 860257 | 82157 | 7535 | 865 | 865 | 0.0011056 | 6.9747e-06 | 158.5167 | 1 | 310 | Tap | 6255 | Fuse | FuseOH | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003718 |  | ARKANSAS | OZARK | 9412:ALTUS | ALTUS_1229 | 941229 | 2020-01-10 19:59 | 2020-01-10 19:59 | 0 | 864 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OZARK | 6007 GRAVEL RD | CMI_MOMENTARY | YES | NO | NO | 860257 | 82157 | 7535 | 865 | 865 | 0 | 0.0010044 | 0 | 1 | 0 | Feeder | ALTUS_1229 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003729 | PD-01102020-00634 | METRO EAST | SHAWNEE | 7435:MISSION HILL | MISSION HILL 24 | 743524 | 2020-01-10 20:03 | 2020-01-10 21:53 | 110.02 | 1 | 2 | 49.0167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | TECUMSEH | 3MS .5E OF SHAWNEE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 114316 | 22090 | 948 | 948 | 5.6979e-05 | 1.1624e-06 | 49.0167 | 1 | 310 | Load | 8686 | Load | Tran1phOH | ADAM CLARK | 580-310-8924 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003724 | PD-01102020-00636 | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1024 | 541024 | 2020-01-10 20:07 | 2020-01-10 22:45 | 157.98 | 1 | 1 | 151 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MADILL | Hwy 199/ Whiskey Creek rd | CMI_NORMAL | NO | NO | NO | 860257 | 77559 | 7203 | 2379 | 661 | 0.00017553 | 1.1624e-06 | 151 | 1 | 310 | Load | 307730 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003734 | PD-01102020-00643 | ARKANSAS | OZARK | 9412:ALTUS | ALTUS_1229 | 941229 | 2020-01-10 20:22 | 2020-01-10 23:12 | 169.85 | 2 | 2 | 337.1667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | ALTUS | 6137 E HIGHWAY 64 | CMI_NORMAL | NO | NO | NO | 860257 | 82157 | 7535 | 865 | 865 | 0.00039194 | 2.3249e-06 | 168.5833 | 1 | 310 | Load | 214408 | Load | Tran1phOH | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003735 |  | METRO EAST | SHAWNEE | 7410:MAUD TAP | MAUD_TAP_1021 | 741021 | 2020-01-10 20:25 | 2020-01-10 20:25 | 0.02 | 759 | 0 | 12.65 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | 0 | 0 | CMI_MOMENTARY | YES | NO | NO | 860257 | 114316 | 22090 | 1015 | 759 | 1.4705e-05 | 0.00088229 | 0.016667 | 1 | 0 | Feeder | MAUD_TAP_1021 | Breaker | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003763 | PD-01102020-00662 | SOUTHERN | DURANT | 5511:BOKCHITO | BOKCHITO 21 | 551121 | 2020-01-10 20:45 | 2020-01-10 23:34 | 168.68 | 1 | 1 | 164.5667 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | BOKCHITO | 1BL W 70E ON TERRY BOKCHITO | CMI_NORMAL | NO | NO | NO | 860257 | 77559 | 15478 | 669 | 669 | 0.0001913 | 1.1624e-06 | 164.5667 | 1 | 310 | Load | 15165 | Load | TranOpenDelta | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Weather | N | DISTRIBUTION | 34.5/19.9kv | 2020-01-10 | 2020 |  | #N/A
J2001.003765 |  | METRO EAST | CHANDLER | 7117:JACKTOWN | JACKTOWN_1742 | 711742 | 2020-01-10 20:46 | 2020-01-10 21:01 | 15.53 | 1 | 1 | 15.5333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MEEKER | 2N HWY 62 + 1/10E HWY 18 SS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 114316 | 7457 | 1011 | 828 | 1.8057e-05 | 1.1624e-06 | 15.5333 | 1 | 310 | Load | 21432 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003764 |  | METRO EAST | SEMINOLE | 7208:CYPRESS | CYPRESS_822 | 720822 | 2020-01-10 20:46 | 2020-01-10 20:58 | 12.27 | 1 | 1 | 12.2667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | HOLDENVILLE | 306 N.BULLITT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 114316 | 13591 | 2518 | 1430 | 1.4259e-05 | 1.1624e-06 | 12.2667 | 1 | 310 | Customer | 5563 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003776 | PD-01102020-00670 | NORTHEAST | SAPULPA | 3216:BEELINE | BEELINE_1626 | 321626 | 2020-01-10 21:03 | 2020-01-11 02:11 | 308.13 | 19 | 10 | 5798.8 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | BIXBY | HARVARD + 151ST NW CRN | CMI_NORMAL | NO | NO | NO | 860257 | 73957 | 40726 | 5561 | 919 | 0.0067408 | 2.2086e-05 | 305.2 | 1 | 310 | Mainline | 63267 | Fuse | FuseOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003768 |  | NORTHEAST | SAPULPA | 3216:BEELINE | BEELINE_1626 | 321626 | 2020-01-10 21:03 | 2020-01-10 21:03 | 0.08 | 905 | 0 | 75.4167 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | GLENPOOL | 3594 OKMULGEE BEELINE EXPY | CMI_MOMENTARY | YES | NO | NO | 860257 | 73957 | 40726 | 5561 | 919 | 8.7668e-05 | 0.001052 | 0.083333 | 1 | 0 | Feeder | BEELINE_1626 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003770 | PD-01102020-00668 | ARKANSAS | POTEAU | 3509:PANAMA | PANAMA 22 | 350922 | 2020-01-10 21:05 | 2020-01-10 22:23 | 78.03 | 1 | 1 | 78.0333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | PANAMA | 25419 WINDING TRAIL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 82157 | 13469 | 1386 | 114 | 9.0709e-05 | 1.1624e-06 | 78.0333 | 1 | 310 | Load | 305012 | Load | Tran1phPad | TOBY C MEAD | 918-658-5596 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003772 | PD-01102020-00669 | NORTHEAST | MUSKOGEE | 3325:WELLS | WELLS_2549 | 332549 | 2020-01-10 21:10 | 2020-01-11 01:06 | 236.07 | 1 | 1 | 129.7667 | 12 | POOR CONNECTION | 17 | JUMPER | EUFAULA | 3 ME ON TEXANNA RD FROM US 69 | CMI_NORMAL | NO | NO | NO | 860257 | 73957 | 33231 | 2373 | 1050 | 0.00015085 | 1.1624e-06 | 129.7667 | 1 | 310 | Load | 198578 | Load | Tran1phOH | JAMES MCDONALD | 405-361-7186 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003777 | PD-01102020-00671 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2022 | 822022 | 2020-01-10 21:10 | 2020-01-10 22:29 | 78.9 | 14 | 17 | 942.4333 | 28 | OTHER (DESCRIBE) | 27 | CUTOUT | OKLAHOMA CITY | 2315 NW.PARK | CMI_NORMAL | NO | NO | NO | 860257 | 168043 | 148241 | 6035 | 2120 | 0.0010955 | 1.6274e-05 | 67.3167 | 1 | 310 | Load | 1807 | Load | Tran1phOH | PETER BILICKI | 619-726-8332 | [5 empty] | Other | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003785 | PD-01102020-00674 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3222 | 813222 | 2020-01-10 21:33 | 2020-01-10 22:21 | 47.63 | 1 | 1 | 36.6833 | 22 | WIND | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 5508 S PENN | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860257 | 158998 | 102083 | 7597 | 1483 | 4.2642e-05 | 1.1624e-06 | 36.6833 | 1 | 320 | Customer | 3004 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003803 | PD-01102020-00676 | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_521 | 530521 | 2020-01-10 21:34 | 2020-01-11 02:40 | 306.47 | 119 | 62 | 35701.9833 | 22 | WIND | 17 | JUMPER | HEALDTON | S OF HAMMON ON 5TH | CMI_NORMAL | NO | NO | NO | 860257 | 77559 | 6791 | 2127 | 1259 | 0.041502 | 0.00013833 | 300.0167 | 1 | 310 | Mainline | 1681 | Fuse | FuseOH | ROBERT J BEARDSLEE | 580-618-2506 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003797 | PD-01102020-00677 | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1522 | 921522 | 2020-01-10 21:43 | 2020-01-11 04:31 | 408.17 | 29 | 15 | 10308.05 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | CHARLESTON | CHAFFEE RD & ST HWY 22 | CMI_NORMAL | NO | NO | NO | 860257 | 82157 | 61153 | 959 | 469 | 0.011983 | 3.3711e-05 | 355.45 | 1 | 310 | Mainline | 2479 | Fuse | FuseOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Weather | N | DISTRIBUTION | 34.5/19.9kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003793 | PD-01102020-00678 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1924 | 851924 | 2020-01-10 21:43 | 2020-01-11 03:51 | 367.53 | 1 | 1 | 366.7333 | 4 | DETERIORATION | 27 | CUTOUT | MIDWEST CITY | 8604 NE.5 | CMI_NORMAL | NO | NO | NO | 860257 | 114316 | 71178 | 12433 | 1605 | 0.00042631 | 1.1624e-06 | 366.7333 | 1 | 310 | Load | 10604 | Load | Tran1phOH | JEREMIAH D WALKER | 405-974-0464 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003792 | PD-01102020-00683 | SOUTHERN | DURANT | 5511:BOKCHITO | BOKCHITO 21 | 551121 | 2020-01-10 21:44 | 2020-01-11 00:41 | 176.97 | 1 | 1 | 170.6167 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | BOKCHITO | WS BOKCHITO N OF H70 | CMI_NORMAL | NO | NO | NO | 860257 | 77559 | 15478 | 669 | 669 | 0.00019833 | 1.1624e-06 | 170.6167 | 1 | 310 | Load | 190295 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Weather | N | DISTRIBUTION | 34.5/19.9kv | 2020-01-10 | 2020 |  | #N/A
J2001.003795 | PD-01102020-00679 | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2131 | 332131 | 2020-01-10 21:46 | 2020-01-11 00:34 | 168.03 | 1 | 1 | 69.0667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | BRAGGS | 300'' E OF NEW CONVIENCE | CMI_NORMAL | NO | NO | NO | 860257 | 73957 | 33231 | 3333 | 1172 | 8.0286e-05 | 1.1624e-06 | 69.0667 | 1 | 310 | Customer | 1194 | Load | Tran1phOH | JAMES MCDONALD | 405-361-7186 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | #N/A
J2001.003796 |  | METRO EAST | CHANDLER | 7118:KEY WEST | KEY_WEST_1846 | 711846 | 2020-01-10 21:46 | 2020-01-10 21:51 | 4.88 | 1 | 1 | 4.8833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DEPEW | 604 E.8TH | CMI_MOMENTARY | YES | NO | NO | 860257 | 114316 | 7457 | 1209 | 469 | 5.6766e-06 | 1.1624e-06 | 4.8833 | 1 | 320 | Customer | 44070 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003810 | PD-01102020-00680 | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-10 21:47 | 2020-01-10 22:58 | 70.68 | 4 | 5 | 271.2667 | 22 | WIND | 23 | FUSE - PRIMARY | MUSTANG | ES MUSTANG RD-NS SW 89 | CMI_NORMAL | NO | NO | NO | 860257 | 128622 | 115890 | 18216 | 4429 | 0.00031533 | 4.6498e-06 | 67.8167 | 1 | 310 | Mainline | 6391 | Fuse | FuseOH | TONY J ILG | 405-714-7441 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2022
J2001.003798 |  | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-01-10 21:48 | 2020-01-10 21:48 | 0.03 | 999 | 0 | 33.3 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 3623 RED CEDAR RD | CMI_MOMENTARY | YES | NO | NO | 860257 | 77559 | 23571 | 2205 | 1000 | 3.8709e-05 | 0.0011613 | 0.033333 | 1 | 0 | Feeder | DRIPPING_SPRI_1129 | Recloser | 0 | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003819 | PD-01102020-00687 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-10 21:56 | 2020-01-11 05:53 | 477.05 | 85 | 42 | 30435.4167 | 25 | LIGHTNING | 37 | CONDUCTOR PRIMARY - OH | MOUNTAINBURG | NWC of lake fort smith co and hwy 71 | CMI_NORMAL | NO | NO | NO | 860257 | 82157 | 61153 | 3788 | 1204 | 0.035379 | 9.8808e-05 | 358.0637 | 1 | 310 | Mainline | 251236 | Fuse | FuseOH | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003814 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-10 21:56 | 2020-01-10 21:56 | 0 | 3788 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MULBERRY | 6007 EAST HWY 64 | CMI_MOMENTARY | YES | NO | NO | 860257 | 82157 | 61153 | 3788 | 1204 | 0 | 0.0044033 | 0 | 1 | 0 | Feeder | SIMMONS_3062 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003816 | PD-01102020-00686 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-10 21:59 | 2020-01-11 03:38 | 339.25 | 2 | 2 | 675.4667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MOUNTAINBURG | MTNBURG AR | CMI_NORMAL | NO | NO | NO | 860257 | 82157 | 61153 | 3788 | 1204 | 0.00078519 | 2.3249e-06 | 337.7333 | 1 | 310 | Secondary | 5802 | Load | Tran1phOH | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003817 | PD-01102020-00684 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-10 21:59 | 2020-01-11 03:56 | 356.72 | 1 | 1 | 314.1 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MOUNTAINBURG | MTNBURG | CMI_NORMAL | NO | NO | NO | 860257 | 82157 | 61153 | 3788 | 1204 | 0.00036512 | 1.1624e-06 | 314.1 | 1 | 310 | Customer | 12179 | Load | Tran1phOH | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003822 | PD-01102020-00682 | NORTHEAST | MUSKOGEE | 3326:JAMESVILLE | JAMESVILLE_2642 | 332642 | 2020-01-10 22:03 | 2020-01-11 02:19 | 255.55 | 1 | 1 | 218.5167 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | HASKELL | HASKELL | CMI_NORMAL | NO | NO | NO | 860257 | 73957 | 33231 | 1549 | 725 | 0.00025401 | 1.1624e-06 | 218.5167 | 1 | 310 | Customer | 10878 | Load | Tran1phOH | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003823 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_622 | 460622 | 2020-01-10 22:07 | 2020-01-10 22:07 | 0 | 765 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | WOODWARD | 1005 CEDAR AVE | CMI_MOMENTARY | YES | NO | NO | 860257 | 53505 | 10416 | 5680 | 765 | 0 | 0.00088927 | 0 | 1 | 0 | Feeder | CEDAR_AVE_622 | Recloser | 0 | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003829 | PD-01102020-00688 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-10 22:11 | 2020-01-11 03:28 | 317.12 | 2 | 4 | 632.1667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MOUNTAINBURG | 1 3/4 M N-MTNBURG ON HWY 71 | CMI_NORMAL | NO | NO | NO | 860257 | 82157 | 61153 | 3788 | 1204 | 0.00073486 | 2.3249e-06 | 316.0833 | 1 | 310 | Load | 1828 | Load | Tran1phOH | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003834 |  | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_521 | 530521 | 2020-01-10 22:21 | 2020-01-11 03:39 | 318.17 | 1 | 1 | 318.1667 | 25 | LIGHTNING | 17 | JUMPER | HEALDTON | 411 STANOLIND | CMI_NORMAL | NO | NO | NO | 860257 | 77559 | 6791 | 2127 | 1259 | 0.00036985 | 1.1624e-06 | 318.1667 | 1 | 310 | Customer | 8395 | Load | Tran1phOH | ROBERT J BEARDSLEE | 580-618-2506 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003836 | PD-01102020-00690 | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1862 | 941862 | 2020-01-10 22:27 | 2020-01-11 02:57 | 269.95 | 1 | 1 | 268.6833 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | CLARKSVILLE | 1 3/4 M SE OF EUREKA BRICK | CMI_NORMAL | NO | NO | NO | 860257 | 82157 | 7535 | 729 | 729 | 0.00031233 | 1.1624e-06 | 268.6833 | 1 | 310 | Load | 15918 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003838 | PD-01102020-00691 | METRO EAST | SHAWNEE | 7417:TRIBBEY | TRIBBEY_1721 | 741721 | 2020-01-10 22:28 | 2020-01-11 02:04 | 215.92 | 1 | 1 | 218.6667 | 27 | TREE:NON PREVENTABLE | 37 | CONDUCTOR PRIMARY - OH | TECUMSEH | MILLSTONE RD, MACOMB | CMI_NORMAL | NO | NO | NO | 860257 | 114316 | 22090 | 241 | 241 | 0.00025419 | 1.1624e-06 | 218.6667 | 1 | 310 | Load | 317215 | Load | Tran1phOH | JEREMIAH D WALKER | 405-974-0464 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003837 | PD-01102020-00692 | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-10 22:29 | 2020-01-11 00:31 | 121.75 | 2 | 2 | 228.9833 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | COAL HILL | COAL HILL AR | CMI_NORMAL | NO | NO | NO | 860257 | 82157 | 7535 | 1503 | 1200 | 0.00026618 | 2.3249e-06 | 114.4917 | 1 | 310 | Load | 14501 | Load | Tran1phOH | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003843 | PD-01102020-00693 | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2124 | 332124 | 2020-01-10 22:37 | 2020-01-10 23:39 | 61.85 | 1 | 1 | 58.95 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | FORT GIBSON | FT GIBSON OK 74434 | CMI_NORMAL | NO | NO | NO | 860257 | 73957 | 33231 | 3333 | 1220 | 6.8526e-05 | 1.1624e-06 | 58.95 | 1 | 310 | Customer | 7845 | Load | Tran1phOH | GARY MICHAEL KNUPP | 918-577-8564 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | #N/A
J2001.003846 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6121 | 836121 | 2020-01-10 22:39 | 2020-01-10 22:52 | 13.2 | 1 | 1 | 13.2 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2117 NW.34 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 168043 | 148241 | 11099 | 1638 | 1.5344e-05 | 1.1624e-06 | 13.2 | 1 | 310 | Customer | 4260 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003845 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6124 | 836124 | 2020-01-10 22:39 | 2020-01-11 00:29 | 110.05 | 2 | 2 | 187.4 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 710 NW.23 | CMI_NORMAL | NO | NO | NO | 860257 | 168043 | 148241 | 11099 | 1765 | 0.00021784 | 2.3249e-06 | 93.7 | 1 | 310 | Secondary | 1254 | Load | TranOH3phDelta | Ties | [6 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-10 | 2020 |  | OK - 2020
J2001.003848 | PD-01102020-00694 | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1522 | 921522 | 2020-01-10 22:43 | 2020-01-11 05:53 | 429.88 | 1 | 3 | 427.9167 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | CHARLESTON | STONE HILL | CMI_NORMAL | NO | NO | NO | 860257 | 82157 | 61153 | 959 | 469 | 0.00049743 | 1.1624e-06 | 427.9167 | 1 | 310 | Customer | 2188 | Load | Tran1phOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Weather | N | DISTRIBUTION | 34.5/19.9kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003849 |  | SOUTHERN | SULPHUR | 5712:JOLLYVILLE | JOLLYVILLE_1264 | 571264 | 2020-01-10 22:46 | 2020-01-10 22:46 | 0 | 251 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | DAVIS | E 1750 RD AND N 3310 RD | CMI_MOMENTARY | YES | NO | NO | 860257 | 77559 | 6809 | 372 | 262 | 0 | 0.00029177 | 0 | 1 | 0 | Feeder | JOLLYVIL_1264 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-10 | 2020 |  | #N/A
J2001.003864 | PD-01102020-00700 | ARKANSAS | FORT SMITH | 9104:J STREET | J_STREET_429 | 910429 | 2020-01-10 22:57 | 2020-01-11 00:22 | 85.02 | 30 | 6 | 2427.5 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | FORT SMITH | N.A BET N.11TH + 12TH | CMI_NORMAL | NO | NO | NO | 860257 | 82157 | 61153 | 2003 | 423 | 0.0028218 | 3.4873e-05 | 80.9167 | 1 | 310 | Mainline | 5187 | Fuse | FuseOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003852 |  | ARKANSAS | FORT SMITH | 9104:J STREET | J_STREET_429 | 910429 | 2020-01-10 22:57 | 2020-01-10 22:57 | 0 | 404 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | FT SMITH | 909 N 3RD ST | CMI_MOMENTARY | YES | NO | NO | 860257 | 82157 | 61153 | 2003 | 423 | 0 | 0.00046963 | 0 | 1 | 0 | Feeder | J STREET_429 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003860 | PD-01102020-00698 | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1722 | 861722 | 2020-01-10 23:04 | 2020-01-11 01:45 | 160.68 | 81 | 76 | 12812.85 | 22 | WIND | 17 | JUMPER | OKLAHOMA CITY | S/O.SE.47 WS.SUNNYLANE | CMI_NORMAL | NO | NO | NO | 860257 | 114316 | 71178 | 6938 | 1787 | 0.014894 | 9.4158e-05 | 158.1833 | 1 | 310 | Mainline | 17951 | Fuse | FuseOH | DENNY J MORGAN | 405-501-1556 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | #N/A
J2001.003866 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-10 23:16 | 2020-01-11 00:58 | 102.65 | 1 | 1 | 68.2833 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | COAL HILL | 1/4M N-HWY 64 + FIRST,COALHILL | CMI_NORMAL | NO | NO | NO | 860257 | 82157 | 7535 | 1503 | 1200 | 7.9376e-05 | 1.1624e-06 | 68.2833 | 1 | 310 | Customer | 2725 | Load | Tran1phOH | [7 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-10 | 2020 |  | Ark - Series 2
J2001.003870 | PD-01102020-00699 | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-01-10 23:23 | 2020-01-11 00:42 | 79.27 | 1 | 1 | 71.961 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | BIXBY | 17350 hwy 64 | CMI_NORMAL | NO | NO | NO | 860257 | 73957 | 40726 | 2743 | 1439 | 8.3651e-05 | 1.1624e-06 | 71.961 | 1 | 310 | Load | 321569 | Load | Tran1phPad | PHIL STICKLER | 918-991-1321 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-10 | 2020 |  | OK - 2021
J2001.003887 | PD-01112020-00001 | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_631 | 730631 | 2020-01-11 00:08 | 2020-01-11 01:50 | 101.6 | 1 | 1 | 101.6 | 28 | OTHER (DESCRIBE) | 23 | FUSE - PRIMARY | SEMINOLE | 1.5MN 9 ON HARVY RD | CMI_NORMAL | NO | NO | NO | 860257 | 114316 | 13591 | 4058 | 665 | 0.0001181 | 1.1624e-06 | 101.6 | 1 | 310 | Load | 90241 | Load | 0 | BRADY A HUFF | 405-519-0701 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.003888 |  | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6524 | 836524 | 2020-01-11 00:11 | 2020-01-11 02:56 | 165.27 | 1 | 1 | 165.2667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | WARR ACRES | 6100 N.MACARTHUR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 128622 | 115890 | 7418 | 1651 | 0.00019211 | 1.1624e-06 | 165.2667 | 1 | 310 | Customer | 50025 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.003893 |  | NORTHEAST | MUSKOGEE | 3325:WELLS | WELLS_2542 | 332542 | 2020-01-11 00:27 | 2020-01-11 01:19 | 51.3 | 4 | 3 | 173.3 | 25 | LIGHTNING | 2 | TRANSFORMER OH | EUFAULA | 300 S/HARRISON/"H"ST | CMI_NORMAL | NO | NO | NO | 860257 | 73957 | 33231 | 2373 | 1319 | 0.00020145 | 4.6498e-06 | 43.325 | 1 | 310 | Tap | 26883 | Fuse | FuseOH | OGE | [6 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | OK - 2022
J2001.003902 |  | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_421 | 710421 | 2020-01-11 01:05 | 2020-01-11 01:05 | 0.07 | 1305 | 0 | 87 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | CHANDLER | N 3450 RD AND HWY 66 | CMI_MOMENTARY | YES | NO | NO | 860257 | 114316 | 7457 | 2821 | 1172 | 0.00010113 | 0.001517 | 0.066667 | 1 | 0 | Feeder | BELLCOW_421 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-11 | 2020 |  | OK - 2021
J2001.003903 | PD-01112020-00024 | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-11 01:12 | 2020-01-11 14:08 | 775.5 | 2 | 2 | 1546.9167 | 27 | TREE:NON PREVENTABLE | 37 | CONDUCTOR PRIMARY - OH | COAL HILL | COAL HILL AR | CMI_NORMAL | NO | NO | NO | 860257 | 82157 | 7535 | 1503 | 1200 | 0.0017982 | 2.3249e-06 | 773.4583 | 1 | 310 | Load | 14501 | Load | Tran1phOH | DWAIN C CAUGHERN | 479-459-0231 | [5 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-11 | 2020 |  | Ark - Series 2
J2001.003911 |  | NORTHEAST | MUSKOGEE | 3117:THREE RIVERS | THREE_RIVERS_1729 | 311729 | 2020-01-11 01:42 | 2020-01-11 02:30 | 47.65 | 1 | 0 | 47.65 | 11 | OVERLOAD | 56 | SCADA - LOCKOUT | 0 | 0 | CMI_NORMAL | NO | NO | NO | 860257 | 73957 | 33231 | 2831 | 1 | 5.539e-05 | 1.1624e-06 | 47.65 | 1 | 0 | Mainline | 311729 | Switch | 0 | [7 empty] | Equipment | N | SUBSTATION | 161kV | 2020-01-11 | 2020 |  | #N/A
J2001.003915 | PD-01112020-00031 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1422 | 311422 | 2020-01-11 01:54 | 2020-01-11 04:29 | 155.03 | 10 | 7 | 1044.6667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MUSKOGEE | 2009 ELGIN | CMI_NORMAL | NO | NO | NO | 860257 | 73957 | 33231 | 4561 | 1166 | 0.0012144 | 1.1624e-05 | 104.4667 | 1 | 310 | Load | 3663 | Load | Tran1phOH | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | OK - 2020
J2001.003916 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-11 02:02 | 2020-01-11 02:02 | 0.37 | 3753 | 0 | 486 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MULBERRY | 6007 EAST HWY 64 | CMI_MOMENTARY | YES | NO | NO | 860257 | 82157 | 61153 | 3788 | 1204 | 0.00056495 | 0.0043626 | 0.1295 | 1 | 0 | Feeder | SIMMONS_3062 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-11 | 2020 |  | Ark - Series 2
J2001.003919 |  | ARKANSAS | OZARK | 9412:ALTUS | ALTUS_1229 | 941229 | 2020-01-11 02:11 | 2020-01-11 02:11 | 0 | 865 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OZARK | 6007 GRAVEL RD | CMI_MOMENTARY | YES | NO | NO | 860257 | 82157 | 7535 | 865 | 865 | 0 | 0.0010055 | 0 | 1 | 0 | Feeder | ALTUS_1229 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-11 | 2020 |  | Ark - Series 2
J2001.003924 | PD-01112020-00032 | NORTHWEST | ENID | 4353:OTTER | OTTER_5341 | 435341 | 2020-01-11 02:31 | 2020-01-11 05:32 | 181.12 | 60 | 41 | 9843 | 22 | WIND | 17 | JUMPER | FAIRMONT | 1/4 MW GARBER Y | CMI_NORMAL | NO | NO | NO | 860257 | 53505 | 37572 | 960 | 792 | 0.011442 | 6.9747e-05 | 164.05 | 1 | 310 | Mainline | 210264 | Recloser | Rec1phHydralic | [7 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2021
J2001.003934 | PD-01112020-00034 | NORTHEAST | MUSKOGEE | 3312:CHECOTAH | CHECOTAH 22 | 331222 | 2020-01-11 03:10 | 2020-01-11 13:02 | 591.27 | 5 | 4 | 1351.5 | 3 | DAMAGED BY PUBLIC | 23 | FUSE - PRIMARY | CHECOTAH | 1 1/4MW OF 69 ON 266 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860257 | 73957 | 33231 | 2889 | 1534 | 0.001571 | 5.8122e-06 | 270.3 | 1 | 310 | Tap | 25721 | Fuse | FuseOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | OK - 2020
J2001.003958 | PD-01112020-00055 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4821 | 824821 | 2020-01-11 05:40 | 2020-01-11 08:38 | 178.33 | 1 | 2 | 178.3333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2236 NW.10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168043 | 148241 | 4189 | 242 | 0.00020729 | 1.1624e-06 | 178.3333 | 1 | 310 | Customer | 71381 | Load | Tran3phPadWye | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2022
J2001.003965 | PD-01112020-00058 | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_421 | 710421 | 2020-01-11 06:53 | 2020-01-11 13:15 | 381.73 | 1 | 1 | 380.9667 | 22 | WIND | 37 | CONDUCTOR PRIMARY - OH | CHANDLER | WEST 15TH | CMI_NORMAL | NO | NO | NO | 860316 | 114316 | 7457 | 2821 | 1172 | 0.00044282 | 1.1624e-06 | 380.9667 | 1 | 310 | Load | 997 | Load | Tran1phOH | TOMMY D ROBERTSON | 405-696-6476 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2021
J2001.003966 | PD-01112020-00060 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2263 | 852263 | 2020-01-11 06:59 | 2020-01-11 09:56 | 177.18 | 1 | 1 | 177.1833 | 13 | PREMATURE FAILURE | 2 | TRANSFORMER OH | OKLAHOMA CITY | 4118 N YOUNGS DR | CMI_NORMAL | NO | NO | NO | 860316 | 114316 | 71178 | 11619 | 1530 | 0.00020595 | 1.1624e-06 | 177.1833 | 1 | 310 | Load | 68461 | Load | Tran1phOH | JUSTIN C TAYLOR | 405-534-1006 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2021
J2001.003972 | PD-01112020-00062 | METRO NORTH | GUTHRIE | 8807:CRESCENT | CRESCENT_723 | 880723 | 2020-01-11 07:14 | 2020-01-11 22:04 | 889.53 | 13 | 16 | 11451.4833 | 25 | LIGHTNING | 1 | TRANSFORMER UG | CASHION | B4 L6 CIMARRON TR | CMI_NORMAL | NO | NO | NO | 860316 | 168043 | 19802 | 1764 | 891 | 0.013311 | 1.5111e-05 | 880.8833 | 1 | 310 | Load | 37458 | Load | Tran1phPad | TOMMY D ROBERTSON | 405-696-6476 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.003976 | PD-01112020-00063 | SOUTHERN | MADILL | 5906:TISHOMINGO | TISHOMINGO_621 | 590621 | 2020-01-11 07:32 | 2020-01-11 09:15 | 103.33 | 1 | 1 | 103.3333 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | TISHOMINGO | 1101 S BYRD ST-TISH | CMI_NORMAL | NO | NO | NO | 860316 | 77559 | 7203 | 967 | 916 | 0.00012011 | 1.1624e-06 | 103.3333 | 1 | 310 | Load | 174024 | Load | Tran3phWye | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2021
J2001.003977 | PD-01112020-00065 | ARKANSAS | OZARK | 9413:RAZORBACK | RAZORBACK_1362 | 941362 | 2020-01-11 07:32 | 2020-01-11 19:04 | 691.97 | 1 | 2 | 640.3167 | 25 | LIGHTNING | 2 | TRANSFORMER OH | SCRANTON | SCRANTON | CMI_NORMAL | NO | NO | NO | 860316 | 82157 | 7535 | 396 | 396 | 0.00074428 | 1.1624e-06 | 640.3167 | 1 | 310 | Customer | 11289 | Load | Tran1phOH | ANDREW SCOTT LONG | 479-739-1879 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | Ark - Series 2
J2001.003978 | PD-01112020-00064 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-11 07:36 | 2020-01-11 09:45 | 129.2 | 30 | 3 | 3334 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MOUNTAINBURG | NWC of lake fort smith co and hwy 71 | CMI_NORMAL | NO | NO | NO | 860316 | 82157 | 61153 | 3788 | 1204 | 0.0038753 | 3.4871e-05 | 111.1333 | 1 | 310 | Mainline | 251236 | Fuse | FuseOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-11 | 2020 |  | Ark - Series 2
J2001.003979 | PD-01112020-00067 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-11 07:53 | 2020-01-11 10:10 | 136.85 | 1 | 1 | 112.0167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MOUNTAINBURG | HWY 71 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 82157 | 61153 | 3788 | 1204 | 0.0001302 | 1.1624e-06 | 112.0167 | 1 | 310 | Customer | 8082 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-11 | 2020 |  | Ark - Series 2
J2001.003983 | PD-01112020-00071 | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_521 | 890521 | 2020-01-11 08:02 | 2020-01-11 10:33 | 150.9 | 1 | 2 | 150.9 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | EL RENO | 1213 W.LONDON **AMORPHOUS*** | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 128622 | 12732 | 6935 | 2211 | 0.0001754 | 1.1624e-06 | 150.9 | 1 | 310 | Customer | 41467 | Load | Tran1phOH | BRANDON H SMITH | 405-371-4294 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.003988 |  | NORTHWEST | ENID | 4240:DEER CREEK | DEER CREEK 48 | 424048 | 2020-01-11 08:23 | 2020-01-11 08:43 | 19.78 | 1 | 1 | 19.7833 | 1 | CANCELLED | 57 | CANCELLED | GARBER | 7.5N.GARBER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 53505 | 37572 | 621 | 476 | 2.2995e-05 | 1.1624e-06 | 19.7833 | 1 | 310 | Load | 6851 | Load | Tran3phWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | #N/A
J2001.003987 | PD-01112020-00072 | METRO WEST | WEST | 8359:YUKON | YUKON_5923 | 835923 | 2020-01-11 08:23 | 2020-01-11 09:24 | 60.83 | 1 | 1 | 56.8833 | 22 | WIND | 21 | FUSE - TRANSFORMER | YUKON | 10 S.11 LITE | CMI_NORMAL | NO | NO | NO | 860316 | 128622 | 115890 | 6412 | 1150 | 6.6119e-05 | 1.1624e-06 | 56.8833 | 1 | 310 | Load | 19394 | Load | Tran1phOH | COLTON RACKLEY | 405-779-5033 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | #N/A
J2001.003990 | PD-01112020-00074 | METRO NORTH | NORTH | 8506:PARK PLACE | PARK_PLACE_623 | 850623 | 2020-01-11 08:32 | 2020-01-11 09:53 | 81.37 | 1 | 1 | 81.3667 | 4 | DETERIORATION | 27 | CUTOUT | OKLAHOMA CITY | 1715 N Walnut | CMI_NORMAL | NO | NO | NO | 860316 | 168043 | 148241 | 830 | 266 | 9.4578e-05 | 1.1624e-06 | 81.3667 | 1 | 310 | Load | 251666 | Load | Tran3phWye | ROBERT HALL | 405-757-9640 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.003997 | PD-01112020-00080 | SOUTHERN | MADILL | 5906:TISHOMINGO | TISHOMINGO_621 | 590621 | 2020-01-11 09:04 | 2020-01-11 09:22 | 17.55 | 1 | 1 | 17.55 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | TISHOMINGO | OHIO + WILSON - TISH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77559 | 7203 | 967 | 916 | 2.0399e-05 | 1.1624e-06 | 17.55 | 1 | 310 | Customer | 11233 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2021
J2001.004000 | PD-01112020-00082 | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_649 | 890649 | 2020-01-11 09:19 | 2020-01-11 12:24 | 185.35 | 1 | 3 | 75.5722 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OAKWOOD | OAKWOOD >MICHIGAN,CHERRY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 128622 | 12732 | 1365 | 278 | 8.7842e-05 | 1.1624e-06 | 75.5722 | 1 | 310 | Customer | 38623 | Load | Tran1phOH | BRANDON H SMITH | 405-371-4294 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004002 | PD-01112020-00085 | METRO NORTH | NORTH | 8347:WILSHIRE | WILSHIRE_4721 | 834721 | 2020-01-11 09:31 | 2020-01-11 10:42 | 71.12 | 1 | 1 | 71.1167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 6205 BELLE DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168043 | 148241 | 4621 | 927 | 8.2663e-05 | 1.1624e-06 | 71.1167 | 1 | 310 | Customer | 27417 | Load | TranOpenDelta | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2022
J2001.004010 | PD-01112020-00089 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-11 09:45 | 2020-01-11 11:46 | 120.97 | 15 | 10 | 1623.75 | 5 | ELECTRICAL TRACKING | 23 | FUSE - PRIMARY | MOUNTAINBURG | WARLOOP RD AT FLTR PLN | CMI_NORMAL | NO | NO | NO | 860316 | 82157 | 61153 | 3788 | 1204 | 0.0018874 | 1.7435e-05 | 108.25 | 1 | 310 | Mainline | 3481 | Recloser | Rec1phHydralic | TRAVIS EARNHART | 479-462-5659 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-11 | 2020 |  | Ark - Series 2
J2001.004008 |  | METRO SOUTH | SOUTH | 8726:NOBLE | NOBLE_2621 | 872621 | 2020-01-11 09:46 | 2020-01-11 09:55 | 8.83 | 1 | 1 | 8.8333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NOBLE | 8TH ST. + HWY 77 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 158998 | 56915 | 2968 | 1447 | 1.0268e-05 | 1.1624e-06 | 8.8333 | 1 | 310 | Customer | 74669 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004011 | PD-01112020-00086 | METRO WEST | WEST | 8158:SARA | SARA_5864 | 815864 | 2020-01-11 09:51 | 2020-01-11 10:47 | 55.72 | 1 | 1 | 51.45 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 12309 SW 27TH ST | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860316 | 128622 | 115890 | 18216 | 4810 | 5.9804e-05 | 1.1624e-06 | 51.45 | 1 | 320 | Customer | 76371 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2022
J2001.004012 | PD-01112020-00088 | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5631 | 865631 | 2020-01-11 09:52 | 2020-01-11 10:58 | 66.38 | 1 | 1 | 66.3833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 5213 EDEN DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 158998 | 102083 | 2747 | 374 | 7.7162e-05 | 1.1624e-06 | 66.3833 | 1 | 310 | Customer | 20091 | Load | Tran1phPad | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004015 | PD-01112020-00091 | SOUTHERN | DURANT | 5511:BOKCHITO | BOKCHITO 21 | 551121 | 2020-01-11 09:57 | 2020-01-11 15:17 | 319.52 | 1 | 1 | 308.6 | 25 | LIGHTNING | 1 | TRANSFORMER UG | BOKCHITO | DSVIS ST/HWY 70 .3S .2N-BOKCHI | CMI_NORMAL | NO | NO | NO | 860316 | 77559 | 15478 | 669 | 669 | 0.00035871 | 1.1624e-06 | 308.6 | 1 | 320 | Customer | 28032 | Load | Tran3phPadWye | JEREMY L MULLENS | 580-775-3134 | [5 empty] | Weather | N | DISTRIBUTION | 34.5/19.9kv | 2020-01-11 | 2020 |  | #N/A
J2001.004017 | PD-01112020-00090 | METRO EAST | EAST | 8416:DUNJEE | DUNJEE_1621 | 841621 | 2020-01-11 10:01 | 2020-01-11 12:40 | 159.28 | 1 | 1 | 159.2833 | 5 | ELECTRICAL TRACKING | 21 | FUSE - TRANSFORMER | CHOCTAW | 14109 NE. 21 | CMI_NORMAL | NO | NO | NO | 860316 | 114316 | 71178 | 3541 | 1553 | 0.00018515 | 1.1624e-06 | 159.2833 | 1 | 310 | Load | 82530 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004020 | PD-01112020-00092 | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1024 | 311024 | 2020-01-11 10:10 | 2020-01-11 12:12 | 122.03 | 1 | 1 | 122.0333 | 4 | DETERIORATION | 50 | CONNECTOR | MUSKOGEE | 1525 IRVING | CMI_NORMAL | NO | NO | NO | 860316 | 73957 | 33231 | 2899 | 1390 | 0.00014185 | 1.1624e-06 | 122.0333 | 1 | 320 | Customer | 8088 | Load | Tran1phOH | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | OK - 2020
J2001.004024 | PD-01112020-00094 | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-01-11 10:20 | 2020-01-11 11:11 | 51.17 | 1 | 1 | 51.1667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7558 NW.10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 128622 | 115890 | 3405 | 2036 | 5.9474e-05 | 1.1624e-06 | 51.1667 | 1 | 310 | Customer | 42158 | Load | Tran1phPad | COLTON RACKLEY | 405-779-5033 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004025 | PD-01112020-00093 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2627 | 862627 | 2020-01-11 10:20 | 2020-01-11 11:16 | 56 | 1 | 1 | 56 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DEL CITY | 3129 DENTWOOD TR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 158998 | 102083 | 7413 | 2000 | 6.5092e-05 | 1.1624e-06 | 56 | 1 | 310 | Customer | 20861 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004027 | PD-01112020-00099 | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1623 | 581623 | 2020-01-11 10:29 | 2020-01-11 12:25 | 116.25 | 1 | 2 | 13.55 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ADA | 2ND+3RD PLS W OF OAK ON KINGS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77559 | 11504 | 3455 | 1649 | 1.575e-05 | 1.1624e-06 | 13.55 | 1 | 310 | Customer | 1580 | Load | TranOHDeltaSplitBank | JORDAN HERBERT-BLUE | 918-839-1152 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004031 | PD-01112020-00103 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-11 10:44 | 2020-01-11 11:51 | 67.47 | 1 | 1 | 49.75 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MOUNTAINBURG | RT 2 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 82157 | 61153 | 3788 | 1204 | 5.7828e-05 | 1.1624e-06 | 49.75 | 1 | 310 | Customer | 7431 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-11 | 2020 |  | Ark - Series 2
J2001.004033 | PD-01112020-00106 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3024 | 743024 | 2020-01-11 10:46 | 2020-01-11 14:19 | 213.12 | 1 | 1 | 213.1167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | SHAWNEE | 716 S.MARKET | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 114316 | 22090 | 6640 | 1639 | 0.00024772 | 1.1624e-06 | 213.1167 | 1 | 310 | Customer | 7682 | Load | Tran1phOH | STEVEN CASKEY | 405-777-8855 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004035 | PD-01112020-00101 | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_863 | 550863 | 2020-01-11 10:52 | 2020-01-11 12:59 | 127.2 | 1 | 1 | 127.2 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MEAD | 6414 HWY 70 WEST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77559 | 15478 | 1103 | 622 | 0.00014785 | 1.1624e-06 | 127.2 | 1 | 310 | Customer | 228788 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004036 | PD-01112020-00102 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1422 | 311422 | 2020-01-11 10:53 | 2020-01-11 12:40 | 107.25 | 1 | 1 | 107.25 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MUSKOGEE | 1102 WEST SHAWNEE AVE | CMI_NORMAL | NO | NO | NO | 860316 | 73957 | 33231 | 4561 | 1166 | 0.00012466 | 1.1624e-06 | 107.25 | 1 | 310 | Load | 400314 | Load | Tran3phWye | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | OK - 2020
J2001.004038 | PD-01112020-00107 | NORTHEAST | MUSKOGEE | 3111:FIVE TRIBES | FIVE_TRIBES_1131 | 311131 | 2020-01-11 11:03 | 2020-01-11 13:58 | 175.48 | 1 | 1 | 137.2667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MUSKOGEE | 702 MOONEY DR MUSKOGEE | CMI_NORMAL | NO | NO | NO | 860316 | 73957 | 33231 | 1680 | 816 | 0.00015955 | 1.1624e-06 | 137.2667 | 1 | 310 | Load | 16463 | Load | TranOpenDelta | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-11 | 2020 |  | #N/A
J2001.004044 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4028 | 834028 | 2020-01-11 11:22 | 2020-01-11 11:26 | 4.57 | 1 | 1 | 4.5667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 8515 CANDLEWOOD DR | CMI_MOMENTARY | YES | NO | NO | 860316 | 128622 | 115890 | 10840 | 1261 | 5.3081e-06 | 1.1624e-06 | 4.5667 | 1 | 310 | Customer | 50017 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004045 | PD-01112020-00112 | ARKANSAS | OZARK | 9413:RAZORBACK | RAZORBACK_1362 | 941362 | 2020-01-11 11:24 | 2020-01-11 14:11 | 166.55 | 2 | 2 | 327.25 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | SCRANTON | 1/4M E-SCRANTON ON HWY 197 | CMI_NORMAL | NO | NO | NO | 860316 | 82157 | 7535 | 396 | 396 | 0.00038038 | 2.3247e-06 | 163.625 | 1 | 310 | Load | 2648 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | Ark - Series 2
J2001.004046 | PD-01112020-00111 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_623 | 870623 | 2020-01-11 11:29 | 2020-01-11 12:56 | 86.95 | 1 | 1 | 86.95 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | 1420 W.LINDSEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 158998 | 56915 | 7362 | 1898 | 0.00010107 | 1.1624e-06 | 86.95 | 1 | 320 | Customer | 54398 | Load | Tran3phPadWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2021
J2001.004050 | PD-01112020-00114 | METRO NORTH | NORTH | 8347:WILSHIRE | WILSHIRE_4723 | 834723 | 2020-01-11 11:46 | 2020-01-11 15:25 | 219.37 | 1 | 1 | 219.3667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3009 SHIRLEY LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168043 | 148241 | 4621 | 1098 | 0.00025498 | 1.1624e-06 | 219.3667 | 1 | 310 | Customer | 23349 | Load | Tran1phOH | PETER BILICKI | 619-726-8332 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2021
J2001.004051 | PD-01112020-00120 | SOUTHERN | DURANT | 5512:COLBERT | COLBERT_1221 | 551221 | 2020-01-11 11:46 | 2020-01-11 14:13 | 147.13 | 1 | 2 | 131.6 | 11 | OVERLOAD | 2 | TRANSFORMER OH | CALERA | 4TH AND MAIN - CALERA | CMI_NORMAL | NO | NO | NO | 860316 | 77559 | 15478 | 2166 | 895 | 0.00015297 | 1.1624e-06 | 131.6 | 1 | 320 | Customer | 28110 | Load | Tran1phOH | JEREMY L MULLENS | 580-775-3134 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004053 | PD-01112020-00115 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6121 | 836121 | 2020-01-11 11:48 | 2020-01-11 15:56 | 247.98 | 1 | 2 | 247.9833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1430 NW.41 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168043 | 148241 | 11099 | 1638 | 0.00028825 | 1.1624e-06 | 247.9833 | 1 | 310 | Customer | 28910 | Load | Tran1phOH | PETER BILICKI | 619-726-8332 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2021
J2001.004054 | PD-01112020-00116 | METRO SOUTH | SOUTH | 8709:LITTLE R LAKE | LITTLE_RIVER_L_921 | 870921 | 2020-01-11 11:50 | 2020-01-11 14:21 | 150.72 | 1 | 1 | 150.7167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | NORMAN | 9800 E.BETHEL RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 158998 | 56915 | 672 | 672 | 0.00017519 | 1.1624e-06 | 150.7167 | 1 | 310 | Load | 56354 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | #N/A
J2001.004056 | PD-01112020-00122 | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1222 | 911222 | 2020-01-11 11:55 | 2020-01-11 14:00 | 125.22 | 1 | 1 | 7.3167 | 12 | POOR CONNECTION | 50 | CONNECTOR | FORT SMITH | 722 N.18 | CMI_NORMAL | NO | NO | NO | 860316 | 82157 | 61153 | 6594 | 1285 | 8.5046e-06 | 1.1624e-06 | 7.3167 | 1 | 310 | Customer | 1100 | Load | Tran1phOH | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | Ark - Series 1
J2001.004060 | PD-01112020-00123 | SOUTHERN | HEALDTON | 5319:FOX | FOX 21 | 531921 | 2020-01-11 12:06 | 2020-01-11 13:27 | 80.65 | 1 | 1 | 80.65 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FOX | HWY 76 & 53E 2S .5W .2NE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77559 | 6791 | 706 | 341 | 9.3745e-05 | 1.1624e-06 | 80.65 | 1 | 310 | Load | 356684 | Load | 0 | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004062 | PD-01112020-00124 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3022 | 743022 | 2020-01-11 12:11 | 2020-01-11 13:45 | 94 | 1 | 2 | 85.75 | 4 | DETERIORATION | 50 | CONNECTOR | SHAWNEE | 820 N BEARD | CMI_NORMAL | NO | NO | NO | 860316 | 114316 | 22090 | 6640 | 2163 | 9.9673e-05 | 1.1624e-06 | 85.75 | 1 | 310 | Customer | 4329 | Load | Tran1phOH | STEVEN CASKEY | 405-777-8855 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2020
J2001.004067 | PD-01112020-00133 | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1222 | 911222 | 2020-01-11 12:18 | 2020-01-11 21:26 | 548.32 | 33 | 33 | 17956.95 | 25 | LIGHTNING | 28 | CROSSARM | FORT SMITH | S.D BET 16 + LEXINGTON | CMI_NORMAL | NO | NO | NO | 860316 | 82157 | 61153 | 6594 | 1285 | 0.020873 | 3.8358e-05 | 544.15 | 1 | 310 | Mainline | 6108 | Recloser | Tripsaver3ph | STEVE K HIGHFILL | 918-869-2785 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | Ark - Series 1
J2001.004064 | PD-01112020-00127 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7429 | 847429 | 2020-01-11 12:18 | 2020-01-11 14:19 | 121.03 | 1 | 1 | 110.0333 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 2424 NE.25 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860316 | 168043 | 148241 | 6152 | 680 | 0.0001279 | 1.1624e-06 | 110.0333 | 1 | 320 | Customer | 6901 | Load | Tran1phOH | PETER BILICKI | 619-726-8332 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2022
J2001.004065 | PD-01112020-00126 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6333 | 816333 | 2020-01-11 12:18 | 2020-01-11 14:56 | 158.02 | 1 | 1 | 148.9333 | 22 | WIND | 31 | CONDUCTOR SERVICE - OH | MOORE | 911 NW.1 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860316 | 158998 | 102083 | 11814 | 1229 | 0.00017311 | 1.1624e-06 | 148.9333 | 1 | 310 | Customer | 20796 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2022
J2001.004066 |  | NORTHEAST | MUSKOGEE | 3137:AGENCY | AGENCY_3769 | 313769 | 2020-01-11 12:22 | 2020-01-11 12:22 | 0 | 136 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MUSKOGEE | 4224 PALM AVE | CMI_MOMENTARY | YES | NO | NO | 860316 | 73957 | 33231 | 136 | 136 | 0 | 0.00015808 | 0 | 1 | 0 | Feeder | AGENCY_3769 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-11 | 2020 |  | #N/A
J2001.004072 | PD-01112020-00131 | METRO WEST | WEST | 8359:YUKON | YUKON_5921 | 835921 | 2020-01-11 12:31 | 2020-01-11 12:54 | 23.27 | 1 | 1 | 23.2667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | YUKON | 901 GARDEN GROVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 128622 | 115890 | 6412 | 1803 | 2.7044e-05 | 1.1624e-06 | 23.2667 | 1 | 310 | Customer | 47474 | Load | Tran1phPad | COLTON RACKLEY | 405-779-5033 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | #N/A
J2001.004071 | PD-01112020-00139 | SOUTHERN | MADILL | 5408:CANEY CREEK | CANEY_CREEK_831 | 540831 | 2020-01-11 12:32 | 2020-01-11 14:43 | 131.45 | 1 | 1 | 128.3333 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | KINGSTON | 5 N MAYTUBBY ST | CMI_NORMAL | NO | NO | NO | 860316 | 77559 | 7203 | 1053 | 629 | 0.00014917 | 1.1624e-06 | 128.3333 | 1 | 310 | Customer | 3750 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004075 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2263 | 852263 | 2020-01-11 12:41 | 2020-01-11 14:47 | 126 | 1 | 1 | 99.85 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 4118 N YOUNGS DR | CMI_NORMAL | NO | NO | NO | 860316 | 114316 | 71178 | 11619 | 1530 | 0.00011606 | 1.1624e-06 | 99.85 | 1 | 310 | Load | 68461 | Load | Tran1phOH | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2021
J2001.004077 | PD-01112020-00140 | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1023 | 541023 | 2020-01-11 12:43 | 2020-01-11 14:03 | 79.67 | 1 | 1 | 73.2833 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | OAKLAND | 105 S.6TH | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860316 | 77559 | 7203 | 2379 | 844 | 8.5182e-05 | 1.1624e-06 | 73.2833 | 1 | 311 | Customer | 16330 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004079 | PD-01112020-00144 | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3722 | 913722 | 2020-01-11 12:46 | 2020-01-11 20:03 | 436.97 | 42 | 31 | 18037.25 | 22 | WIND | 34 | CONDUCTOR SECONDARY - OH | FORT SMITH | GRAND AV BETW N.46+47 | CMI_NORMAL | NO | NO | NO | 860316 | 82157 | 61153 | 4565 | 1438 | 0.020966 | 4.8819e-05 | 429.4583 | 1 | 310 | Tap | 3866 | Fuse | FuseOH | STEVE K HIGHFILL | 918-869-2785 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | Ark - Series 3
J2001.004085 | PD-01112020-00142 | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-01-11 12:52 | 2020-01-11 15:22 | 149.5 | 1 | 1 | 149.5 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | TISHOMINGO | 1M W TISH ON HWY 22 S SIDE | CMI_NORMAL | NO | NO | NO | 860316 | 77559 | 7203 | 2191 | 1673 | 0.00017377 | 1.1624e-06 | 149.5 | 1 | 320 | Load | 190166 | Load | Tran3phWye | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004084 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4028 | 834028 | 2020-01-11 12:53 | 2020-01-11 13:09 | 16.17 | 1 | 1 | 16.1667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 8515 CANDLEWOOD DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 128622 | 115890 | 10840 | 1261 | 1.8792e-05 | 1.1624e-06 | 16.1667 | 1 | 310 | Customer | 50017 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004083 | PD-01112020-00146 | METRO EAST | EAST | 8416:DUNJEE | DUNJEE_1623 | 841623 | 2020-01-11 12:53 | 2020-01-11 14:54 | 121.12 | 1 | 1 | 111.2833 | 27 | TREE:NON PREVENTABLE | 21 | FUSE - TRANSFORMER | SPENCER | 3529 SUNSET TR | CMI_NORMAL | NO | NO | NO | 860316 | 114316 | 71178 | 3541 | 1988 | 0.00012935 | 1.1624e-06 | 111.2833 | 1 | 310 | Customer | 11468 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004086 | PD-01112020-00145 | METRO EAST | SEMINOLE | 7208:CYPRESS | CYPRESS_821 | 720821 | 2020-01-11 12:58 | 2020-01-11 14:31 | 92.75 | 1 | 3 | 87.5667 | 22 | WIND | 31 | CONDUCTOR SERVICE - OH | HOLDENVILLE | 214.5 S BULLITT | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860316 | 114316 | 13591 | 2518 | 1088 | 0.00010178 | 1.1624e-06 | 87.5667 | 1 | 321 | Customer | 4484 | Load | Tran1phOH | BRADY A HUFF | 405-519-0701 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | #N/A
J2001.004089 | PD-01112020-00148 | NORTHEAST | MUSKOGEE | 3137:AGENCY | AGENCY_3769 | 313769 | 2020-01-11 13:04 | 2020-01-11 14:20 | 75.8 | 1 | 1 | 75.8 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | MUSKOGEE | 111 S.CHEROKEE | CMI_NORMAL | NO | NO | NO | 860316 | 73957 | 33231 | 136 | 136 | 8.8107e-05 | 1.1624e-06 | 75.8 | 1 | 320 | Load | 147174 | Load | Tran3phPadWye | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-11 | 2020 |  | #N/A
J2001.004090 | PD-01112020-00151 | METRO WEST | WEST | 8359:YUKON | YUKON_5922 | 835922 | 2020-01-11 13:11 | 2020-01-11 13:45 | 33.9 | 1 | 1 | 33.9 | 12 | POOR CONNECTION | 50 | CONNECTOR | YUKON | 106 CORNWELL DR 7 | CMI_NORMAL | NO | NO | NO | 860316 | 128622 | 115890 | 6412 | 1635 | 3.9404e-05 | 1.1624e-06 | 33.9 | 1 | 310 | Customer | 24536 | Load | Tran1phOH | COLTON RACKLEY | 405-779-5033 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | #N/A
J2001.004091 | PD-01112020-00150 | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_631 | 730631 | 2020-01-11 13:12 | 2020-01-11 15:56 | 164.15 | 1 | 1 | 155.3333 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | SEMINOLE | 1100 KIMBERLY CT | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860316 | 114316 | 13591 | 4058 | 665 | 0.00018055 | 1.1624e-06 | 155.3333 | 1 | 320 | Customer | 13825 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004093 | PD-01112020-00152 | ARKANSAS | FORT SMITH | 9111:MASSARD | MASSARD_1129 | 911129 | 2020-01-11 13:16 | 2020-01-11 14:31 | 74.18 | 1 | 1 | 74.1833 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 100 S,200 W-S.74TH + ROGERS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 82157 | 61153 | 4983 | 356 | 8.6228e-05 | 1.1624e-06 | 74.1833 | 1 | 310 | Customer | 4836 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-11 | 2020 |  | Ark - Series 3
J2001.004098 | PD-01112020-00154 | METRO EAST | EAST | 8411:ACORN | ACORN_1172 | 841172 | 2020-01-11 13:31 | 2020-01-11 15:11 | 100.07 | 1 | 1 | 100.0667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | L15,B1-WOODLAND HILLS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 114316 | 71178 | 1790 | 699 | 0.00011631 | 1.1624e-06 | 100.0667 | 1 | 310 | Customer | 72910 | Load | Tran1phPad | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004107 | PD-01112020-00159 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4864 | 824864 | 2020-01-11 13:57 | 2020-01-11 16:21 | 143.78 | 1 | 1 | 21.0096 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 823 SW.24 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168043 | 148241 | 4189 | 2023 | 2.4421e-05 | 1.1624e-06 | 21.0096 | 1 | 310 | Customer | 17462 | Load | TranOpenDelta | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2021
J2001.004110 | PD-01112020-00166 | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6223 | 866223 | 2020-01-11 14:11 | 2020-01-11 15:06 | 55.37 | 1 | 1 | 55.3667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | Turtlewood Addition | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 114316 | 71178 | 7202 | 2230 | 6.4356e-05 | 1.1624e-06 | 55.3667 | 1 | 320 | Customer | 246649 | Load | Tran1phPad | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004111 | PD-01112020-00169 | ARKANSAS | POTEAU | 3514:HEAVENER | HEAVENER 22 | 351422 | 2020-01-11 14:21 | 2020-01-11 14:37 | 16.12 | 1 | 1 | 14.3333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | HEAVENER | 1.5MS ON OLD HWY 59 | CMI_NORMAL | NO | NO | NO | 860316 | 82157 | 13469 | 1766 | 1303 | 1.6661e-05 | 1.1624e-06 | 14.3333 | 1 | 310 | Load | 13655 | Load | Tran1phOH | TOBY C MEAD | 918-658-5596 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | OK - 2021
J2001.004112 | PD-01112020-00167 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7024 | 817024 | 2020-01-11 14:22 | 2020-01-11 16:03 | 101.05 | 1 | 1 | 6.6891 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 616 SE.72 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 158998 | 102083 | 9938 | 1752 | 7.7752e-06 | 1.1624e-06 | 6.6891 | 1 | 310 | Customer | 17377 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004113 | PD-01112020-00170 | METRO EAST | EAST | 8411:ACORN | ACORN_1172 | 841172 | 2020-01-11 14:25 | 2020-01-11 19:20 | 295.18 | 3 | 2 | 876.45 | 29 | TREES : GROW IN | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | 12001 NE.EXPRESSWAY | CMI_NORMAL | NO | NO | NO | 860316 | 114316 | 71178 | 1790 | 699 | 0.0010188 | 3.4871e-06 | 292.15 | 1 | 310 | Load | 11901 | Load | TranOpenDelta | TOMMY D ROBERTSON | 405-696-6476 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004115 | PD-01112020-00175 | NORTHWEST | ENID | 4240:DEER CREEK | DEER CREEK 48 | 424048 | 2020-01-11 14:32 | 2020-01-11 16:14 | 101.97 | 1 | 2 | 98.0333 | 22 | WIND | 17 | JUMPER | GARBER | 7.5N.GARBER | CMI_NORMAL | NO | NO | NO | 860316 | 53505 | 37572 | 621 | 476 | 0.00011395 | 1.1624e-06 | 98.0333 | 1 | 310 | Load | 6851 | Load | Tran3phWye | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | #N/A
J2001.004118 |  | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3729 | 833729 | 2020-01-11 14:33 | 2020-01-11 14:39 | 6.65 | 1 | 1 | 6.65 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1005 NW.87 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168043 | 148241 | 5758 | 1401 | 7.7297e-06 | 1.1624e-06 | 6.65 | 1 | 310 | Customer | 35597 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2021
J2001.004117 | PD-01112020-00172 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-01-11 14:34 | 2020-01-11 16:54 | 140.08 | 1 | 1 | 140.0833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | CHOCTAW | 2444 EISENHOUR DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 114316 | 71178 | 11619 | 3533 | 0.00016283 | 1.1624e-06 | 140.0833 | 1 | 310 | Customer | 57449 | Load | Tran1phOH | STEVEN CASKEY | 405-777-8855 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004119 |  | METRO EAST | EAST | 8411:ACORN | ACORN_1172 | 841172 | 2020-01-11 14:36 | 2020-01-11 14:41 | 4.62 | 1 | 1 | 4.6167 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 5401 NE.122ND | CMI_MOMENTARY | YES | NO | NO | 860316 | 114316 | 71178 | 1790 | 699 | 5.3662e-06 | 1.1624e-06 | 4.6167 | 1 | 310 | Customer | 5565 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004120 |  | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3729 | 833729 | 2020-01-11 14:40 | 2020-01-11 14:42 | 2.08 | 1 | 1 | 2.0833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1005 NW.87 | CMI_MOMENTARY | YES | NO | NO | 860316 | 168043 | 148241 | 5758 | 1401 | 2.4216e-06 | 1.1624e-06 | 2.0833 | 1 | 310 | Customer | 35597 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2021
J2001.004125 | PD-01112020-00173 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4124 | 814124 | 2020-01-11 14:40 | 2020-01-11 15:57 | 76.88 | 1 | 2 | 22.3319 | 27 | TREE:NON PREVENTABLE | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 414 SW.40 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860316 | 158998 | 102083 | 5802 | 2010 | 2.5958e-05 | 1.1624e-06 | 22.3319 | 1 | 321 | Customer | 46935 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | #N/A
J2001.004126 | PD-01112020-00174 | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-01-11 14:44 | 2020-01-11 15:37 | 52.68 | 1 | 1 | 52.6833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 9112 SE 74TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 158998 | 56915 | 4204 | 974 | 6.1237e-05 | 1.1624e-06 | 52.6833 | 1 | 310 | Customer | 71257 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004127 |  | METRO EAST | EAST | 8411:ACORN | ACORN_1172 | 841172 | 2020-01-11 14:57 | 2020-01-11 20:01 | 304.68 | 11 | 1 | 2868.9833 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | .5ME COLTRANE/N.NE108 | CMI_NORMAL | NO | NO | NO | 860316 | 114316 | 71178 | 1790 | 699 | 0.0033348 | 1.2786e-05 | 260.8167 | 1 | 310 | Mainline | 4649 | Switch | SwitchOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004132 | PD-01112020-00177 | METRO NORTH | NORTH | 8464:BRYANT | BRYANT_6421 | 846421 | 2020-01-11 15:28 | 2020-01-11 16:04 | 36.25 | 1 | 1 | 7.964 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 14311 SMITHURST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168043 | 148241 | 1894 | 1265 | 9.257e-06 | 1.1624e-06 | 7.964 | 1 | 310 | Customer | 61745 | Load | Tran1phPad | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004137 | PD-01112020-00180 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1122 | 511122 | 2020-01-11 15:37 | 2020-01-11 16:36 | 59.22 | 1 | 1 | 49.3167 | 25 | LIGHTNING | 20 | FUSE BARREL | DICKSON | .2E GENE AUTRY RD .2N .1E | CMI_NORMAL | NO | NO | NO | 860316 | 77559 | 23571 | 2205 | 1205 | 5.7324e-05 | 1.1624e-06 | 49.3167 | 1 | 320 | Customer | 29623 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004143 | PD-01112020-00182 | SOUTHERN | ARDMORE | 5108:WOLF CREEK | WOLF CREEK 22 | 510822 | 2020-01-11 16:08 | 2020-01-11 16:20 | 11.67 | 1 | 1 | 127.3843 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | WILSON | CONOCO/O L GRAY RD .1S .1W | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77559 | 23571 | 448 | 236 | 0.00014807 | 1.1624e-06 | 127.3843 | 1 | 310 | Load | 198600 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004153 | PD-01112020-00185 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7424 | 847424 | 2020-01-11 16:49 | 2020-01-11 17:42 | 52.55 | 1 | 1 | 6.1831 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1212 NE.39 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168043 | 148241 | 6152 | 2197 | 7.187e-06 | 1.1624e-06 | 6.1831 | 1 | 310 | Customer | 5976 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2020
J2001.004154 | PD-01112020-00187 | SOUTHERN | MADILL | 5906:TISHOMINGO | TISHOMINGO_621 | 590621 | 2020-01-11 16:50 | 2020-01-11 17:06 | 15.53 | 1 | 1 | 15.5333 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | TISHOMINGO | S MURRAY + WILSON | CMI_NORMAL | NO | NO | NO | 860316 | 77559 | 7203 | 967 | 916 | 1.8055e-05 | 1.1624e-06 | 15.5333 | 1 | 320 | Load | 28977 | Load | Tran3phWye | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2021
J2001.004161 | PD-01112020-00190 | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2922 | 812922 | 2020-01-11 17:03 | 2020-01-11 19:31 | 147.72 | 45 | 50 | 6075 | 4 | DETERIORATION | 17 | JUMPER | OKLAHOMA CITY | SW36 + LIBERTY | CMI_NORMAL | NO | NO | NO | 860316 | 158998 | 102083 | 6376 | 1136 | 0.0070614 | 5.2306e-05 | 135 | 1 | 310 | Tap | 21621 | Fuse | FuseOH | DENNY J MORGAN | 405-501-1556 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | #N/A
J2001.004162 | PD-01112020-00191 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1424 | 311424 | 2020-01-11 17:13 | 2020-01-11 20:12 | 179.45 | 1 | 1 | 111.7167 | 4 | DETERIORATION | 50 | CONNECTOR | MUSKOGEE | 1/4MN OF HILLTOP ON N69 | CMI_NORMAL | NO | NO | NO | 860316 | 73957 | 33231 | 4561 | 798 | 0.00012986 | 1.1624e-06 | 111.7167 | 1 | 310 | Load | 20812 | Load | Tran1phOH | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | OK - 2020
J2001.004175 | PD-01112020-00195 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2224 | 832224 | 2020-01-11 18:03 | 2020-01-11 18:19 | 15.72 | 1 | 1 | 15.7167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 3204 NESBITT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168058 | 148255 | 9168 | 1427 | 1.8268e-05 | 1.1624e-06 | 15.7167 | 1 | 310 | Customer | 8562 | Load | TranOpenDelta | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | #N/A
J2001.004176 |  | ARKANSAS | POTEAU | 3514:HEAVENER | HEAVENER 22 | 351422 | 2020-01-11 18:06 | 2020-01-11 19:40 | 94.22 | 89 | 0 | 726.8333 | 4 | DETERIORATION | 27 | CUTOUT | HEAVENER | E AVE C + E THIRD | CMI_NORMAL | NO | NO | NO | 860316 | 82163 | 13472 | 1767 | 1304 | 0.00084484 | 0.00010345 | 8.1667 | 1 | 0 | Mainline | 27155 | Fuse | FuseOH | TOBY C MEAD | 918-658-5596 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-11 | 2020 |  | OK - 2021
J2001.004181 | PD-01112020-00196 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-01-11 18:46 | 2020-01-11 19:45 | 59.3 | 1 | 1 | 59.3 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | CHOCTAW | 2444 EISENHOUR DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 114333 | 71184 | 11623 | 3534 | 6.8928e-05 | 1.1624e-06 | 59.3 | 1 | 310 | Customer | 57449 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004182 | PD-01112020-00197 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-11 18:55 | 2020-01-11 21:31 | 155.9 | 1 | 1 | 155.9 | 29 | TREES : GROW IN | 37 | CONDUCTOR PRIMARY - OH | WINSLOW | 22785 CARTER RD | CMI_NORMAL | NO | NO | NO | 860316 | 82163 | 61155 | 3788 | 1204 | 0.00018121 | 1.1624e-06 | 155.9 | 1 | 311 | Customer | 16517 | Load | Tran1phOH | TRAVIS EARNHART | 479-462-5659 | [5 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-11 | 2020 |  | Ark - Series 2
J2001.004183 |  | SOUTHERN | ARDMORE | 5108:WOLF CREEK | WOLF CREEK 22 | 510822 | 2020-01-11 19:05 | 2020-01-11 19:23 | 18.1 | 1 | 1 | 18.1 | 1 | CANCELLED | 57 | CANCELLED | WILSON | CONOCO/O L GRAY RD .1S .1W | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77561 | 23571 | 448 | 236 | 2.1039e-05 | 1.1624e-06 | 18.1 | 1 | 310 | Load | 198600 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004201 |  | SOUTHERN | PAULS VALLEY | 5620:PRAIRIE POINT | PRAIRIE_POINT_2021 | 562021 | 2020-01-11 21:14 | 2020-01-12 02:27 | 312.3 | 2 | 3 | 581.75 | 11 | OVERLOAD | 2 | TRANSFORMER OH | ELMORE CITY | CARTER + MO ST | CMI_NORMAL | NO | NO | NO | 860316 | 77561 | 6204 | 607 | 569 | 0.00067621 | 2.3247e-06 | 290.875 | 1 | 310 | Load | 7451 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2021
J2001.004203 | PD-01112020-00203 | SOUTHERN | PAULS VALLEY | 5620:PRAIRIE POINT | PRAIRIE_POINT_2021 | 562021 | 2020-01-11 21:33 | 2020-01-12 02:15 | 281.7 | 2 | 2 | 543.65 | 11 | OVERLOAD | 2 | TRANSFORMER OH | ELMORE CITY | CARTER DR AT SOHIO AVE -ELMORC | CMI_NORMAL | NO | NO | NO | 860316 | 77561 | 6204 | 607 | 569 | 0.00063192 | 2.3247e-06 | 271.825 | 1 | 310 | Secondary | 4147 | Load | Tran1phOH | ROBERT J BEARDSLEE | 580-618-2506 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2021
J2001.004204 | PD-01112020-00204 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1225 | 831225 | 2020-01-11 21:40 | 2020-01-12 | 139.68 | 20 | 24 | 2726.3333 | 22 | WIND | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 5200 N.HALES DR | CMI_NORMAL | NO | NO | NO | 860316 | 168058 | 148255 | 7738 | 882 | 0.003169 | 2.3247e-05 | 136.3167 | 1 | 311 | Load | 21346 | Load | TranOpenDelta | TONY J ILG | 405-714-7441 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2022
J2001.004215 | PD-01112020-00205 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2263 | 852263 | 2020-01-11 22:37 | 2020-01-12 01:31 | 174.33 | 1 | 1 | 171.9667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 4118 N YOUNGS DR | CMI_NORMAL | NO | NO | NO | 860316 | 114333 | 71184 | 11623 | 1533 | 0.00019989 | 1.1624e-06 | 171.9667 | 1 | 310 | Load | 68461 | Load | Tran1phOH | JEREMIAH D WALKER | 405-974-0464 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | OK - 2021
J2001.004230 | PD-01122020-00001 | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-01-11 23:56 | 2020-01-12 04:55 | 299.2 | 25 | 33 | 7292.9167 | 22 | WIND | 17 | JUMPER | OKLAHOMA CITY | NW.7 AND GREENVALE | CMI_NORMAL | NO | NO | NO | 860316 | 128627 | 115894 | 3405 | 2036 | 0.008477 | 2.9059e-05 | 291.7167 | 1 | 310 | Mainline | 11305 | Fuse | FuseRiser | DENNY J MORGAN | 405-501-1556 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-11 | 2020 |  | #N/A
J2001.004231 |  | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-01-12 00:06 | 2020-01-12 00:13 | 6.27 | 1 | 1 | 6.2667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ADA | 1001 E.GARDENIA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77561 | 11504 | 2518 | 1090 | 7.2841e-06 | 1.1624e-06 | 6.2667 | 1 | 310 | Customer | 10644 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-12 | 2020 |  | #N/A
J2001.004242 | PD-01122020-00005 | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2124 | 332124 | 2020-01-12 01:18 | 2020-01-12 04:56 | 218.32 | 2 | 3 | 418.0833 | 4 | DETERIORATION | 27 | CUTOUT | FORT GIBSON | FT GIBSON OK 74434 | CMI_NORMAL | NO | NO | NO | 860316 | 73958 | 33231 | 3333 | 1220 | 0.00048596 | 2.3247e-06 | 209.0417 | 1 | 310 | Load | 7845 | Load | Tran1phOH | BRUCE A PAULUS | 479-220-7661 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-12 | 2020 |  | #N/A
J2001.004264 | PD-01122020-00008 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3023 | 743023 | 2020-01-12 04:35 | 2020-01-12 06:51 | 136 | 23 | 10 | 3044.8167 | 4 | DETERIORATION | 20 | FUSE BARREL | BETHEL ACRES | .5MS BETHEL SCHOOL | CMI_NORMAL | NO | NO | NO | 860316 | 114333 | 22095 | 6640 | 1137 | 0.0035392 | 2.6734e-05 | 132.3833 | 1 | 310 | Mainline | 1219 | Fuse | FuseOH | STEVEN CASKEY | 405-777-8855 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | OK - 2021
J2001.004273 | PD-01122020-00010 | METRO SOUTH | SOUTH | 5607:ROSEDALE TAP | ROSEDALE_TAP_724 | 560724 | 2020-01-12 05:12 | 2020-01-12 11:18 | 366.02 | 67 | 28 | 24404.75 | 4 | DETERIORATION | 27 | CUTOUT | BYARS | NW CORNER BRUAMS & 140TH | CMI_NORMAL | NO | NO | NO | 860316 | 159005 | 56915 | 987 | 339 | 0.028367 | 7.7878e-05 | 364.25 | 1 | 310 | Mainline | 208414 | Recloser | Rec3phHydralic | DENNY J MORGAN | 405-501-1556 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-12 | 2020 |  | OK - 2021
J2001.004278 | PD-01122020-00011 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3925 | 833925 | 2020-01-12 05:40 | 2020-01-12 07:03 | 82.6 | 1 | 1 | 82.6 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 4624 NW.59 | CMI_NORMAL | NO | NO | NO | 860316 | 168058 | 148255 | 7848 | 2182 | 9.6011e-05 | 1.1624e-06 | 82.6 | 1 | 310 | Customer | 23737 | Load | Tran1phOH | COLTON RACKLEY | 405-779-5033 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | OK - 2022
J2001.004287 |  | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2223 | 882223 | 2020-01-12 06:42 | 2020-01-12 11:12 | 270.38 | 1 | 2 | 270.3833 | 4 | DETERIORATION | 27 | CUTOUT | EDMOND | 5300 INDIAN-HILL RD | CMI_NORMAL | NO | NO | NO | 860316 | 168058 | 19803 | 5386 | 1203 | 0.00031428 | 1.1624e-06 | 270.3833 | 1 | 310 | Customer | 57759 | Load | Tran1phOH | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004293 | PD-01122020-00015 | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2921 | 812921 | 2020-01-12 07:12 | 2020-01-12 09:56 | 163.85 | 19 | 15 | 3038.4167 | 22 | WIND | 17 | JUMPER | OKLAHOMA CITY | SW 41 + INDEPENDENCE | CMI_NORMAL | NO | NO | NO | 860316 | 159005 | 102090 | 6376 | 1481 | 0.0035317 | 2.2085e-05 | 159.9167 | 1 | 310 | Tap | 17542 | Fuse | FuseOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-12 | 2020 |  | #N/A
J2001.004292 | PD-01122020-00014 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2222 | 832222 | 2020-01-12 07:20 | 2020-01-12 09:42 | 141.95 | 1 | 2 | 141.95 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2247 NW.42 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168058 | 148255 | 9168 | 1556 | 0.000165 | 1.1624e-06 | 141.95 | 1 | 320 | Customer | 14845 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-12 | 2020 |  | OK - 2022
J2001.004300 |  | SOUTHERN | DURANT | 5504:BUTTERFIELD | BUTTERFIELD_431 | 550431 | 2020-01-12 08:07 | 2020-01-12 08:07 | 0.02 | 96 | 0 | 1.6 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | DURANT | 2401 CALE SWITCH RD | CMI_MOMENTARY | YES | NO | NO | 860316 | 77561 | 15479 | 3484 | 96 | 1.8598e-06 | 0.00011159 | 0.016667 | 1 | 0 | Feeder | BUTTEFLD_431 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004304 | PD-01122020-00019 | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2923 | 812923 | 2020-01-12 08:22 | 2020-01-12 10:38 | 135.62 | 48 | 27 | 4540 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | 1150 W OF MAY SS SW59 | CMI_NORMAL | NO | NO | NO | 860316 | 159005 | 102090 | 6376 | 1633 | 0.0052771 | 5.5793e-05 | 94.5833 | 1 | 310 | Mainline | 27214 | Fuse | FuseRiser | BAD ORDER PRIMARY RES COORD | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-12 | 2020 |  | #N/A
J2001.004303 |  | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2923 | 812923 | 2020-01-12 08:22 | 2020-01-12 08:22 | 0 | 1633 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 6401 MCLEMORE | CMI_MOMENTARY | YES | NO | NO | 860316 | 159005 | 102090 | 6376 | 1633 | 0 | 0.0018981 | 0 | 1 | 0 | Feeder | SW 64TH_2923 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-12 | 2020 |  | #N/A
J2001.004306 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6922 | 846922 | 2020-01-12 08:29 | 2020-01-12 08:48 | 19.02 | 1 | 1 | 19.0167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1001 NW.105 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168058 | 148255 | 7717 | 1486 | 2.2104e-05 | 1.1624e-06 | 19.0167 | 1 | 310 | Customer | 49073 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004310 | PD-01122020-00029 | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1623 | 581623 | 2020-01-12 08:37 | 2020-01-12 10:58 | 141.07 | 1 | 1 | 133.1333 | 4 | DETERIORATION | 50 | CONNECTOR | ADA | 2ND+3RD PLS W OF OAK ON KINGS | CMI_NORMAL | NO | NO | NO | 860316 | 77561 | 11504 | 3454 | 1649 | 0.00015475 | 1.1624e-06 | 133.1333 | 1 | 310 | Customer | 1580 | Load | TranOHDeltaSplitBank | JORDAN HERBERT-BLUE | 918-839-1152 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004311 | PD-01122020-00021 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1222 | 831222 | 2020-01-12 08:39 | 2020-01-12 14:10 | 330.95 | 5 | 14 | 478.6667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 2207 DAWN-MARIE DR | CMI_NORMAL | NO | NO | NO | 860316 | 168058 | 148255 | 7738 | 1009 | 0.00055638 | 5.8118e-06 | 95.7333 | 1 | 310 | Load | 12946 | Load | TranOpenDelta | TOMMY D ROBERTSON | 405-696-6476 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | OK - 2021
J2001.004315 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1225 | 831225 | 2020-01-12 09:01 | 2020-01-12 09:08 | 6.88 | 1 | 1 | 6.8833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 5200 N.HALES DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168058 | 148255 | 7738 | 882 | 8.0009e-06 | 1.1624e-06 | 6.8833 | 1 | 310 | Customer | 21346 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | OK - 2022
J2001.004318 | PD-01122020-00026 | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1722 | 861722 | 2020-01-12 09:19 | 2020-01-12 11:11 | 112.15 | 1 | 2 | 112.15 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4116 CUNNINGHAM DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 114333 | 71184 | 6938 | 1787 | 0.00013036 | 1.1624e-06 | 112.15 | 1 | 320 | Customer | 52340 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-12 | 2020 |  | #N/A
J2001.004326 |  | METRO SOUTH | SOUTH | 5607:ROSEDALE TAP | ROSEDALE_TAP_724 | 560724 | 2020-01-12 09:32 | 2020-01-12 11:27 | 114.67 | 1 | 1 | 114.6667 | 4 | DETERIORATION | 27 | CUTOUT | BYARS | BYARS 2N,.3E,.2N,.1E | CMI_NORMAL | NO | NO | NO | 860316 | 159005 | 56915 | 987 | 339 | 0.00013328 | 1.1624e-06 | 114.6667 | 1 | 310 | Customer | 17586 | Load | Tran1phOH | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-12 | 2020 |  | OK - 2021
J2001.004330 |  | METRO EAST | EAST | 8542:RENO | RENO_4224 | 854224 | 2020-01-12 09:46 | 2020-01-12 11:27 | 101.48 | 1 | 1 | 90.6 | 4 | DETERIORATION | 27 | CUTOUT | DEL CITY | 3101 NE.4 | CMI_NORMAL | NO | NO | NO | 860316 | 114333 | 71184 | 5212 | 1221 | 0.00010531 | 1.1624e-06 | 90.6 | 1 | 310 | Customer | 973 | Load | Tran3phWye | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | OK - 2022
J2001.004335 |  | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5431 | 865431 | 2020-01-12 09:56 | 2020-01-12 12:45 | 169.45 | 26 | 23 | 4028.5 | 4 | DETERIORATION | 12 | POLE | MOORE | TURNER AV + NE.2 | CMI_PLANNED | YES | NO | NO | 860316 | 159005 | 102090 | 9806 | 1377 | 0.0046826 | 3.0221e-05 | 154.9423 | 1 | 308 | Mainline | 31731 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004339 | PD-01122020-00033 | METRO WEST | WEST | 8359:YUKON | YUKON_5922 | 835922 | 2020-01-12 10:08 | 2020-01-12 11:03 | 55.4 | 1 | 1 | 55.4 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | YUKON | 106 CORNWELL DR 7 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 128627 | 115894 | 6413 | 1635 | 6.4395e-05 | 1.1624e-06 | 55.4 | 1 | 310 | Customer | 24536 | Load | Tran1phOH | COLTON RACKLEY | 405-779-5033 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-12 | 2020 |  | #N/A
J2001.004342 | PD-01122020-00036 | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4529 | 824529 | 2020-01-12 10:10 | 2020-01-12 12:26 | 136.08 | 62 | 23 | 7378 | 22 | WIND | 17 | JUMPER | OKLAHOMA CITY | 4000 E CO LN S0F RENO | CMI_NORMAL | NO | NO | NO | 860316 | 128627 | 115894 | 3405 | 257 | 0.0085759 | 7.2067e-05 | 119 | 1 | 310 | Mainline | 24967 | Fuse | FuseOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004343 | PD-01122020-00037 | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_626 | 550626 | 2020-01-12 10:24 | 2020-01-12 12:54 | 150.37 | 1 | 1 | 150.3667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DURANT | 19TH + MISS K126 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77561 | 15479 | 6734 | 1000 | 0.00017478 | 1.1624e-06 | 150.3667 | 1 | 310 | Customer | 15453 | Load | Tran1phPad | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004359 | PD-01122020-00040 | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_649 | 890649 | 2020-01-12 11:31 | 2020-01-12 12:26 | 54.53 | 1 | 1 | 54.5333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OAKWOOD | OAKWOOD >MICHIGAN,CHERRY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 128627 | 12733 | 1365 | 278 | 6.3388e-05 | 1.1624e-06 | 54.5333 | 1 | 310 | Customer | 38623 | Load | Tran1phOH | BRANDON H SMITH | 405-371-4294 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004361 | PD-01122020-00041 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_528 | 510528 | 2020-01-12 11:32 | 2020-01-12 12:49 | 76.92 | 6 | 8 | 442.4 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ARDMORE | 1217.5 CULBERTSON | CMI_NORMAL | NO | NO | NO | 860316 | 77561 | 23571 | 4770 | 1118 | 0.00051423 | 6.9742e-06 | 73.7333 | 1 | 310 | Secondary | 14040 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-12 | 2020 |  | #N/A
J2001.004366 | PD-01122020-00042 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-12 11:52 | 2020-01-12 13:24 | 91.73 | 1 | 1 | 91.7333 | 25 | LIGHTNING | 2 | TRANSFORMER OH | MOUNTAINBURG | 407 1/2 COZY COVE | CMI_NORMAL | NO | NO | NO | 860316 | 82163 | 61155 | 3788 | 1204 | 0.00010663 | 1.1624e-06 | 91.7333 | 1 | 310 | Load | 196757 | Load | Tran1phOH | TRAVIS EARNHART | 479-462-5659 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-12 | 2020 |  | Ark - Series 2
J2001.004371 | PD-01122020-00047 | SOUTHERN | DURANT | 5511:BOKCHITO | BOKCHITO 21 | 551121 | 2020-01-12 12:16 | 2020-01-12 13:41 | 84.75 | 1 | 1 | 84.75 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | BOKCHITO | .5BLW E DAVIS ON MAIN BOKCHITO | CMI_NORMAL | NO | NO | NO | 860316 | 77561 | 15479 | 669 | 669 | 9.851e-05 | 1.1624e-06 | 84.75 | 1 | 320 | Customer | 22054 | Load | TranOpenDelta | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Weather | N | DISTRIBUTION | 34.5/19.9kv | 2020-01-12 | 2020 |  | #N/A
J2001.004374 | PD-01122020-00050 | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_521 | 890521 | 2020-01-12 12:20 | 2020-01-12 15:55 | 215.13 | 1 | 1 | 215.1333 | 5 | ELECTRICAL TRACKING | 21 | FUSE - TRANSFORMER | EL RENO | 215 N.HOFF | CMI_NORMAL | NO | NO | NO | 860316 | 128627 | 12733 | 6935 | 2211 | 0.00025006 | 1.1624e-06 | 215.1333 | 1 | 310 | Customer | 50879 | Load | Tran1phOH | BRANDON H SMITH | 405-371-4294 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004378 | PD-01122020-00049 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7024 | 817024 | 2020-01-12 12:25 | 2020-01-12 14:16 | 110.57 | 1 | 2 | 101.9333 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 6420 S.PHILLIPS | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860316 | 159005 | 102090 | 9938 | 1752 | 0.00011848 | 1.1624e-06 | 101.9333 | 1 | 310 | Customer | 25533 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004382 | PD-01122020-00058 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6522 | 836522 | 2020-01-12 12:46 | 2020-01-12 14:15 | 88.8 | 1 | 1 | 42.7485 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 8308 LOWERY LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 128627 | 115894 | 7418 | 1861 | 4.9689e-05 | 1.1624e-06 | 42.7485 | 1 | 310 | Customer | 27533 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | OK - 2021
J2001.004387 | PD-01122020-00056 | METRO EAST | SEMINOLE | 7505:WEWOKA | WEWOKA 21 | 750521 | 2020-01-12 12:46 | 2020-01-12 14:02 | 75.73 | 2 | 2 | 127.1 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | WEWOKA | 7O9 S MEKUSUKEY | CMI_NORMAL | NO | NO | NO | 860316 | 114333 | 13596 | 2469 | 1282 | 0.00014774 | 2.3247e-06 | 63.55 | 1 | 310 | Secondary | 11305 | Load | Tran1phOH | BRADY A HUFF | 405-519-0701 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-12 | 2020 |  | OK - 2021
J2001.004381 | PD-01122020-00054 | SOUTHERN | DURANT | 5505:DURANT | DURANT 22 | 550522 | 2020-01-12 12:46 | 2020-01-12 15:08 | 141.65 | 1 | 1 | 141.65 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DURANT | 122 E MAIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77561 | 15479 | 1317 | 797 | 0.00016465 | 1.1624e-06 | 141.65 | 1 | 310 | Customer | 781 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004388 | PD-01122020-00060 | METRO EAST | SEMINOLE | 7312:JUMPER CREEK | JUMPER_CREEK_1225 | 731225 | 2020-01-12 12:56 | 2020-01-12 17:18 | 262.35 | 2 | 4 | 523.0667 | 4 | DETERIORATION | 27 | CUTOUT | KONAWA | 2 SEC LN W VAMSA CEMET | CMI_NORMAL | NO | NO | NO | 860316 | 114333 | 13596 | 1216 | 331 | 0.00060799 | 2.3247e-06 | 261.5333 | 1 | 310 | Tap | 2500 | Fuse | FuseOH | JEREMIAH D WALKER | 405-974-0464 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-12 | 2020 |  | OK - 2021
J2001.004392 | PD-01122020-00064 | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_621 | 460621 | 2020-01-12 13:22 | 2020-01-12 16:02 | 160.23 | 1 | 2 | 147.2 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | WOODWARD | 1711 2nd St | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860316 | 53506 | 10416 | 5680 | 787 | 0.0001711 | 1.1624e-06 | 147.2 | 1 | 321 | Customer | 11562 | Load | Tran1phOH | HAYDEN BIERIG | 580-748-0538 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-12 | 2020 |  | #N/A
J2001.004397 | PD-01122020-00065 | SOUTHERN | HEALDTON | 5122:DILLARD | DILLARD_2223 | 512223 | 2020-01-12 13:30 | 2020-01-12 14:54 | 83.78 | 1 | 1 | 83.7833 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | HEALDTON | HERRELL LSE | CMI_NORMAL | NO | NO | NO | 860316 | 77561 | 6791 | 1186 | 338 | 9.7387e-05 | 1.1624e-06 | 83.7833 | 1 | 310 | Load | 4349 | Load | Tran3phWye | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004398 | PD-01122020-00062 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1926 | 851926 | 2020-01-12 13:34 | 2020-01-12 15:15 | 100.8 | 1 | 1 | 100.8 | 23 | CUSTOMER EQUIPMENT | 15 | METER - SECONDARY | MIDWEST CITY | 1209 N.LLOYD DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 114333 | 71184 | 12434 | 2126 | 0.00011717 | 1.1624e-06 | 100.8 | 1 | 310 | Customer | 26041 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | OK - 2021
J2001.004418 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6965 | 846965 | 2020-01-12 15:41 | 2020-01-12 15:41 | 0 | 46 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 401 NE 122ND ST | CMI_MOMENTARY | YES | NO | NO | 860316 | 168058 | 148255 | 7717 | 46 | 0 | 5.3469e-05 | 0 | 1 | 0 | Feeder | MEMORIAL_6965 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004419 | PD-01122020-00072 | SOUTHERN | HEALDTON | 5122:DILLARD | DILLARD_2222 | 512222 | 2020-01-12 15:41 | 2020-01-12 15:55 | 13.77 | 1 | 1 | 13.7667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | WILSON | 509 W ADA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77561 | 6791 | 1186 | 697 | 1.6002e-05 | 1.1624e-06 | 13.7667 | 1 | 321 | Customer | 7595 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004426 | PD-01122020-00075 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4823 | 824823 | 2020-01-12 15:55 | 2020-01-12 17:52 | 117.17 | 1 | 2 | 105.15 | 22 | WIND | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | 2930 SW.16 | CMI_NORMAL | NO | NO | NO | 860316 | 168058 | 148255 | 4189 | 1795 | 0.00012222 | 1.1624e-06 | 105.15 | 1 | 310 | Customer | 57179 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | OK - 2021
J2001.004423 | PD-01122020-00073 | METRO EAST | CHANDLER | 7117:JACKTOWN | JACKTOWN_1743 | 711743 | 2020-01-12 15:57 | 2020-01-12 17:10 | 73.02 | 1 | 1 | 67.3833 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | MEEKER | % RT 1 BOX 97 | CMI_NORMAL | NO | NO | NO | 860316 | 114333 | 7458 | 1011 | 183 | 7.8324e-05 | 1.1624e-06 | 67.3833 | 1 | 310 | Load | 9938 | Load | TranOH3phDelta | SCOTT C PERRY | 405-258-6044 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004425 | PD-01122020-00076 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5024 | 865024 | 2020-01-12 16:05 | 2020-01-12 21:31 | 325.78 | 1 | 1 | 30.0167 | 22 | WIND | 31 | CONDUCTOR SERVICE - OH | MIDWEST CITY | 515 E.ERCOUPE | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860316 | 114333 | 71184 | 8622 | 1072 | 3.489e-05 | 1.1624e-06 | 30.0167 | 1 | 310 | Customer | 32989 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | OK - 2022
J2001.004428 | PD-01122020-00077 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6121 | 836121 | 2020-01-12 16:32 | 2020-01-12 18:06 | 93.57 | 1 | 1 | 91.4333 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | OKLAHOMA CITY | 1115 NW.34 | CMI_NORMAL | NO | NO | NO | 860316 | 168058 | 148255 | 11102 | 1638 | 0.00010628 | 1.1624e-06 | 91.4333 | 1 | 320 | Customer | 1925 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | OK - 2021
J2001.004432 | PD-01122020-00078 | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8131 | 838131 | 2020-01-12 16:36 | 2020-01-12 21:16 | 279.52 | 55 | 36 | 9138.25 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | MEADOWS AT RIVER BEND | CMI_NORMAL | NO | NO | NO | 860316 | 128627 | 115894 | 8953 | 1828 | 0.010622 | 6.393e-05 | 166.15 | 1 | 310 | Mainline | 113713 | Fuse | FuseRiser | BEAU S HUDSON | 405-306-8284 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004431 | PD-01122020-00080 | NORTHEAST | MUSKOGEE | 3327:VIAN | VIAN 22 | 332722 | 2020-01-12 16:39 | 2020-01-12 18:52 | 132.78 | 1 | 1 | 132.7833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | VIAN | VIAN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 73958 | 33231 | 779 | 779 | 0.00015434 | 1.1624e-06 | 132.7833 | 1 | 310 | Customer | 9749 | Load | Tran1phOH | JAMES MCDONALD | 405-361-7186 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-12 | 2020 |  | OK - 2021
J2001.004435 | PD-01122020-00079 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2029 | 862029 | 2020-01-12 16:47 | 2020-01-12 22:26 | 338.8 | 1 | 1 | 23.5153 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 714 SE.21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 159005 | 102090 | 4741 | 982 | 2.7333e-05 | 1.1624e-06 | 23.5153 | 1 | 310 | Customer | 7110 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004439 | PD-01122020-00082 | METRO EAST | SEMINOLE | 7512:CROMWELL | CROMWELL 47 | 751247 | 2020-01-12 16:56 | 2020-01-12 18:48 | 111.77 | 1 | 2 | 21.9167 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | WEWOKA | 1MS I40 3/4MW HWY 56 1650 S | CMI_NORMAL | NO | NO | NO | 860316 | 114333 | 13596 | 309 | 309 | 2.5475e-05 | 1.1624e-06 | 21.9167 | 1 | 310 | Load | 20905 | Load | Tran1phOH | BRADY A HUFF | 405-519-0701 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-12 | 2020 |  | #N/A
J2001.004441 | PD-01122020-00083 | SOUTHERN | SULPHUR | 5705:SULPHUR | SULPHUR_521 | 570521 | 2020-01-12 17:06 | 2020-01-12 19:49 | 162.93 | 1 | 1 | 162.9333 | 13 | PREMATURE FAILURE | 35 | CONDUCTOR PRIMARY - UG FEEDER | SULPHUR | 914 E TULSA | CMI_NORMAL | NO | NO | NO | 860316 | 77561 | 6809 | 3630 | 755 | 0.00018939 | 1.1624e-06 | 162.9333 | 1 | 310 | Customer | 15594 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004443 | PD-01122020-00084 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_724 | 870724 | 2020-01-12 17:20 | 2020-01-12 19:17 | 117.28 | 1 | 2 | 117.2833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | ALAMEDA SQ. SHOPPING CENTER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 159005 | 56915 | 11831 | 2411 | 0.00013633 | 1.1624e-06 | 117.2833 | 1 | 310 | Customer | 74970 | Load | Tran3phPadWye | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004446 | PD-01122020-00086 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6023 | 836023 | 2020-01-12 17:38 | 2020-01-12 21:28 | 229.98 | 1 | 1 | 229.9833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | BETHANY | 6907 NW.52 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 128627 | 115894 | 5504 | 1479 | 0.00026732 | 1.1624e-06 | 229.9833 | 1 | 310 | Customer | 8627 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-12 | 2020 |  | OK - 2022
J2001.004448 | PD-01122020-00087 | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_647 | 890647 | 2020-01-12 17:40 | 2020-01-12 20:51 | 191.47 | 4 | 4 | 765.8667 | 25 | LIGHTNING | 34 | CONDUCTOR SECONDARY - OH | LONGDALE | ANCHORAGE TR PK | CMI_NORMAL | NO | NO | NO | 860316 | 128627 | 12733 | 1365 | 1069 | 0.00089022 | 4.6495e-06 | 191.4667 | 1 | 310 | Secondary | 50223 | Load | Tran1phOH | BRANDON H SMITH | 405-371-4294 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004474 | PD-01122020-00091 | NORTHWEST | ENID | 4119:GLENWOOD | GLENWOOD_1922 | 411922 | 2020-01-12 18:46 | 2020-01-12 20:56 | 129.55 | 1 | 2 | 122.6833 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | ENID | 4716 MANCHESTER DR ENID | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860316 | 53506 | 37572 | 5413 | 1560 | 0.0001426 | 1.1624e-06 | 122.6833 | 1 | 310 | Customer | 12732 | Load | Tran1phPad | C-TSENID1 TOM SEEDORF | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004538 | PD-01122020-00093 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_526 | 510526 | 2020-01-12 20:01 | 2020-01-12 22:04 | 122.72 | 2 | 3 | 223.1167 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | ARDMORE | 712 C NW. | CMI_NORMAL | NO | NO | NO | 860316 | 77561 | 23571 | 4770 | 1619 | 0.00025934 | 2.3247e-06 | 111.5583 | 1 | 310 | Secondary | 3721 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-12 | 2020 |  | OK - 2020
J2001.004585 |  | NORTHEAST | SAPULPA | 3220:KELLYVILLE | KELLYVILLE_2029 | 322029 | 2020-01-12 20:27 | 2020-01-12 20:40 | 13.02 | 1 | 1 | 13.0167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SAPULPA | 3 W ON HEYBURN + 1/4 N + 1/8E | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 73958 | 40727 | 2550 | 970 | 1.513e-05 | 1.1624e-06 | 13.0167 | 1 | 310 | Load | 43894 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | OK - 2022
J2001.004603 | PD-01122020-00099 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2227 | 832227 | 2020-01-12 20:42 | 2020-01-13 02:35 | 352.88 | 1 | 1 | 115.3 | 22 | WIND | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 2320 NW.32 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860316 | 168058 | 148255 | 9168 | 1045 | 0.00013402 | 1.1624e-06 | 115.3 | 1 | 310 | Customer | 3745 | Load | Tran1phOH | DENNY J MORGAN | 405-501-1556 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-12 | 2020 |  | OK - 2022
J2001.004614 | PD-01122020-00100 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4821 | 824821 | 2020-01-12 20:56 | 2020-01-12 23:43 | 166.77 | 1 | 1 | 92.9667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 2109 W. SHERIDAN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168058 | 148255 | 4189 | 242 | 0.00010806 | 1.1624e-06 | 92.9667 | 1 | 310 | Customer | 1037 | Load | TranOpenDelta | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | OK - 2022
J2001.004615 | PD-01122020-00101 | METRO NORTH | GUTHRIE | 8819:LIBERTY LAKE | LIBERTY_LAKE_1923 | 881923 | 2020-01-12 20:59 | 2020-01-12 22:34 | 94.63 | 1 | 1 | 87.85 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | GUTHRIE | 817 ROCK CREEK DR | CMI_NORMAL | NO | NO | NO | 860316 | 168058 | 19803 | 3348 | 1824 | 0.00010211 | 1.1624e-06 | 87.85 | 1 | 310 | Load | 61103 | Load | Tran1phOH | SCOTT C PERRY | 405-258-6044 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004619 |  | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_526 | 510526 | 2020-01-12 21:34 | 2020-01-12 22:13 | 39.03 | 18 | 19 | 333.9 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | ARDMORE | 712 C NW. | CMI_NORMAL | NO | NO | NO | 860316 | 77561 | 23571 | 4770 | 1619 | 0.00038811 | 2.0923e-05 | 18.55 | 1 | 310 | Load | 3721 | Load | Tran1phOH | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-12 | 2020 |  | OK - 2020
J2001.004634 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5123 | 815123 | 2020-01-12 22:43 | 2020-01-12 23:01 | 18.07 | 2 | 2 | 36.1333 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 7705 SACREMENTO | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 159005 | 102090 | 13935 | 1326 | 4.2e-05 | 2.3247e-06 | 18.0667 | 1 | 308 | Secondary | 44876 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004638 | PD-01132020-00001 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1924 | 851924 | 2020-01-12 23:57 | 2020-01-13 01:16 | 78.6 | 1 | 1 | 10.1721 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 2720 N.DOUGLAS BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 114333 | 71184 | 12434 | 1605 | 1.1824e-05 | 1.1624e-06 | 10.1721 | 1 | 320 | Customer | 15819 | Load | Tran1phOH | PETER BILICKI | 619-726-8332 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-12 | 2020 |  | #N/A
J2001.004671 | PD-01132020-00018 | NORTHWEST | ENID | 4109:WAUKOMIS | WAUKOMIS 24 | 410924 | 2020-01-13 07:54 | 2020-01-13 17:26 | 571.45 | 4 | 3 | 366.7261 | 22 | WIND | 37 | CONDUCTOR PRIMARY - OH | ENID | 4MW, 1.5MS, DRUMMOND | CMI_NORMAL | NO | NO | NO | 860316 | 53506 | 37572 | 1556 | 522 | 0.00042627 | 4.6495e-06 | 91.6815 | 1 | 310 | Mainline | 382428 | Fuse | FuseOH | JOSH SHEPHERD | 580-583-5632 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004672 | PD-01132020-00024 | METRO WEST | WEST | 8158:SARA | SARA_5864 | 815864 | 2020-01-13 08:01 | 2020-01-13 09:13 | 72.35 | 1 | 1 | 16.5556 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | * HAYFIELD + SW 15 TERR. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 128627 | 115894 | 18216 | 4810 | 1.9244e-05 | 1.1624e-06 | 16.5556 | 1 | 310 | Customer | 76000 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2022
J2001.004673 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-01-13 08:07 | 2020-01-13 15:25 | 437.87 | 1 | 0 | 176.2167 | 4 | DETERIORATION | 28 | CROSSARM | 0 | 17147 S HWY 64 | CMI_PLANNED | YES | NO | NO | 860316 | 73958 | 40727 | 2743 | 1439 | 0.00020483 | 1.1624e-06 | 176.2167 | 1 | 0 | Load | 303851 | Load | Tran3phWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | OK - 2021
J2001.004674 | PD-01132020-00027 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2023 | 822023 | 2020-01-13 08:09 | 2020-01-13 08:45 | 36.17 | 1 | 1 | 11.9523 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3301 NW.20 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168058 | 148255 | 6035 | 1028 | 1.3893e-05 | 1.1624e-06 | 11.9523 | 1 | 310 | Customer | 15663 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | OK - 2022
J2001.004676 | PD-01132020-00037 | ARKANSAS | FORT SMITH | 9104:J STREET | J_STREET_431 | 910431 | 2020-01-13 08:17 | 2020-01-13 09:21 | 64.5 | 1 | 1 | 64.5 | 11 | OVERLOAD | 21 | FUSE - TRANSFORMER | FORT SMITH | 1105 BALLMAN RD | CMI_NORMAL | NO | NO | NO | 860316 | 82163 | 61155 | 2004 | 845 | 7.4972e-05 | 1.1624e-06 | 64.5 | 1 | 310 | Customer | 216000 | Load | Tran3phWye | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-13 | 2020 |  | Ark - Series 2
J2001.004683 | PD-01132020-00066 | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4526 | 824526 | 2020-01-13 08:37 | 2020-01-13 12:15 | 218.15 | 1 | 1 | 218.15 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 0 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860316 | 0 | 0 | 0 | 0 | 0.00025357 | 1.1624e-06 | 218.15 | 1 | 320 | Customer |  | 0 | 0 | BOBBY RHODES | 405-306-8284 |  |  |  |  | 06/02/2020 note from burchamc. Reference J2001.004683 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Emailed Brent Miller with blank transformer and circuit #'s. Manually completed blank Job Region, Job Area, etc. | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004682 |  | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4823 | 824823 | 2020-01-13 08:37 | 2020-01-13 09:44 | 66.65 | 9 | 0 | 599.6478 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | OKLAHOMA CITY | 3516 SW.21 | CMI_PLANNED | YES | NO | NO | 860316 | 168058 | 148255 | 4189 | 1795 | 0.00069701 | 1.0461e-05 | 66.6275 | 1 | 0 | Load | 11982 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2021
J2001.004684 | PD-01132020-00070 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1423 | 311423 | 2020-01-13 08:42 | 2020-01-13 09:49 | 67.03 | 1 | 1 | 67.0333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 610 N 17TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 73958 | 33231 | 4561 | 1496 | 7.7917e-05 | 1.1624e-06 | 67.0333 | 1 | 320 | Customer | 5780 | Load | Tran1phOH | REID R WILLIAMS | 512-618-8800 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | OK - 2020
J2001.004698 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3831 | 913831 | 2020-01-13 08:58 | 2020-01-13 12:43 | 224.23 | 1 | 1 | 216.25 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 900 S. FRESNO,WHEELER | CMI_PLANNED | YES | NO | NO | 860316 | 82163 | 61155 | 2932 | 485 | 0.00025136 | 1.1624e-06 | 216.25 | 1 | 308 | Tap | 4863 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-13 | 2020 |  | Ark - Series 2
J2001.004693 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6322 | 816322 | 2020-01-13 08:59 | 2020-01-13 09:44 | 44.92 | 1 | 1 | 38.15 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | MOORE | 2600 N.SANTA-FE | CMI_PLANNED | YES | NO | NO | 860316 | 159005 | 102090 | 11814 | 1816 | 4.4344e-05 | 1.1624e-06 | 38.15 | 1 | 310 | Customer | 39782 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004692 | PD-01132020-00110 | SOUTHERN | ARDMORE | 5124:BERWYN | BERWYN_2423 | 512423 | 2020-01-13 09:00 | 2020-01-13 09:35 | 35.45 | 1 | 1 | 35.45 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SPRINGER | NW CORNER HWY 77+53 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77561 | 23571 | 1034 | 774 | 4.1206e-05 | 1.1624e-06 | 35.45 | 1 | 310 | Load | 22468 | Load | Tran1phOH | RANDAL G CALLAWAY | 580-220-8449 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004696 | PD-01132020-00116 | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_523 | 890523 | 2020-01-13 09:06 | 2020-01-13 10:38 | 92.05 | 1 | 1 | 76.5833 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | EL RENO | 2005 1/2 EAST HWY 66 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860316 | 128627 | 12733 | 6935 | 1251 | 8.9018e-05 | 1.1624e-06 | 76.5833 | 1 | 310 | Load | 79839 | Load | Tran3phWye | MICHAEL T MAHEN | 405-210-6029 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004701 | PD-01132020-00122 | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5822 | 845822 | 2020-01-13 09:12 | 2020-01-13 11:00 | 108.48 | 1 | 1 | 108.4833 | 3 | DAMAGED BY PUBLIC | 52 | CONDUCTOR SECURITY LIGHT - UG | OKLAHOMA CITY | NE.63+ DOUGLAS BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 114333 | 71184 | 2986 | 934 | 0.0001261 | 1.1624e-06 | 108.4833 | 1 | 321 | Load | 24354 | Load | Tran1phOH | ADAM CLARK | 580-310-8924 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | #N/A
J2001.004702 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7424 | 847424 | 2020-01-13 09:14 | 2020-01-13 09:14 | 0 | 2197 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 1131 NE 33RD ST | CMI_MOMENTARY | YES | NO | NO | 860316 | 168058 | 148255 | 6152 | 2197 | 0 | 0.0025537 | 0 | 1 | 0 | Feeder | STONEWALL_7424 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-13 | 2020 |  | OK - 2020
J2001.004703 | PD-01132020-00147 | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6222 | 866222 | 2020-01-13 09:18 | 2020-01-13 10:13 | 55.3 | 1 | 1 | 55.3 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 12615 SE 18TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 114333 | 71184 | 7203 | 1901 | 6.4279e-05 | 1.1624e-06 | 55.3 | 1 | 310 | Customer | 335144 | Load | Tran1phPad | ADAM CLARK | 580-310-8924 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004705 | PD-01132020-00139 | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_521 | 530521 | 2020-01-13 09:22 | 2020-01-13 09:40 | 18.42 | 1 | 1 | 18.4167 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | HEALDTON | 411 MAGNOLIA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77561 | 6791 | 2127 | 1259 | 2.1407e-05 | 1.1624e-06 | 18.4167 | 1 | 310 | Customer | 9214 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | OK - 2020
J2001.004708 |  | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_863 | 550863 | 2020-01-13 09:27 | 2020-01-13 11:32 | 124.63 | 2 | 1 | 144.3667 | 1 | CANCELLED | 1 | TRANSFORMER UG | MEAD | PARKLAKE DR | CMI_PLANNED | YES | NO | NO | 860316 | 77561 | 15479 | 1103 | 622 | 0.00016781 | 2.3247e-06 | 72.1833 | 1 | 308 | Load | 224669 | Load | Tran1phPad | Crew | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004712 | PD-01132020-00159 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_724 | 870724 | 2020-01-13 09:30 | 2020-01-13 11:47 | 137.42 | 1 | 1 | 137.4167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | ALAMEDA SQ. SHOPPING CENTER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 159005 | 56915 | 11831 | 2411 | 0.00015973 | 1.1624e-06 | 137.4167 | 1 | 310 | Customer | 74970 | Load | Tran3phPadWye | SHANE DRAKE | 405-326-9052 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004719 | PD-01132020-00171 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-01-13 09:39 | 2020-01-13 10:45 | 66.35 | 1 | 1 | 66.35 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | THE VILLAGE | 1532 W.HEFNER RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168058 | 148255 | 8784 | 1951 | 7.7123e-05 | 1.1624e-06 | 66.35 | 1 | 320 | Load | 59494 | Load | TranOpenDelta | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2021
J2001.004718 |  | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5822 | 845822 | 2020-01-13 09:39 | 2020-01-13 10:17 | 38.2 | 1 | 1 | 38.2 | 4 | DETERIORATION | 54 | LIGHTING - SECURITY | SPENCER | 5301 LISTEN CI | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860316 | 114333 | 71184 | 2986 | 934 | 4.4402e-05 | 1.1624e-06 | 38.2 | 1 | 310 | Load | 40993 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | #N/A
J2001.004720 | PD-01132020-00193 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5029 | 865029 | 2020-01-13 09:43 | 2020-01-13 11:02 | 78.85 | 1 | 1 | 78.85 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 1620 S AIR-DEPOT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 114333 | 71184 | 8622 | 1735 | 9.1652e-05 | 1.1624e-06 | 78.85 | 1 | 310 | Load | 61682 | Load | Tran3phWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004722 |  | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3222 | 813222 | 2020-01-13 09:49 | 2020-01-13 11:51 | 121.98 | 1 | 1 | 111.8833 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | SW 66TH/CNTRY CLB | CMI_PLANNED | YES | NO | NO | 860316 | 159005 | 102090 | 7598 | 1484 | 0.00013005 | 1.1624e-06 | 111.8833 | 1 | 308 | Tap | 6147 | Fuse | FuseRiser | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | #N/A
J2001.004727 | PD-01132020-00181 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-01-13 09:55 | 2020-01-13 11:04 | 69.15 | 1 | 1 | 69.15 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 1915 NW.12 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860316 | 168058 | 148255 | 11102 | 2036 | 8.0377e-05 | 1.1624e-06 | 69.15 | 1 | 310 | Customer | 16192 | Load | TranOpenDelta | ADAM COX | 405-328-8938 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2021
J2001.004728 |  | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_721 | 590721 | 2020-01-13 09:57 | 2020-01-13 10:02 | 4.95 | 1 | 1 | 4.95 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MANNSVILLE | WEST OF MANNSVILLE-CATFISH HSE | CMI_MOMENTARY | YES | NO | NO | 860316 | 77561 | 7203 | 2191 | 504 | 5.7537e-06 | 1.1624e-06 | 4.95 | 1 | 310 | Customer | 10316 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2021
J2001.004729 | PD-01132020-00188 | SOUTHERN | PAULS VALLEY | 5619:RUSH CREEK | RUSH_CREEK_1922 | 561922 | 2020-01-13 09:59 | 2020-01-13 10:49 | 50.27 | 1 | 1 | 50.2667 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | PAULS VALLEY | PAULS VALLEY ST SCH | CMI_NORMAL | NO | NO | NO | 860316 | 77561 | 6204 | 2073 | 1193 | 5.8428e-05 | 1.1624e-06 | 50.2667 | 1 | 320 | Load | 90164 | Load | 0 | BRUCE E BEAM | 405-626-0490 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | OK - 2021
J2001.004732 | PD-01132020-00192 | NORTHEAST | MUSKOGEE | 3111:FIVE TRIBES | FIVE_TRIBES_1129 | 311129 | 2020-01-13 10:01 | 2020-01-13 11:23 | 82 | 1 | 1 | 82 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MUSKOGEE | 2 MI E HWY64+DAVIS FLD JUNCT | CMI_NORMAL | NO | NO | NO | 860316 | 73958 | 33231 | 1680 | 864 | 9.5314e-05 | 1.1624e-06 | 82 | 1 | 310 | Load | 16300 | Load | Tran1phOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-13 | 2020 |  | #N/A
J2001.004733 |  | METRO NORTH | NORTH | 8209:CLASSEN | CLASSEN_965 | 820965 | 2020-01-13 10:01 | 2020-01-13 10:06 | 4.9 | 1 | 1 | 4.9 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 900 NW.8 | CMI_MOMENTARY | YES | NO | NO | 860316 | 168058 | 148255 | 3880 | 830 | 5.6956e-06 | 1.1624e-06 | 4.9 | 1 | 310 | Customer | 74573 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004734 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-13 10:05 | 2020-01-13 14:19 | 254.42 | 5 | 3 | 1260 | 4 | DETERIORATION | 12 | POLE | HARTMAN | HARTMAN,W-HANSON ON STEVENS ST | CMI_PLANNED | YES | NO | NO | 860316 | 82163 | 7536 | 1504 | 1200 | 0.0014646 | 5.8118e-06 | 252 | 1 | 308 | Load | 4900 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-13 | 2020 |  | Ark - Series 2
J2001.004735 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-13 10:05 | 2020-01-13 14:17 | 252.2 | 3 | 2 | 736.375 | 4 | DETERIORATION | 12 | POLE | HARTMAN | HARTMAN AR-STEPHENS ST. | CMI_PLANNED | YES | NO | NO | 860316 | 82163 | 7536 | 1504 | 1200 | 0.00085594 | 3.4871e-06 | 245.4583 | 1 | 308 | Load | 549 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-13 | 2020 |  | Ark - Series 2
J2001.004736 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-13 10:05 | 2020-01-13 14:18 | 253.05 | 1 | 1 | 233.5 | 4 | DETERIORATION | 12 | POLE | HARTMAN | STEVENS ST,1/4 M. W. OF MAIN | CMI_PLANNED | YES | NO | NO | 860316 | 82163 | 7536 | 1504 | 1200 | 0.00027141 | 1.1624e-06 | 233.5 | 1 | 308 | Load | 15319 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-13 | 2020 |  | Ark - Series 2
J2001.004743 | PD-01132020-00196 | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5429 | 865429 | 2020-01-13 10:05 | 2020-01-13 17:43 | 458.08 | 36 | 34 | 7226.5 | 3 | DAMAGED BY PUBLIC | 1 | TRANSFORMER UG | MOORE | E OF MORGAN + SE.4 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 159005 | 102090 | 9806 | 1661 | 0.0083998 | 4.1845e-05 | 200.7361 | 1 | 310 | Mainline | 18646 | Fuse | FuseRiser | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004737 |  | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5429 | 865429 | 2020-01-13 10:05 | 2020-01-13 10:05 | 0 | 553 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MOORE | MORGAN AND NE 4TH, SW CORNER | CMI_MOMENTARY | YES | NO | NO | 860316 | 159005 | 102090 | 9806 | 1661 | 0 | 0.00064279 | 0 | 1 | 0 | Mainline | 351940 | Recloser | Rec3phElectronic | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004738 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1226 | 831226 | 2020-01-13 10:06 | 2020-01-13 10:12 | 5.98 | 1 | 2 | 5.9833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1424 NW.42 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168058 | 148255 | 7738 | 1746 | 6.9548e-06 | 1.1624e-06 | 5.9833 | 1 | 310 | Customer | 454 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2021
J2001.004745 | PD-01132020-00200 | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-01-13 10:11 | 2020-01-13 12:20 | 129 | 1 | 3 | 74.2833 | 12 | POOR CONNECTION | 50 | CONNECTOR | BIXBY | 117 E WASHINGTON | CMI_NORMAL | NO | NO | NO | 860316 | 73958 | 40727 | 2743 | 1439 | 8.6344e-05 | 1.1624e-06 | 74.2833 | 1 | 320 | Customer | 41449 | Load | Tran1phOH | JOSHUA N MCKINNEY | 918-863-6313 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | OK - 2021
J2001.004744 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2521 | 912521 | 2020-01-13 10:12 | 2020-01-13 11:36 | 83.87 | 17 | 12 | 885.1333 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | FORT SMITH | S. 30 N. QUINCY | CMI_PLANNED | YES | NO | NO | 860316 | 82163 | 61155 | 2732 | 410 | 0.0010288 | 1.976e-05 | 52.0667 | 1 | 308 | Mainline | 2587 | Fuse | FuseRiser | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | Ark - Series 2
J2001.004753 |  | METRO EAST | EAST | 8416:DUNJEE | DUNJEE_1623 | 841623 | 2020-01-13 10:21 | 2020-01-13 11:16 | 54.95 | 1 | 1 | 43.7833 | 4 | DETERIORATION | 28 | CROSSARM | NICOMA PARK | 2500 OVERHOLSER DR | CMI_PLANNED | YES | NO | NO | 860316 | 114333 | 71184 | 3541 | 1988 | 5.0892e-05 | 1.1624e-06 | 43.7833 | 1 | 308 | Load | 57048 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004755 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_722 | 870722 | 2020-01-13 10:25 | 2020-01-13 11:24 | 59.5 | 6 | 3 | 357.6 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | NORMAN | .5MW E.96TH AV + HWY 9 | CMI_PLANNED | YES | NO | NO | 860316 | 159005 | 56915 | 11831 | 1582 | 0.00041566 | 6.9742e-06 | 59.6 | 1 | 310 | Mainline | 20907 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004756 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_722 | 870722 | 2020-01-13 10:25 | 2020-01-13 11:24 | 59.55 | 2 | 1 | 86.5167 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | NORMAN | .5MW E.96TH AV + HWY 9 | CMI_PLANNED | YES | NO | NO | 860316 | 159005 | 56915 | 11831 | 1582 | 0.00010056 | 2.3247e-06 | 43.2583 | 1 | 308 | Mainline | 20908 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004762 | PD-01132020-00238 | NORTHWEST | ENID | 4353:OTTER | OTTER_5341 | 435341 | 2020-01-13 10:31 | 2020-01-13 14:04 | 212.58 | 1 | 1 | 212.5833 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | MARSHALL | 2.5S,2W,2S,3/8W-MARSHALL | CMI_NORMAL | NO | NO | NO | 860316 | 53506 | 37572 | 960 | 792 | 0.0002471 | 1.1624e-06 | 212.5833 | 1 | 310 | Customer | 4004 | Load | TranOpenDelta | STEVEN LORENZ | 580-822-3566 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2021
J2001.004759 |  | METRO WEST | WEST | 8321:PIEDMONT | PIEDMONT_2164 | 832164 | 2020-01-13 10:32 | 2020-01-13 11:36 | 64.73 | 6 | 4 | 380.5 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 15925 N.MACARTHUR | CMI_PLANNED | YES | NO | NO | 860316 | 128627 | 115894 | 6286 | 3003 | 0.00044228 | 6.9742e-06 | 63.4167 | 1 | 308 | Load | 70754 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004767 | PD-01132020-00249 | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1421 | 911421 | 2020-01-13 10:39 | 2020-01-13 11:07 | 28.07 | 1 | 1 | 28.0667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 3711 WIRSING AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 82163 | 61155 | 4737 | 1746 | 3.2624e-05 | 1.1624e-06 | 28.0667 | 1 | 320 | Customer | 6796 | Load | Tran1phOH | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-13 | 2020 |  | Ark - Series 1
J2001.004770 |  | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1722 | 911722 | 2020-01-13 10:46 | 2020-01-13 14:30 | 224.47 | 5 | 6 | 1121.8598 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 9020 ROYALRIDGE DR | CMI_PLANNED | YES | NO | NO | 860316 | 82163 | 61155 | 4236 | 1474 | 0.001304 | 5.8118e-06 | 224.372 | 1 | 310 | Load | 584 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-13 | 2020 |  | #N/A
J2001.004773 | PD-01132020-00266 | NORTHEAST | MUSKOGEE | 3327:VIAN | VIAN 22 | 332722 | 2020-01-13 10:52 | 2020-01-13 12:11 | 79.23 | 1 | 1 | 79.2333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | VIAN | VIAN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 73958 | 33231 | 779 | 779 | 9.2098e-05 | 1.1624e-06 | 79.2333 | 1 | 310 | Customer | 9749 | Load | Tran1phOH | JAMES MCDONALD | 405-361-7186 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | OK - 2021
J2001.004781 | PD-01132020-00272 | METRO EAST | SHAWNEE | 7407:REMINGTON | REMINGTON 21 | 740721 | 2020-01-13 11:04 | 2020-01-13 13:06 | 122.5 | 1 | 2 | 119.3 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | SHAWNEE | 2222 E. MAIN-SHAWNEE | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860316 | 114333 | 22095 | 3665 | 2020 | 0.00013867 | 1.1624e-06 | 119.3 | 1 | 310 | Load | 19989 | Load | Tran1phPad | BRYAN K TATUM | 405-659-0746 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | OK - 2021
J2001.004779 | PD-01132020-00279 | NORTHEAST | SAPULPA | 7610:PRINCEVILLE | PRINCEVILLE_1021 | 761021 | 2020-01-13 11:04 | 2020-01-13 12:24 | 80.4 | 1 | 1 | 70.6333 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | FREEDOM HILL | 1 3/4MN OF JCT 33-48 (ES) | CMI_NORMAL | NO | NO | NO | 860316 | 73958 | 40727 | 304 | 304 | 8.2102e-05 | 1.1624e-06 | 70.6333 | 1 | 310 | Load | 18832 | Load | Tran1phOH | GREGORY R HOOVER | 918-261-6803 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | #N/A
J2001.004778 |  | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2731 | 872731 | 2020-01-13 11:04 | 2020-01-13 11:04 | 0.08 | 2611 | 0 | 217.5833 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | NORMAN | 1000 ROCKCREEK RD | CMI_MOMENTARY | YES | NO | NO | 860316 | 159005 | 56915 | 6459 | 0 | 0.00025291 | 0.0030349 | 0.083333 | 1 | 0 | Substation | STUBBEMN_123 | Breaker | SubRecloser | Circuit Operation | [5 empty] | 06/02/2020 note from burchamc. Reference J2001.004778 in iDashboard report OSI_Job_Detail_Viewer. The job references Device STUBBEMN_2731 and STUBBEMN_2729. Probably should have been two jobs. Used Lead Device ID STUBBEMN_2731 to Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004785 | PD-01132020-00277 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1522 | 811522 | 2020-01-13 11:09 | 2020-01-13 15:33 | 264.48 | 1 | 1 | 25.516 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2511 SW.27 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 159005 | 102090 | 6056 | 1940 | 2.9659e-05 | 1.1624e-06 | 25.516 | 1 | 310 | Customer | 33105 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | OK - 2022
J2001.004786 | PD-01132020-00275 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6126 | 836126 | 2020-01-13 11:10 | 2020-01-13 16:20 | 310.08 | 2 | 3 | 340.4833 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 605.5 NW.31 | CMI_NORMAL | NO | NO | NO | 860316 | 168058 | 148255 | 11102 | 456 | 0.00039577 | 2.3247e-06 | 170.2417 | 1 | 310 | Secondary | 35967 | Load | Tran1phOH | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2022
J2001.004792 | PD-01132020-00285 | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1862 | 941862 | 2020-01-13 11:14 | 2020-01-13 12:26 | 72.43 | 8 | 11 | 664.1333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | LAMAR | LAMAR, E-2ND ST ON SEMINARY ST | CMI_NORMAL | NO | NO | NO | 860316 | 82163 | 7536 | 729 | 729 | 0.00077196 | 9.2989e-06 | 83.0167 | 1 | 310 | Load | 5274 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | Ark - Series 2
J2001.004788 | PD-01132020-00283 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7424 | 847424 | 2020-01-13 11:18 | 2020-01-13 11:50 | 31.6 | 3 | 2 | 79.95 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1900 NE.50 | CMI_NORMAL | NO | NO | NO | 860316 | 168058 | 148255 | 6152 | 2197 | 9.2931e-05 | 3.4871e-06 | 26.65 | 1 | 310 | Load | 13978 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2020
J2001.004791 | PD-01132020-00284 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7024 | 817024 | 2020-01-13 11:20 | 2020-01-13 12:56 | 95.8 | 1 | 1 | 95.8 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | SW.66 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 159005 | 102090 | 9938 | 1752 | 0.00011135 | 1.1624e-06 | 95.8 | 1 | 310 | Customer | 31090 | Load | Tran1phPad | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004794 |  | SOUTHERN | MADILL | 5408:CANEY CREEK | CANEY_CREEK_823 | 540823 | 2020-01-13 11:29 | 2020-01-13 12:08 | 39.07 | 4 | 4 | 148.6 | 4 | DETERIORATION | 2 | TRANSFORMER OH | KINGSTON | 6 N Cherokee | CMI_PLANNED | YES | NO | NO | 860316 | 77561 | 7203 | 1053 | 423 | 0.00017273 | 4.6495e-06 | 37.15 | 1 | 308 | Load | 10914 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004795 |  | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1371 | 831371 | 2020-01-13 11:30 | 2020-01-13 13:04 | 94.37 | 276 | 106 | 25139 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | YUKON | 400 FT S HWY66 ON FRIS | CMI_PLANNED | YES | NO | NO | 860316 | 128627 | 115894 | 7870 | 3775 | 0.029221 | 0.00032081 | 91.0833 | 1 | 310 | Mainline | 25892 | Switch | SwitchOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004800 |  | METRO WEST | WEST | 8158:SARA | SARA_5864 | 815864 | 2020-01-13 11:33 | 2020-01-13 13:06 | 92.58 | 4 | 5 | 350.2667 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | YUKON | WINFIELD/CHURCHILL | CMI_PLANNED | YES | NO | NO | 860316 | 128627 | 115894 | 18216 | 4810 | 0.00040714 | 4.6495e-06 | 87.5667 | 1 | 310 | Secondary | 84883 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2022
J2001.004804 |  | METRO WEST | WEST | 8321:PIEDMONT | PIEDMONT_2164 | 832164 | 2020-01-13 11:47 | 2020-01-13 12:43 | 56.33 | 3 | 2 | 147.85 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 15812 N MACARTHUR BL | CMI_PLANNED | YES | NO | NO | 860316 | 128627 | 115894 | 6286 | 3003 | 0.00017186 | 3.4871e-06 | 49.2833 | 1 | 308 | Load | 363714 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004805 |  | METRO NORTH | GUTHRIE | 8813:FITZGERALD CR | FITZGERALD_CR_1342 | 881342 | 2020-01-13 11:49 | 2020-01-13 13:33 | 104.38 | 1 | 1 | 72.1667 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | LANGSTON | .5M W LANGSTON 1M S | CMI_PLANNED | YES | NO | NO | 860316 | 168058 | 19803 | 1044 | 808 | 8.3884e-05 | 1.1624e-06 | 72.1667 | 1 | 310 | Customer | 37645 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004809 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-01-13 11:50 | 2020-01-13 11:59 | 8.6 | 1 | 1 | 8.6 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7524 NW 6TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 128627 | 115894 | 3405 | 2036 | 9.9963e-06 | 1.1624e-06 | 8.6 | 1 | 310 | Customer | 38147 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004808 |  | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_422 | 580422 | 2020-01-13 11:51 | 2020-01-13 11:57 | 5.72 | 1 | 1 | 5.7167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ADA | 215 S.MISS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77561 | 11504 | 3411 | 1426 | 6.6448e-06 | 1.1624e-06 | 5.7167 | 1 | 310 | Customer | 8356 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004807 |  | METRO WEST | WEST | 8321:PIEDMONT | PIEDMONT_2164 | 832164 | 2020-01-13 11:52 | 2020-01-13 13:12 | 80.52 | 108 | 2 | 2332.8 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | 16205 N MACARTHUR BL | CMI_PLANNED | YES | NO | NO | 860316 | 128627 | 115894 | 6286 | 3003 | 0.0027116 | 0.00012554 | 21.6 | 1 | 310 | Mainline | 258808 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004811 | PD-01132020-00321 | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-01-13 11:55 | 2020-01-13 13:19 | 83.78 | 1 | 1 | 83.7833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | TISHOMINGO | US HWY 377 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77561 | 7203 | 2191 | 1673 | 9.7387e-05 | 1.1624e-06 | 83.7833 | 1 | 310 | Customer | 3429 | Load | Tran1phOH | DAVID TAYLOR | 580-574-4517 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004813 | PD-01132020-00328 | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_522 | 560522 | 2020-01-13 12:00 | 2020-01-13 14:24 | 144.48 | 1 | 1 | 133.5167 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | PAOLI | PAOLI SR CITIZEN S CTR-HWY 145 | CMI_NORMAL | NO | NO | NO | 860316 | 77561 | 6204 | 2455 | 827 | 0.00015519 | 1.1624e-06 | 133.5167 | 1 | 310 | Customer | 25339 | Load | Tran1phOH | BRUCE E BEAM | 405-626-0490 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | OK - 2022
J2001.004817 | PD-01132020-00343 | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-01-13 12:14 | 2020-01-13 13:54 | 99.72 | 1 | 2 | 96.25 | 12 | POOR CONNECTION | 50 | CONNECTOR | TISHOMINGO | 110 E.MAIN | CMI_NORMAL | NO | NO | NO | 860316 | 77561 | 7203 | 2191 | 1673 | 0.00011188 | 1.1624e-06 | 96.25 | 1 | 310 | Customer | 1343 | Load | Tran1phOH | DAVID TAYLOR | 580-574-4517 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004818 |  | SOUTHERN | MADILL | 5408:CANEY CREEK | CANEY_CREEK_823 | 540823 | 2020-01-13 12:16 | 2020-01-13 14:14 | 117.23 | 4 | 3 | 195.7 | 4 | DETERIORATION | 2 | TRANSFORMER OH | KINGSTON | 105 N Choctaw | CMI_PLANNED | YES | NO | NO | 860316 | 77561 | 7203 | 1053 | 423 | 0.00022747 | 4.6495e-06 | 48.925 | 1 | 308 | Load | 14630 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004820 | PD-01132020-00346 | SOUTHERN | MADILL | 5409:LITTLE CITY | LITTLE CITY 21 | 540921 | 2020-01-13 12:19 | 2020-01-13 16:12 | 232.97 | 1 | 2 | 232.9667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | BRIDGEVIEW | .2WBRDG AVE+LAKE ST-BRIDGEVIEW | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77561 | 7203 | 611 | 592 | 0.00027079 | 1.1624e-06 | 232.9667 | 1 | 310 | Customer | 22025 | Load | Tran1phOH | DAVID TAYLOR | 580-574-4517 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004826 | PD-01132020-00354 | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5421 | 865421 | 2020-01-13 12:30 | 2020-01-13 15:16 | 166.35 | 4 | 4 | 624.6 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | MOORE | 1819 SHELLY CT | CMI_NORMAL | NO | NO | NO | 860316 | 159005 | 102090 | 9806 | 1879 | 0.00072601 | 4.6495e-06 | 156.15 | 1 | 310 | Secondary | 62365 | Load | Tran1phPad | BAD ORDER PRIMARY RES COORD | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004828 | PD-01132020-00405 | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5421 | 865421 | 2020-01-13 12:31 | 2020-01-13 15:42 | 190.77 | 7 | 5 | 827.1667 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | MOORE | 1005 NE.17 | CMI_NORMAL | NO | NO | NO | 860316 | 159005 | 102090 | 9806 | 1879 | 0.00096147 | 8.1365e-06 | 118.1667 | 1 | 310 | Load | 62363 | Load | Tran1phPad | MIKE MITCHELL | 405-996-8178 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004840 | PD-01132020-00368 | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2823 | 312823 | 2020-01-13 12:36 | 2020-01-13 17:56 | 320.43 | 4 | 3 | 825.3 | 4 | DETERIORATION | 1 | TRANSFORMER UG | MUSKOGEE | 1007 S.UTAH CT | CMI_NORMAL | NO | NO | NO | 860316 | 73958 | 33231 | 5271 | 1391 | 0.0009593 | 4.6495e-06 | 206.325 | 1 | 308 | Load | 9856 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-13 | 2020 |  | #N/A
J2001.004995 |  | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2823 | 312823 | 2020-01-13 12:36 | 2020-01-13 18:00 | 324.57 | 10 | 11 | 3245.8185 | 4 | DETERIORATION | 1 | TRANSFORMER UG | MUSKOGEE | 0 | CMI_NORMAL | NO | NO | NO | 860316 | 73958 | 33231 | 5271 | 1391 | 0.0037728 | 1.1624e-05 | 324.5818 | 1 | 310 | Mainline | 9856-1 | Switch | SwitchDefault | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-13 | 2020 |  | #N/A
J2001.004997 |  | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2823 | 312823 | 2020-01-13 12:36 | 2020-01-13 18:09 | 333.25 | 9 | 14 | 1464.75 | 4 | DETERIORATION | 1 | TRANSFORMER UG | MUSKOGEE | 901 S.UTAH | CMI_NORMAL | NO | NO | NO | 860316 | 73958 | 33231 | 5271 | 1391 | 0.0017026 | 1.0461e-05 | 162.75 | 1 | 310 | Load | 15864 | Load | Tran1phPad | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-13 | 2020 |  | #N/A
J2001.004831 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1862 | 941862 | 2020-01-13 12:38 | 2020-01-13 17:18 | 280.28 | 1 | 0 | 280.2711 | 4 | DETERIORATION | 12 | POLE | LAMAR | .5ME OF HWY 64 ON HWY 359 | CMI_PLANNED | YES | NO | NO | 860316 | 82163 | 7536 | 729 | 729 | 0.00032578 | 1.1624e-06 | 280.2711 | 1 | 0 | Load | 225908 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | Ark - Series 2
J2001.004833 | PD-01132020-00369 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3624 | 853624 | 2020-01-13 12:42 | 2020-01-13 13:18 | 36.12 | 1 | 1 | 14.6787 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1319.5 NE.6 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168058 | 148255 | 5919 | 928 | 1.7062e-05 | 1.1624e-06 | 14.6787 | 1 | 310 | Customer | 48440 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004834 |  | METRO WEST | WEST | 8321:PIEDMONT | PIEDMONT_2164 | 832164 | 2020-01-13 12:42 | 2020-01-13 13:26 | 43.73 | 4 | 4 | 135.4 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 15709 N MacARTHUR | CMI_PLANNED | YES | NO | NO | 860316 | 128627 | 115894 | 6286 | 3003 | 0.00015738 | 4.6495e-06 | 33.85 | 1 | 310 | Load | 24159 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004835 | PD-01132020-00362 | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2131 | 332131 | 2020-01-13 12:45 | 2020-01-13 13:24 | 38.87 | 1 | 1 | 38.8667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKAY | OKAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 73958 | 33231 | 3333 | 1172 | 4.5177e-05 | 1.1624e-06 | 38.8667 | 1 | 310 | Customer | 3412 | Load | TranOpenDelta | JAMES C EVANS | 918-869-1174 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-13 | 2020 |  | #N/A
J2001.004842 | PD-01132020-00373 | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1024 | 541024 | 2020-01-13 12:52 | 2020-01-13 15:43 | 171.4 | 1 | 2 | 171.4 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MADILL | 2.4 E GLASSES SUB .4N .1W | CMI_NORMAL | NO | NO | NO | 860316 | 77561 | 7203 | 2379 | 661 | 0.00019923 | 1.1624e-06 | 171.4 | 1 | 310 | Load | 219740 | Load | Tran1phOH | DAVID TAYLOR | 580-574-4517 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004846 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-13 13:03 | 2020-01-13 22:05 | 542 | 1 | 0 | 46.7833 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | 0 | BETWEEN HARTMAN AND CLARKSVILE | CMI_PLANNED | YES | NO | NO | 860316 | 82163 | 7536 | 1504 | 1200 | 5.4379e-05 | 1.1624e-06 | 46.7833 | 1 | 0 | Load | 15788 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-13 | 2020 |  | Ark - Series 2
J2001.004849 | PD-01132020-00395 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4821 | 824821 | 2020-01-13 13:12 | 2020-01-13 13:56 | 43.67 | 1 | 1 | 43.6667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2109 W. SHERIDAN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168058 | 148255 | 4189 | 242 | 5.0757e-05 | 1.1624e-06 | 43.6667 | 1 | 310 | Customer | 1037 | Load | TranOpenDelta | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2022
J2001.004848 |  | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1371 | 831371 | 2020-01-13 13:13 | 2020-01-13 13:18 | 5.77 | 1 | 1 | 5.7667 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | YUKON | SIGNALMAN RD | CMI_PLANNED | YES | NO | NO | 860316 | 128627 | 115894 | 7870 | 3775 | 6.703e-06 | 1.1624e-06 | 5.7667 | 1 | 310 | Customer | 248579 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004857 | PD-01132020-00413 | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_621 | 770621 | 2020-01-13 13:23 | 2020-01-13 14:56 | 93.42 | 1 | 2 | 88.0333 | 12 | POOR CONNECTION | 50 | CONNECTOR | BRISTOW | 6.5 NW OF BRISTOW ON HWY 16 SS | CMI_NORMAL | NO | NO | NO | 860316 | 73958 | 40727 | 3781 | 1575 | 0.00010233 | 1.1624e-06 | 88.0333 | 1 | 310 | Load | 19209 | Load | Tran1phOH | GREGORY R HOOVER | 918-261-6803 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | OK - 2021
J2001.004858 | PD-01132020-00407 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-01-13 13:23 | 2020-01-13 14:25 | 62.15 | 1 | 1 | 62.15 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4748 NW.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168058 | 148255 | 9239 | 1940 | 7.2241e-05 | 1.1624e-06 | 62.15 | 1 | 310 | Customer | 35033 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2021
J2001.004863 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6124 | 836124 | 2020-01-13 13:36 | 2020-01-13 13:46 | 9.18 | 1 | 1 | 9.1833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1608 NW.31 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168058 | 148255 | 11102 | 1766 | 1.0674e-05 | 1.1624e-06 | 9.1833 | 1 | 310 | Customer | 35061 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2020
J2001.004862 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_722 | 870722 | 2020-01-13 13:37 | 2020-01-13 15:34 | 117.58 | 1 | 0 | 116.4333 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | NORMAN | .4ME E.84TH AV + HWY 9 | CMI_PLANNED | YES | NO | NO | 860316 | 159005 | 56915 | 11831 | 1582 | 0.00013534 | 1.1624e-06 | 116.4333 | 1 | 0 | Tap | 22019 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004866 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-13 13:43 | 2020-01-13 13:53 | 10.62 | 2169 | 229 | 23027.55 | 6 | HOT LINE HOLD ORDER | 45 | SUBSTATION CIRCUIT | FT SMITH | 4699 S ZERO ST | CMI_NORMAL | NO | NO | NO | 860316 | 82163 | 61155 | 2732 | 2120 | 0.026766 | 0.0025212 | 10.6167 | 1 | 311 | Feeder | CARNALL_2564 | Recloser | SubRecloser | [7 empty] | Other | N | SUBSTATION | 69kV | 2020-01-13 | 2020 |  | Ark - Series 2
J2001.004870 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_871 | 830871 | 2020-01-13 13:44 | 2020-01-13 14:01 | 16.83 | 1 | 1 | 16.8333 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 17313 RIDGEWOOD DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168058 | 148255 | 19357 | 4238 | 1.9566e-05 | 1.1624e-06 | 16.8333 | 1 | 310 | Customer | 243998 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2021
J2001.004873 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-13 13:49 | 2020-01-13 14:10 | 20.65 | 1 | 1 | 4.4833 | 1 | CANCELLED | 57 | CANCELLED | LAVACA | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 0 | 0 | 0 | 0 | 5.2113e-06 | 1.1624e-06 | 4.4833 | 1 | 310 | Customer |  | 0 | 0 | [6 empty] | 06/02/2020 note from burchamc. Reference J2001.004873 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | Ark - Series 2
J2001.004878 | PD-01132020-00444 | NORTHEAST | MUSKOGEE | 3326:JAMESVILLE | JAMESVILLE_2621 | 332621 | 2020-01-13 13:50 | 2020-01-13 15:18 | 87.67 | 1 | 2 | 59.3833 | 4 | DETERIORATION | 4 | SWITCH - OIL | BALD HILL | .8 ME BALDHILL STORE ON HWY 16 | CMI_NORMAL | NO | NO | NO | 860316 | 73958 | 33231 | 1548 | 272 | 6.9025e-05 | 1.1624e-06 | 59.3833 | 1 | 310 | Load | 17887 | Load | Tran1phOH | JOSH CHENEY | 918-619-3590 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | OK - 2020
J2001.004876 | PD-01132020-00439 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6921 | 846921 | 2020-01-13 13:57 | 2020-01-13 15:04 | 67.12 | 1 | 1 | 59.7667 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | EDMOND | 4208 S.JORDAN | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860316 | 168058 | 148255 | 7717 | 1353 | 6.9471e-05 | 1.1624e-06 | 59.7667 | 1 | 310 | Customer | 59571 | Load | Tran1phOH | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004880 | PD-01132020-00448 | NORTHEAST | MUSKOGEE | 3326:JAMESVILLE | JAMESVILLE_2621 | 332621 | 2020-01-13 14:07 | 2020-01-13 15:02 | 54.87 | 1 | 1 | 11.8614 | 4 | DETERIORATION | 4 | SWITCH - OIL | OKMULGEE | twin hills school on twin hills rd. | CMI_NORMAL | NO | NO | NO | 860316 | 73958 | 33231 | 1548 | 272 | 1.3787e-05 | 1.1624e-06 | 11.8614 | 1 | 320 | Load | 325001 | Load | Tran3phWye | JACQUELINE D HANNA | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | OK - 2020
J2001.004886 | PD-01132020-00466 | SOUTHERN | ARDMORE | 5109:ARDMORE WEST | ARDMORE_WEST_931 | 510931 | 2020-01-13 14:12 | 2020-01-13 15:18 | 65.68 | 59 | 30 | 3300.0667 | 3 | DAMAGED BY PUBLIC | 17 | JUMPER | ARDMORE | PLAINVIEW/MYALL .5S WS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77561 | 23571 | 1315 | 701 | 0.0038359 | 6.8579e-05 | 55.9333 | 1 | 310 | Mainline | 7222 | Fuse | FuseOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004883 | PD-01132020-00463 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2031 | 862031 | 2020-01-13 14:14 | 2020-01-13 18:03 | 228.6 | 1 | 1 | 228.6 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1160 SE 19th Te | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 159005 | 102090 | 4741 | 1440 | 0.00026572 | 1.1624e-06 | 228.6 | 1 | 310 | Customer | 11369 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2021
J2001.004887 | PD-01132020-00458 | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-01-13 14:17 | 2020-01-13 15:22 | 64.62 | 1 | 1 | 64.6167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1105 N MARKWELL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 128627 | 115894 | 3405 | 2036 | 7.5108e-05 | 1.1624e-06 | 64.6167 | 1 | 320 | Customer | 76594 | Load | TranOpenDelta | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004893 | PD-01132020-00470 | SOUTHERN | DURANT | 5511:BOKCHITO | BOKCHITO 21 | 551121 | 2020-01-13 14:25 | 2020-01-13 15:45 | 80.15 | 1 | 1 | 80.15 | 11 | OVERLOAD | 21 | FUSE - TRANSFORMER | BENNINGTON | .5W BENNINGTON ON HWY 70 | CMI_NORMAL | NO | NO | NO | 860316 | 77561 | 15479 | 669 | 669 | 9.3163e-05 | 1.1624e-06 | 80.15 | 1 | 320 | Customer | 28254 | Load | TranOpenDelta | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kv | 2020-01-13 | 2020 |  | #N/A
J2001.004895 | PD-01132020-00480 | METRO EAST | SEMINOLE | 7307:LITTLE RIVER | LITTLE_RIVER_722 | 730722 | 2020-01-13 14:27 | 2020-01-13 15:44 | 77.15 | 1 | 2 | 68.3167 | 22 | WIND | 17 | JUMPER | LIMA | 2 2tenths me 4tenths mn 2tenths e | CMI_NORMAL | NO | NO | NO | 860316 | 114333 | 13596 | 574 | 428 | 7.9409e-05 | 1.1624e-06 | 68.3167 | 1 | 310 | Load | 250864 | Load | 0 | BRADY A HUFF | 405-519-0701 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | #N/A
J2001.004901 | PD-01132020-00489 | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_823 | 870823 | 2020-01-13 14:32 | 2020-01-13 17:25 | 172.9 | 1 | 2 | 172.9 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | NORMAN | 333 E BROOKS ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 159005 | 56915 | 6775 | 2380 | 0.00020097 | 1.1624e-06 | 172.9 | 1 | 310 | Customer | 381033 | Load | Tran3phPadWye | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004900 | PD-01132020-00486 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6333 | 816333 | 2020-01-13 14:33 | 2020-01-13 16:38 | 124.55 | 3 | 3 | 348.825 | 12 | POOR CONNECTION | 50 | CONNECTOR | MOORE | 713 N.ARNOLD AV | CMI_NORMAL | NO | NO | NO | 860316 | 159005 | 102090 | 11814 | 1229 | 0.00040546 | 3.4871e-06 | 116.275 | 1 | 310 | Secondary | 36796 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2022
J2001.004909 |  | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2821 | 312821 | 2020-01-13 14:43 | 2020-01-13 14:43 | 0 | 1151 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MUSKOGEE | 2431 INDIANA | CMI_MOMENTARY | YES | NO | NO | 860316 | 73958 | 33231 | 5271 | 1151 | 0 | 0.0013379 | 0 | 1 | 0 | Feeder | HANCOCK_2821 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-13 | 2020 |  | #N/A
J2001.004910 |  | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2821 | 312821 | 2020-01-13 14:45 | 2020-01-13 16:51 | 125.55 | 47 | 6 | 574.9667 | 4 | DETERIORATION | 23 | FUSE - PRIMARY | MUSKOGEE | VIRGINIA + AGUSTA | CMI_NORMAL | NO | NO | NO | 860316 | 73958 | 33231 | 5271 | 1151 | 0.00066832 | 5.4631e-05 | 12.2333 | 1 | 310 | Mainline | 14677 | Fuse | FuseRiser | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-13 | 2020 |  | #N/A
J2001.004911 |  | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2821 | 312821 | 2020-01-13 14:45 | 2020-01-13 15:23 | 38.2 | 1 | 1 | 38.2 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MUSKOGEE | 2202 AUGUSTA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 73958 | 33231 | 5271 | 1151 | 4.4402e-05 | 1.1624e-06 | 38.2 | 1 | 310 | Customer | 4757 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-13 | 2020 |  | #N/A
J2001.004913 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4033 | 834033 | 2020-01-13 14:51 | 2020-01-13 15:10 | 19.18 | 1 | 1 | 19.1833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7220 NW 112th Street | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 128627 | 115894 | 10841 | 1115 | 2.2298e-05 | 1.1624e-06 | 19.1833 | 1 | 310 | Customer | 80559 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004914 | PD-01132020-00500 | NORTHEAST | MUSKOGEE | 3326:JAMESVILLE | JAMESVILLE_2621 | 332621 | 2020-01-13 14:52 | 2020-01-13 15:19 | 27.27 | 1 | 1 | 14.3548 | 4 | DETERIORATION | 4 | SWITCH - OIL | BALD HILL | J T MARTIN LEASE | CMI_NORMAL | NO | NO | NO | 860316 | 73958 | 33231 | 1548 | 272 | 1.6685e-05 | 1.1624e-06 | 14.3548 | 1 | 320 | Customer | 13323 | Load | Tran1phOH | JOSH CHENEY | 918-619-3590 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | OK - 2020
J2001.004916 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2525 | 912525 | 2020-01-13 14:57 | 2020-01-13 17:32 | 154.32 | 1 | 1 | 146.1167 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 4401 SAVANNAH | CMI_PLANNED | YES | NO | NO | 860316 | 82163 | 61155 | 2732 | 198 | 0.00016984 | 1.1624e-06 | 146.1167 | 1 | 308 | Mainline | 4537 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | Ark - Series 2
J2001.004920 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-01-13 15:12 | 2020-01-13 15:23 | 10.72 | 1 | 1 | 10.7167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7524 NW 6TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 128627 | 115894 | 3405 | 2036 | 1.2457e-05 | 1.1624e-06 | 10.7167 | 1 | 310 | Customer | 38147 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004928 |  | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_521 | 320521 | 2020-01-13 15:33 | 2020-01-13 15:43 | 9.4 | 1 | 1 | 9.4 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SAPULPA | 502 S.POPLAR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 73958 | 40727 | 3837 | 1607 | 1.0926e-05 | 1.1624e-06 | 9.4 | 1 | 310 | Customer | 45630 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | OK - 2022
J2001.004933 | PD-01132020-00522 | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5631 | 865631 | 2020-01-13 15:35 | 2020-01-13 19:57 | 262.05 | 410 | 313 | 40467 | 4 | DETERIORATION | 17 | JUMPER | OKLAHOMA CITY | 2739 SE 59TH ST | CMI_NORMAL | NO | NO | NO | 860316 | 159005 | 102090 | 2747 | 374 | 0.047037 | 0.00047657 | 98.7 | 1 | 310 | Feeder | FOSTER_5631 | Recloser | SubRecloser | JUSTIN C TAYLOR | 405-534-1006 | [5 empty] | Equipment | N | SUBSTATION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004930 | PD-01132020-00523 | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1373 | 831373 | 2020-01-13 15:36 | 2020-01-13 19:24 | 227.98 | 1 | 1 | 227.9833 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 9801 Blake Landing | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860316 | 128627 | 115894 | 7870 | 4095 | 0.000265 | 1.1624e-06 | 227.9833 | 1 | 320 | Customer | 257712 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004938 |  | METRO EAST | EAST | 8542:RENO | RENO_4224 | 854224 | 2020-01-13 15:40 | 2020-01-13 20:15 | 275.12 | 1 | 2 | 257.6333 | 4 | DETERIORATION | 17 | JUMPER | DEL CITY | 901 N.SOONER | CMI_NORMAL | NO | NO | NO | 860316 | 114333 | 71184 | 5212 | 1221 | 0.00029946 | 1.1624e-06 | 257.6333 | 1 | 310 | Customer | 8138 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2022
J2001.004944 | PD-01132020-00541 | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2722 | 872722 | 2020-01-13 15:43 | 2020-01-13 18:53 | 189.9 | 1 | 3 | 150.5833 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 348 WEWOKA DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 159005 | 56915 | 6459 | 1362 | 0.00017503 | 1.1624e-06 | 150.5833 | 1 | 310 | Secondary | 33997 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004948 |  | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1724 | 861724 | 2020-01-13 15:43 | 2020-01-13 20:12 | 268.27 | 1 | 2 | 254.0167 | 5 | ELECTRICAL TRACKING | 17 | JUMPER | OKLAHOMA CITY | 5112 SE.54 | CMI_NORMAL | NO | NO | NO | 860316 | 114333 | 71184 | 6938 | 2054 | 0.00029526 | 1.1624e-06 | 254.0167 | 1 | 310 | Customer | 22506 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | #N/A
J2001.004941 | PD-01132020-00535 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4862 | 824862 | 2020-01-13 15:46 | 2020-01-13 19:47 | 241.5 | 2 | 4 | 493.4997 | 22 | WIND | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 716 W.RENO | CMI_NORMAL | NO | NO | NO | 860316 | 168058 | 148255 | 4189 | 127 | 0.00057363 | 2.3247e-06 | 246.7499 | 1 | 321 | Secondary | 1060 | Load | TranOpenDelta | DENNY J MORGAN | 405-501-1556 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2022
J2001.004935 |  | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1724 | 861724 | 2020-01-13 15:47 | 2020-01-13 20:13 | 265.38 | 1 | 1 | 250.2333 | 5 | ELECTRICAL TRACKING | 17 | JUMPER | OKLAHOMA CITY | 5200 SE.56 | CMI_NORMAL | NO | NO | NO | 860316 | 114333 | 71184 | 6938 | 2054 | 0.00029086 | 1.1624e-06 | 250.2333 | 1 | 310 | Customer | 22544 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | #N/A
J2001.004936 |  | NORTHWEST | ENID | 4109:WAUKOMIS | WAUKOMIS 24 | 410924 | 2020-01-13 15:48 | 2020-01-13 17:26 | 97.53 | 3 | 3 | 104.85 | 22 | WIND | 37 | CONDUCTOR PRIMARY - OH | ENID | 4MW, 1.5MS, DRUMMOND | CMI_PLANNED | YES | NO | NO | 860316 | 53506 | 37572 | 1556 | 522 | 0.00012187 | 3.4871e-06 | 34.95 | 1 | 308 | Mainline | 382428 | Fuse | FuseOH | [7 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004940 | PD-01132020-00539 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_526 | 510526 | 2020-01-13 15:52 | 2020-01-13 16:15 | 23.3 | 1 | 1 | 23.3 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ARDMORE | 712 C NW. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77561 | 23571 | 4770 | 1619 | 2.7083e-05 | 1.1624e-06 | 23.3 | 1 | 310 | Customer | 3721 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | OK - 2020
J2001.004945 |  | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5622 | 865622 | 2020-01-13 15:55 | 2020-01-13 20:09 | 253.37 | 1 | 1 | 253.3667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 4700 SE.59 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 159005 | 102090 | 2747 | 264 | 0.0002945 | 1.1624e-06 | 253.3667 | 1 | 310 | Load | 21805 | Load | TranOH3phDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004950 | PD-01132020-00552 | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2923 | 812923 | 2020-01-13 15:57 | 2020-01-13 18:32 | 155.05 | 32 | 20 | 3792 | 13 | PREMATURE FAILURE | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | 100 SOFSW57 ON MAY AV | CMI_NORMAL | NO | NO | NO | 860316 | 159005 | 102090 | 6376 | 1633 | 0.0044077 | 3.7196e-05 | 118.5 | 1 | 310 | Mainline | 27216 | Fuse | FuseRiser | HOWARD GETCHELL | 530-410-8920 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | #N/A
J2001.004956 |  | NORTHEAST | MUSKOGEE | 3326:JAMESVILLE | JAMESVILLE_2642 | 332642 | 2020-01-13 16:09 | 2020-01-13 16:36 | 26.7 | 2 | 1 | 43.3333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | HASKELL | HASKELL | CMI_PLANNED | YES | NO | NO | 860316 | 73958 | 33231 | 1548 | 725 | 5.0369e-05 | 2.3247e-06 | 21.6667 | 1 | 308 | Load | 1812 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | #N/A
J2001.004966 | PD-01132020-00583 | NORTHWEST | ENID | 4256:SINCL BLKWELL | SINCLAIR BLACKWELL 21 | 425621 | 2020-01-13 16:30 | 2020-01-13 19:43 | 192.93 | 1 | 1 | 155.2667 | 23 | CUSTOMER EQUIPMENT | 23 | FUSE - PRIMARY | NARDIN | 1MN,1.5MW-BLACKWELL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 53506 | 37572 | 1 | 1 | 0.00018048 | 1.1624e-06 | 155.2667 | 1 | 310 | Load | 90081 | Load | 0 | DENNIS PEARSON | 580-541-4106 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | #N/A
J2001.004967 | PD-01132020-00584 | METRO NORTH | GUTHRIE | 8819:LIBERTY LAKE | LIBERTY_LAKE_1921 | 881921 | 2020-01-13 16:30 | 2020-01-13 17:26 | 55.88 | 1 | 1 | 55.8833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | GUTHRIE | 7940 E WATERLOO RD | CMI_NORMAL | NO | NO | NO | 860316 | 168058 | 19803 | 3348 | 1524 | 6.4957e-05 | 1.1624e-06 | 55.8833 | 1 | 320 | Load | 252103 | Load | TranOpenDelta | SCOTT C PERRY | 405-258-6044 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004969 | PD-01132020-00594 | SOUTHERN | ARDMORE | 5117:MARIETTA | MARIETTA_1722 | 511722 | 2020-01-13 16:38 | 2020-01-13 17:42 | 63.67 | 1 | 1 | 63.6667 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | MARIETTA | MN11/4W OF THACKRVL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77561 | 23571 | 1594 | 956 | 7.4004e-05 | 1.1624e-06 | 63.6667 | 1 | 310 | Customer | 19470 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | #N/A
J2001.004970 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6126 | 836126 | 2020-01-13 16:39 | 2020-01-13 17:01 | 21.7 | 1 | 1 | 21.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 605.5 NW.31 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168058 | 148255 | 11102 | 456 | 2.5223e-05 | 1.1624e-06 | 21.7 | 1 | 320 | Customer | 35967 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2022
J2001.004968 |  | NORTHEAST | SAPULPA | 3213:BOWDEN | BOWDEN_1329 | 321329 | 2020-01-13 16:39 | 2020-01-13 16:50 | 10.1 | 1 | 1 | 10.1 | 1 | CANCELLED | 57 | CANCELLED | SAPULPA | 6500 97TH W AVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 73958 | 40727 | 3371 | 1516 | 1.174e-05 | 1.1624e-06 | 10.1 | 1 | 310 | Load | 48322 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2020
J2001.004972 | PD-01132020-00590 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5132 | 815132 | 2020-01-13 16:46 | 2020-01-13 18:50 | 124.32 | 1 | 1 | 124.3167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2645 SW.74 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 159005 | 102090 | 13935 | 2003 | 0.0001445 | 1.1624e-06 | 124.3167 | 1 | 310 | Customer | 46791 | Load | Tran1phPad | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004980 | PD-01132020-00600 | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_521 | 560521 | 2020-01-13 16:56 | 2020-01-13 18:22 | 86.33 | 5 | 7 | 356 | 4 | DETERIORATION | 27 | CUTOUT | PAULS VALLEY | 205 N CHESTNUT | CMI_NORMAL | NO | NO | NO | 860316 | 77561 | 6204 | 2455 | 468 | 0.0004138 | 5.8118e-06 | 71.2 | 1 | 310 | Load | 11569 | Load | Tran1phOH | CHAD A DOTSON | 405-488-5658 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | OK - 2022
J2001.005004 |  | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_521 | 560521 | 2020-01-13 16:56 | 2020-01-13 18:26 | 90.13 | 1 | 2 | 90.1333 | 4 | DETERIORATION | 27 | CUTOUT | PAULS VALLEY | 205 N CHESTNUT | CMI_NORMAL | NO | NO | NO | 860316 | 77561 | 6204 | 2455 | 468 | 0.00010477 | 1.1624e-06 | 90.1333 | 1 | 310 | Load | 11569 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | OK - 2022
J2001.004979 | PD-01132020-00598 | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_622 | 730622 | 2020-01-13 16:57 | 2020-01-13 17:44 | 46.67 | 1 | 1 | 41.4167 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | SEMINOLE | 1224 N JEFFERSON | CMI_NORMAL | NO | NO | NO | 860316 | 114333 | 13596 | 4059 | 1252 | 4.8141e-05 | 1.1624e-06 | 41.4167 | 1 | 320 | Customer | 5329 | Load | Tran1phOH | BRADY A HUFF | 405-519-0701 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2020
J2001.004992 | PD-01132020-00608 | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_422 | 580422 | 2020-01-13 17:18 | 2020-01-13 18:53 | 94.6 | 8 | 7 | 619.6333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ADA | 122 E.18 | CMI_NORMAL | NO | NO | NO | 860316 | 77561 | 11504 | 3411 | 1426 | 0.00072024 | 9.2989e-06 | 77.4542 | 1 | 310 | Load | 1344 | Load | Tran1phOH | JORDAN HERBERT-BLUE | 918-839-1152 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.004999 | PD-01132020-00610 | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_623 | 410623 | 2020-01-13 17:54 | 2020-01-13 19:15 | 81.4 | 1 | 1 | 81.4 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ENID | 2705 WESTWIND SQUARE--ENID | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 53506 | 37572 | 6013 | 1546 | 9.4616e-05 | 1.1624e-06 | 81.4 | 1 | 310 | Customer | 8296 | Load | Tran1phPad | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | #N/A
J2001.005000 | PD-01132020-00613 | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1623 | 581623 | 2020-01-13 17:59 | 2020-01-13 19:16 | 77.3 | 1 | 1 | 77.3 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ADA | 1128 S.CHERRY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77561 | 11504 | 3454 | 1649 | 8.9851e-05 | 1.1624e-06 | 77.3 | 1 | 310 | Customer | 4219 | Load | Tran1phOH | JORDAN HERBERT-BLUE | 918-839-1152 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.005003 | PD-01132020-00616 | ARKANSAS | OZARK | 9412:ALTUS | ALTUS_1229 | 941229 | 2020-01-13 18:23 | 2020-01-13 19:49 | 86.02 | 1 | 1 | 83.6667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | OZARK | W-ALTUS, N-CENTER CROSS SCHOOL | CMI_NORMAL | NO | NO | NO | 860316 | 82162 | 7536 | 865 | 865 | 9.7251e-05 | 1.1624e-06 | 83.6667 | 1 | 310 | Load | 17604 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-13 | 2020 |  | Ark - Series 2
J2001.005006 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-01-13 18:34 | 2020-01-13 18:40 | 5.75 | 1 | 1 | 5.75 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4768 NW.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168051 | 148248 | 9238 | 1940 | 6.6836e-06 | 1.1624e-06 | 5.75 | 1 | 310 | Customer | 35037 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2021
J2001.005008 | PD-01132020-00618 | SOUTHERN | MADILL | 5408:CANEY CREEK | CANEY_CREEK_831 | 540831 | 2020-01-13 18:40 | 2020-01-13 19:43 | 63.15 | 1 | 1 | 63.15 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | KINGSTON | 203 S CHICKASAW ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 77559 | 7202 | 1053 | 629 | 7.3403e-05 | 1.1624e-06 | 63.15 | 1 | 310 | Customer | 13831 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.005009 | PD-01132020-00620 | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1731 | 831731 | 2020-01-13 18:44 | 2020-01-13 19:07 | 23.22 | 1 | 1 | 23.2167 | 23 | CUSTOMER EQUIPMENT | 15 | METER - SECONDARY | OKLAHOMA CITY | 12405 INDIAN-CRK BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168051 | 148248 | 6642 | 2017 | 2.6986e-05 | 1.1624e-06 | 23.2167 | 1 | 320 | Customer | 31980 | Load | Tran1phPad | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | #N/A
J2001.005012 | PD-01132020-00626 | NORTHEAST | SAPULPA | 3213:BOWDEN | BOWDEN_1329 | 321329 | 2020-01-13 19:23 | 2020-01-13 20:32 | 68.57 | 2 | 2 | 104.4333 | 12 | POOR CONNECTION | 50 | CONNECTOR | SAPULPA | 6203 S.80-W MIDWAY ACRES B-4 | CMI_NORMAL | NO | NO | NO | 860316 | 73950 | 40727 | 3371 | 1516 | 0.00012139 | 2.3247e-06 | 52.2167 | 1 | 310 | Secondary | 42872 | Load | Tran1phOH | CGI ADMIN | 918-261-6802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2020
J2001.005020 | PD-01132020-00629 | NORTHWEST | ENID | 4123:KREMLIN TAP | KREMLIN TAP 21 | 412321 | 2020-01-13 20:06 | 2020-01-13 21:28 | 81.73 | 1 | 2 | 76.7167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | KREMLIN | 2 BK S-KREMLIN BANK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 53506 | 37572 | 432 | 414 | 8.9173e-05 | 1.1624e-06 | 76.7167 | 1 | 310 | Customer | 4461 | Load | Tran1phOH | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | #N/A
J2001.005027 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6123 | 836123 | 2020-01-13 20:37 | 2020-01-14 01:07 | 269.63 | 1 | 2 | 259.55 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 204 NW.33 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 168051 | 148248 | 11100 | 942 | 0.00030169 | 1.1624e-06 | 259.55 | 1 | 310 | Customer | 13685 | Load | Tran1phOH | Crew | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2020
J2001.005025 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6123 | 836123 | 2020-01-13 20:37 | 2020-01-14 01:07 | 269.38 | 9 | 10 | 2337 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 220 NW.33 | CMI_NORMAL | NO | NO | NO | 860316 | 168051 | 148248 | 11100 | 942 | 0.0027164 | 1.0461e-05 | 259.6667 | 1 | 310 | Load | 1725 | Load | Tran1phOH | Crew | [6 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-13 | 2020 |  | OK - 2020
J2001.005029 | PD-01132020-00646 | METRO WEST | WEST | 8359:YUKON | YUKON_5922 | 835922 | 2020-01-13 20:55 | 2020-01-13 22:39 | 104.27 | 1 | 1 | 104.2667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | YUKON | 106 CORNWELL DR 7 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 128638 | 115906 | 6425 | 1635 | 0.0001212 | 1.1624e-06 | 104.2667 | 1 | 310 | Customer | 24536 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | #N/A
J2001.005030 | PD-01132020-00647 | SOUTHERN | PAULS VALLEY | 5619:RUSH CREEK | RUSH_CREEK_1922 | 561922 | 2020-01-13 21:06 | 2020-01-13 22:05 | 58.57 | 1 | 2 | 55.25 | 4 | DETERIORATION | 20 | FUSE BARREL | PAULS VALLEY | RT 2 BOX 77 | CMI_NORMAL | NO | NO | NO | 860316 | 77559 | 6204 | 2073 | 1193 | 6.4221e-05 | 1.1624e-06 | 55.25 | 1 | 310 | Load | 16127 | Load | Tran1phOH | CHAD A DOTSON | 405-488-5658 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-13 | 2020 |  | OK - 2021
J2001.005047 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_629 | 460629 | 2020-01-13 23:31 | 2020-01-13 23:54 | 23.6 | 1419 | 144 | 33488.4 | 17 | TRANSMISSION OPERATION | 56 | SCADA - LOCKOUT | WOODWARD | 1005 CEDAR AVE | CMI_PLANNED | YES | NO | NO | 860316 | 53506 | 10416 | 5680 | 931 | 0.038926 | 0.0016494 | 23.6 | 1 | 310 | Feeder | CEDAR_AVE_629 | Recloser | 0 | [7 empty] | Equipment | N | TRANSMISSION | 69kV | 2020-01-13 | 2020 |  | #N/A
J2001.005048 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_621 | 460621 | 2020-01-13 23:31 | 2020-01-13 23:42 | 11.08 | 787 | 41 | 8722.5833 | 17 | TRANSMISSION OPERATION | 56 | SCADA - LOCKOUT | WOODWARD | 1005 CEDAR AVE | CMI_PLANNED | YES | NO | NO | 860316 | 53506 | 10416 | 5680 | 787 | 0.010139 | 0.00091478 | 11.0833 | 1 | 310 | Feeder | CEDAR_AVE_621 | Recloser | 0 | [7 empty] | Equipment | N | TRANSMISSION | 69kV | 2020-01-13 | 2020 |  | #N/A
J2001.005056 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_631 | 460631 | 2020-01-13 23:31 | 2020-01-13 23:55 | 24.05 | 1170 | 108 | 28138.5 | 17 | TRANSMISSION OPERATION | 56 | SCADA - LOCKOUT | WOODWARD | 1005 CEDAR AVE | CMI_PLANNED | YES | NO | NO | 860316 | 53506 | 10416 | 5680 | 1170 | 0.032707 | 0.00136 | 24.05 | 1 | 310 | Feeder | CEDAR_AVE_631 | Recloser | 0 | [7 empty] | Equipment | N | TRANSMISSION | 69kV | 2020-01-13 | 2020 |  | #N/A
J2001.005071 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_623 | 460623 | 2020-01-13 23:31 | 2020-01-13 23:42 | 11.52 | 2304 | 121 | 26534.4 | 17 | TRANSMISSION OPERATION | 56 | SCADA - LOCKOUT | WOODWARD | 1005 CEDAR AVE | CMI_PLANNED | YES | NO | NO | 860316 | 53506 | 10416 | 5680 | 1539 | 0.030843 | 0.0026781 | 11.5167 | 1 | 310 | Feeder | CEDAR_AVE_623 | Recloser | 0 | [7 empty] | Equipment | N | TRANSMISSION | 69kV | 2020-01-13 | 2020 |  | #N/A
J2001.005083 |  | ARKANSAS | OZARK | 9224:BRANCH | BRANCH_2463 | 922463 | 2020-01-14 00:05 | 2020-01-14 00:43 | 37.9 | 1 | 1 | 37.9 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | CARBON CITY | HUBCAP RD.-WEST FORK - WEST SD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 82162 | 7536 | 1791 | 820 | 4.4054e-05 | 1.1624e-06 | 37.9 | 1 | 308 | Customer | 15355 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-14 | 2020 |  | Ark - Series 3
J2001.005082 |  | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1222 | 911222 | 2020-01-14 00:15 | 2020-01-14 00:35 | 19.53 | 1 | 1 | 19.5333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 1700 DODSON AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 82162 | 61154 | 6593 | 1285 | 2.2705e-05 | 1.1624e-06 | 19.5333 | 1 | 320 | Customer | 5240 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | Ark - Series 1
J2001.005093 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-14 02:45 | 2020-01-14 02:45 | 0 | 3788 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MULBERRY | 6007 EAST HWY 64 | CMI_MOMENTARY | YES | NO | NO | 860316 | 82162 | 61154 | 3788 | 1204 | 0 | 0.004403 | 0 | 1 | 0 | Feeder | SIMMONS_3062 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-14 | 2020 |  | Ark - Series 2
J2001.005099 |  | ARKANSAS | FORT SMITH | 9115:BATTLEFIELD | BATTLEFIELD_1521 | 911521 | 2020-01-14 03:16 | 2020-01-14 04:00 | 43.98 | 1 | 1 | 43.9833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | CHAPEN DR. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860316 | 82162 | 61154 | 1187 | 1158 | 5.1125e-05 | 1.1624e-06 | 43.9833 | 1 | 308 | Customer | 19157 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-14 | 2020 |  | #N/A
J2001.005096 | PD-01142020-00016 | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1022 | 541022 | 2020-01-14 03:26 | 2020-01-14 09:14 | 348.32 | 1 | 2 | 327.2667 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | MADILL | 308.5 S.12TH AV | CMI_NORMAL | NO | NO | NO | 860316 | 77559 | 7202 | 2379 | 873 | 0.0003804 | 1.1624e-06 | 327.2667 | 1 | 310 | Customer | 16193 | Load | Tran1phOH | DAVID TAYLOR | 580-574-4517 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005103 | PD-01142020-00020 | METRO WEST | WEST | 8158:SARA | SARA_5864 | 815864 | 2020-01-14 04:40 | 2020-01-14 07:29 | 168.43 | 1 | 3 | 23.3333 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 4820 HAMBLETONIAN LN | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860309 | 128638 | 115906 | 18216 | 4810 | 2.7122e-05 | 1.1624e-06 | 23.3333 | 1 | 320 | Customer | 403818 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2022
J2001.005110 | PD-01142020-00026 | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-14 06:36 | 2020-01-14 08:42 | 125.73 | 2 | 1 | 247.6667 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | ARKOMA | ARKOMA | CMI_NORMAL | NO | NO | NO | 860309 | 82162 | 61154 | 2931 | 874 | 0.00028788 | 2.3247e-06 | 123.8333 | 1 | 310 | Tap | 178968 | Fuse | FuseOH | JOHN MEEH | 918-413-0959 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-14 | 2020 |  | Ark - Series 2
J2001.005112 | PD-01142020-00040 | NORTHEAST | SAPULPA | 3214:LONE STAR | LONE_STAR_1422 | 321422 | 2020-01-14 07:15 | 2020-01-14 08:14 | 59.15 | 1 | 1 | 59.15 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SAPULPA | 3907 S HICKORY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 73950 | 40727 | 2654 | 1095 | 6.8754e-05 | 1.1624e-06 | 59.15 | 1 | 310 | Customer | 40087 | Load | Tran1phOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005115 |  | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1022 | 311022 | 2020-01-14 07:37 | 2020-01-14 07:37 | 0 | 1156 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MUSKOGEE | 1541 COUNTRY CLUB PLACE | CMI_MOMENTARY | YES | NO | NO | 860309 | 73950 | 33223 | 2899 | 1093 | 0 | 0.0013437 | 0 | 1 | 0 | Feeder | RIVERSIDE_1022 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-14 | 2020 |  | #N/A
J2001.005116 | PD-01142020-00041 | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1022 | 311022 | 2020-01-14 07:40 | 2020-01-14 11:05 | 205.35 | 1 | 1 | 42.2333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MUSKOGEE | N OF BACONE ON HARRIS RD | CMI_NORMAL | NO | NO | NO | 860309 | 73950 | 33223 | 2899 | 1093 | 4.9091e-05 | 1.1624e-06 | 42.2333 | 1 | 310 | Load | 8541 | Load | Tran1phOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | #N/A
J2001.005119 | PD-01142020-00046 | NORTHEAST | SAPULPA | 3216:BEELINE | BEELINE_1633 | 321633 | 2020-01-14 07:53 | 2020-01-14 11:35 | 221.68 | 1 | 1 | 204.1167 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | GLENPOOL | 5 lots NW of Hartford & 137th PL | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860309 | 73950 | 40727 | 5562 | 1947 | 0.00023726 | 1.1624e-06 | 204.1167 | 1 | 310 | Customer | 363902 | Load | Tran1phPad | CONTRACTOR 5 DAVID ELLIOT INC | 918-639-5055 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005120 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-14 08:04 | 2020-01-14 12:39 | 274.47 | 1 | 1 | 238.5667 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | ES TAYLOR AVE CHAFFEE | CMI_PLANNED | YES | NO | NO | 860309 | 82162 | 61154 | 2732 | 2120 | 0.0002773 | 1.1624e-06 | 238.5667 | 1 | 308 | Load | 200726 | Load | Tran3phWye | Contractor | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | Ark - Series 2
J2001.005127 | PD-01142020-00058 | NORTHEAST | SAPULPA | 3210:HICKORY HILL | HICKORY_HILL_1021 | 321021 | 2020-01-14 08:18 | 2020-01-14 10:07 | 108.82 | 1 | 1 | 108.8167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SAPULPA | 754 N.MOCCASIN ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 73950 | 40727 | 2683 | 1437 | 0.00012649 | 1.1624e-06 | 108.8167 | 1 | 310 | Customer | 45659 | Load | Tran1phOH | CGI ADMIN | 918-261-6802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2022
J2001.005126 | PD-01142020-00061 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-14 08:20 | 2020-01-14 09:32 | 72.03 | 1 | 2 | 15.1311 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DYER | Line Str and Kerkendall | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 82162 | 61154 | 3788 | 1204 | 1.7588e-05 | 1.1624e-06 | 15.1311 | 1 | 320 | Customer | 1258 | Load | Tran1phOH | KRIS L HALMES | 479-430-9447 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-14 | 2020 |  | Ark - Series 2
J2001.005131 | PD-01142020-00075 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2031 | 862031 | 2020-01-14 08:30 | 2020-01-14 11:17 | 166.55 | 1 | 2 | 86.2022 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2520 S.HIGH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 159005 | 102090 | 4741 | 1440 | 0.0001002 | 1.1624e-06 | 86.2022 | 1 | 320 | Load | 14327 | Load | TranOpenDelta | JUSTIN C TAYLOR | 405-534-1006 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2021
J2001.005133 | PD-01142020-00101 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3722 | 833722 | 2020-01-14 08:35 | 2020-01-14 09:51 | 76.32 | 7 | 7 | 364.5833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | NICHOLS HILLS | 1519 GLENWOOD AV | CMI_NORMAL | NO | NO | NO | 860309 | 168051 | 148248 | 5759 | 1109 | 0.00042378 | 8.1366e-06 | 52.0833 | 1 | 310 | Load | 3780 | Load | TranOpenDelta | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2022
J2001.005137 |  | ARKANSAS | FORT SMITH | 9508:WHITESIDE | WHITESIDE_822 | 950822 | 2020-01-14 08:45 | 2020-01-14 14:23 | 337.68 | 3 | 3 | 599.65 | 4 | DETERIORATION | 12 | POLE | VAN BUREN | 2524 GRIFFIN PK CI | CMI_PLANNED | YES | NO | NO | 860309 | 82162 | 61154 | 1919 | 209 | 0.00069702 | 3.4871e-06 | 199.8833 | 1 | 308 | Load | 14791 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-14 | 2020 |  | Ark - Series 2
J2001.005139 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1225 | 831225 | 2020-01-14 08:58 | 2020-01-14 09:46 | 47.85 | 14 | 2 | 451.9667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 2405 NW.54 | CMI_PLANNED | YES | NO | NO | 860309 | 168051 | 148248 | 7738 | 882 | 0.00052535 | 1.6273e-05 | 32.2833 | 1 | 310 | Load | 11556 | Load | TranOHDeltaSplitBank | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2022
J2001.005140 | PD-01142020-00107 | SOUTHERN | ARDMORE | 5109:ARDMORE WEST | ARDMORE_WEST_931 | 510931 | 2020-01-14 08:58 | 2020-01-14 11:13 | 134.92 | 1 | 2 | 131.2667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | ARDMORE | 4303 HESS RD | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860309 | 77559 | 23571 | 1315 | 701 | 0.00015258 | 1.1624e-06 | 131.2667 | 1 | 310 | Customer | 198646 | Load | Tran1phPad | JOE LOFTIS | 918-884-5349 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005144 | PD-01142020-00112 | METRO SOUTH | SOUTH | 8728:CHERRY CREEK | CHERRY_CREEK_2823 | 872823 | 2020-01-14 08:59 | 2020-01-14 12:26 | 207.47 | 1 | 1 | 207.4667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | WS I-35 1/2 M N OF ROBINSON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 159005 | 56915 | 7101 | 1298 | 0.00024115 | 1.1624e-06 | 207.4667 | 1 | 310 | Customer | 78115 | Load | Tran1phPad | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005147 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2123 | 822123 | 2020-01-14 09:02 | 2020-01-14 09:26 | 23.95 | 28 | 0 | 48.7667 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | 3801 NW 20TH ST | CMI_PLANNED | YES | NO | NO | 860309 | 168051 | 148248 | 9238 | 1489 | 5.6685e-05 | 3.2546e-05 | 1.7417 | 1 | 0 | Tap | 19778 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005149 | PD-01142020-00115 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7424 | 847424 | 2020-01-14 09:03 | 2020-01-14 10:26 | 82.8 | 1 | 1 | 82.8 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | OKLAHOMA CITY | NE.48TH + LOTTIE NWC | CMI_NORMAL | NO | NO | NO | 860309 | 168051 | 148248 | 6152 | 2197 | 9.6244e-05 | 1.1624e-06 | 82.8 | 1 | 320 | Load | 24126 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005152 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2123 | 822123 | 2020-01-14 09:07 | 2020-01-14 09:26 | 18.65 | 5 | 0 | 73.2083 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | 2022 N ROFF AV | CMI_PLANNED | YES | NO | NO | 860309 | 168051 | 148248 | 9238 | 1489 | 8.5095e-05 | 5.8119e-06 | 14.6417 | 1 | 0 | Tap | 19779 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005153 |  | METRO NORTH | GUTHRIE | 8813:FITZGERALD CR | FITZGERALD_CR_1342 | 881342 | 2020-01-14 09:09 | 2020-01-14 09:09 | 0 | 808 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | COYLE | N HENNEY RD + E COUNTY RD 73 | CMI_MOMENTARY | YES | NO | NO | 860309 | 168051 | 19803 | 1044 | 808 | 0 | 0.0009392 | 0 | 1 | 0 | Feeder | FITZ CK_1342 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005156 | PD-01142020-00127 | METRO NORTH | GUTHRIE | 8813:FITZGERALD CR | FITZGERALD_CR_1342 | 881342 | 2020-01-14 09:13 | 2020-01-14 10:13 | 59.83 | 2 | 3 | 106.9167 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | LANGSTON | LANGSTON OK | CMI_NORMAL | NO | NO | NO | 860309 | 168051 | 19803 | 1044 | 808 | 0.00012428 | 2.3247e-06 | 53.4583 | 1 | 310 | Secondary | 32188 | Load | Tran1phOH | KELLEY D WATSON | 405-763-8148 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005157 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-14 09:15 | 2020-01-14 09:21 | 6.63 | 2154 | 127 | 14288.2 | 6 | HOT LINE HOLD ORDER | 45 | SUBSTATION CIRCUIT | FT SMITH | 4699 S ZERO ST | CMI_NORMAL | NO | NO | NO | 860309 | 82162 | 61154 | 2732 | 2120 | 0.016608 | 0.0025038 | 6.6333 | 1 | 310 | Feeder | CARNALL_2564 | Recloser | SubRecloser | [7 empty] | Other | N | SUBSTATION | 69kV | 2020-01-14 | 2020 |  | Ark - Series 2
J2001.005178 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-14 09:15 | 2020-01-14 13:27 | 252.3 | 14 | 1 | 3478.5333 | 4 | DETERIORATION | 1 | TRANSFORMER UG | LAVACA | RURAL-HOLT ADD.1900 EOF RVRD. | CMI_PLANNED | YES | NO | NO | 860309 | 82162 | 61154 | 2732 | 2120 | 0.0040434 | 1.6273e-05 | 248.4667 | 1 | 310 | Load | 1295 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | Ark - Series 2
J2001.005159 | PD-01142020-00148 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-01-14 09:15 | 2020-01-14 12:08 | 172.52 | 1 | 1 | 172.5167 | 5 | ELECTRICAL TRACKING | 21 | FUSE - TRANSFORMER | MOUNTAINBURG | OLD SHEPHERD SPRINGS RD | CMI_NORMAL | NO | NO | NO | 860309 | 82162 | 61154 | 3788 | 1204 | 0.00020053 | 1.1624e-06 | 172.5167 | 1 | 310 | Load | 220489 | Load | TranOH3phDelta | KRIS L HALMES | 479-430-9447 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-14 | 2020 |  | Ark - Series 2
J2001.005160 |  | SOUTHERN | DURANT | 5512:COLBERT | COLBERT_1222 | 551222 | 2020-01-14 09:18 | 2020-01-14 11:18 | 120.7 | 3 | 0 | 82.85 | 4 | DETERIORATION | 2 | TRANSFORMER OH | COLBERT | BOX 24 | CMI_PLANNED | YES | NO | NO | 860309 | 77559 | 15478 | 2165 | 1270 | 9.6303e-05 | 3.4871e-06 | 27.6167 | 1 | 0 | Load | 14263 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005161 |  | SOUTHERN | DURANT | 5512:COLBERT | COLBERT_1222 | 551222 | 2020-01-14 09:18 | 2020-01-14 11:55 | 157.52 | 3 | 1 | 425.05 | 4 | DETERIORATION | 12 | POLE | COLBERT | LEECRAFT + SMITH | CMI_PLANNED | YES | NO | NO | 860309 | 77559 | 15478 | 2165 | 1270 | 0.00049407 | 3.4871e-06 | 141.6833 | 1 | 308 | Load | 18297 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005163 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-14 09:19 | 2020-01-14 12:22 | 183.3 | 2 | 1 | 358.7333 | 4 | DETERIORATION | 12 | POLE | HARTMAN | HARTMAN | CMI_PLANNED | YES | NO | NO | 860309 | 82162 | 7536 | 1504 | 1200 | 0.00041698 | 2.3247e-06 | 179.3667 | 1 | 308 | Load | 2404 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-14 | 2020 |  | Ark - Series 2
J2001.005164 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-14 09:19 | 2020-01-14 12:22 | 182.93 | 2 | 0 | 358.5 | 4 | DETERIORATION | 12 | POLE | HARTMAN | HARTMAN | CMI_PLANNED | YES | NO | NO | 860309 | 82162 | 7536 | 1504 | 1200 | 0.00041671 | 2.3247e-06 | 179.25 | 1 | 0 | Load | 13990 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-14 | 2020 |  | Ark - Series 2
J2001.005171 | PD-01142020-00154 | NORTHEAST | SAPULPA | 7610:PRINCEVILLE | PRINCEVILLE_1021 | 761021 | 2020-01-14 09:23 | 2020-01-14 14:12 | 289.43 | 1 | 2 | 272.6667 | 25 | LIGHTNING | 31 | CONDUCTOR SERVICE - OH | FREEDOM HILL | 1 3/4MN OF JCT 33-48 (ES) | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860309 | 73950 | 40727 | 304 | 304 | 0.00031694 | 1.1624e-06 | 272.6667 | 1 | 320 | Load | 18832 | Load | Tran1phOH | GREGORY R HOOVER | 918-261-6803 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | #N/A
J2001.005177 |  | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2024 | 822024 | 2020-01-14 09:26 | 2020-01-14 09:32 | 6.05 | 1 | 1 | 6.05 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2404 N.LINN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 168051 | 148248 | 6034 | 1774 | 7.0324e-06 | 1.1624e-06 | 6.05 | 1 | 310 | Customer | 7787 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005174 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2229 | 852229 | 2020-01-14 09:26 | 2020-01-14 10:25 | 58.82 | 7 | 1 | 194.95 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | HARRAH | 5504 W.LAKEVIEW DR | CMI_PLANNED | YES | NO | NO | 860309 | 114330 | 71183 | 11623 | 1387 | 0.0002266 | 8.1366e-06 | 27.85 | 1 | 308 | Load | 45679 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005179 | PD-01142020-00142 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7424 | 847424 | 2020-01-14 09:30 | 2020-01-14 10:14 | 44.05 | 1 | 2 | 44.05 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4900 N.LINCOLN BLVD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 168051 | 148248 | 6152 | 2197 | 5.1203e-05 | 1.1624e-06 | 44.05 | 1 | 321 | Load | 69594 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005185 | PD-01142020-00146 | NORTHWEST | ENID | 4107:CLEVELAND AVE | CLEVELAND_AVE_722 | 410722 | 2020-01-14 09:34 | 2020-01-14 10:43 | 69.22 | 1 | 2 | 65.3 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | ENID | 801 W. OKLAHOMA ST. | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860309 | 53506 | 37572 | 4460 | 1378 | 7.5903e-05 | 1.1624e-06 | 65.3 | 1 | 320 | Customer | 15424 | Load | Tran1phOH | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | #N/A
J2001.005186 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2122 | 822122 | 2020-01-14 09:37 | 2020-01-14 09:49 | 12.65 | 46 | 0 | 173.2667 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | 4105 NW 20TH ST | CMI_PLANNED | YES | NO | NO | 860309 | 168051 | 148248 | 9238 | 2013 | 0.0002014 | 5.3469e-05 | 3.7667 | 1 | 0 | Tap | 16915 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005189 | PD-01142020-00157 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7423 | 847423 | 2020-01-14 09:42 | 2020-01-14 11:41 | 119.25 | 1 | 2 | 43.298 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 1608 NE.27 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860309 | 168051 | 148248 | 6152 | 1286 | 5.0328e-05 | 1.1624e-06 | 43.298 | 1 | 320 | Customer | 24475 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2022
J2001.005191 |  | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2022 | 822022 | 2020-01-14 09:44 | 2020-01-14 10:34 | 50.7 | 1 | 1 | 50.7 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 2341 W.LINDLEY | CMI_PLANNED | YES | NO | NO | 860309 | 168051 | 148248 | 6034 | 2119 | 5.8932e-05 | 1.1624e-06 | 50.7 | 1 | 310 | Customer | 10492 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005193 | PD-01142020-00159 | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_621 | 880621 | 2020-01-14 09:50 | 2020-01-14 13:28 | 218.38 | 1 | 1 | 187.6333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | GUTHRIE | 6MS 1/4ME PINE ST | CMI_NORMAL | NO | NO | NO | 860309 | 168051 | 19803 | 5161 | 1876 | 0.0002181 | 1.1624e-06 | 187.6333 | 1 | 310 | Load | 32435 | Load | Tran1phOH | DENNY J MORGAN | 405-501-1556 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005199 |  | NORTHWEST | ENID | 4461:TURKEY CREEK | TURKEY_CREEK_6121 | 446121 | 2020-01-14 10:02 | 2020-01-14 11:39 | 97.2 | 1 | 1 | 93.6333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | DOVER | HW81 AND BOUNDRY | CMI_PLANNED | YES | NO | NO | 860309 | 53506 | 37572 | 436 | 416 | 0.00010884 | 1.1624e-06 | 93.6333 | 1 | 308 | Load | 193225 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | #N/A
J2001.005200 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6324 | 816324 | 2020-01-14 10:05 | 2020-01-14 10:21 | 16.47 | 1 | 1 | 16.4667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MOORE | 800 NW.12 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 159005 | 102090 | 11814 | 2048 | 1.914e-05 | 1.1624e-06 | 16.4667 | 1 | 310 | Customer | 48396 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2021
J2001.005201 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-14 10:07 | 2020-01-14 13:48 | 220.83 | 4 | 1 | 779.9667 | 4 | DETERIORATION | 12 | POLE | HARTMAN | 7004 US HWY 64 | CMI_PLANNED | YES | NO | NO | 860309 | 82162 | 7536 | 1504 | 1200 | 0.00090661 | 4.6495e-06 | 194.9917 | 1 | 308 | Load | 5316 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-14 | 2020 |  | Ark - Series 2
J2001.005205 | PD-01142020-00169 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2029 | 862029 | 2020-01-14 10:13 | 2020-01-14 10:57 | 44.25 | 1 | 1 | 44.25 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 412 SE.20 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 159005 | 102090 | 4741 | 982 | 5.1435e-05 | 1.1624e-06 | 44.25 | 1 | 320 | Customer | 12706 | Load | Tran1phOH | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005204 |  | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_423 | 710423 | 2020-01-14 10:14 | 2020-01-14 11:36 | 81.8 | 3 | 2 | 243.75 | 4 | DETERIORATION | 2 | TRANSFORMER OH | CHANDLER | 346480 E890 Rd | CMI_PLANNED | YES | NO | NO | 860309 | 114330 | 7458 | 2820 | 975 | 0.00028333 | 3.4871e-06 | 81.25 | 1 | 308 | Mainline | 7939 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005206 |  | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-01-14 10:19 | 2020-01-14 13:00 | 161.23 | 2 | 2 | 286.8 | 4 | DETERIORATION | 12 | POLE | EL RENO | 301 W.JONES RD | CMI_PLANNED | YES | NO | NO | 860309 | 128638 | 12732 | 6934 | 1823 | 0.00033337 | 2.3247e-06 | 143.4 | 1 | 308 | Load | 34933 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005208 |  | METRO EAST | SHAWNEE | 7412:PEARSON | PEARSON 21 | 741221 | 2020-01-14 10:23 | 2020-01-14 12:49 | 145.83 | 2 | 0 | 57.9667 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | ST. LOUIS | 1BLK E OF CAFE | CMI_PLANNED | YES | NO | NO | 860309 | 114330 | 22093 | 677 | 677 | 6.7379e-05 | 2.3247e-06 | 28.9833 | 1 | 0 | Load | 13031 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | OK - 2021
J2001.005214 | PD-01142020-00201 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7031 | 817031 | 2020-01-14 10:39 | 2020-01-14 11:49 | 70.12 | 1 | 1 | 70.1167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 424 SW.92 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 159005 | 102090 | 9938 | 1891 | 8.1502e-05 | 1.1624e-06 | 70.1167 | 1 | 320 | Customer | 62801 | Load | Tran1phPad | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005216 |  | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2822 | 312822 | 2020-01-14 10:48 | 2020-01-14 10:59 | 11.8 | 1 | 1 | 11.8 | 1 | CANCELLED | 57 | CANCELLED | MUSKOGEE | COBBLESTONE VILLAS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 73950 | 33223 | 5271 | 1107 | 1.3716e-05 | 1.1624e-06 | 11.8 | 1 | 310 | Customer | 209207 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005218 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-14 10:51 | 2020-01-14 18:38 | 466.97 | 3 | 0 | 1296.1 | 4 | DETERIORATION | 12 | POLE | ARKOMA | 421 SUMNER | CMI_PLANNED | YES | NO | NO | 860309 | 82162 | 61154 | 2931 | 874 | 0.0015066 | 3.4871e-06 | 432.0333 | 1 | 0 | Load | 782 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-14 | 2020 |  | Ark - Series 2
J2001.005220 | PD-01142020-00221 | METRO WEST | WEST | 8342:BRADEN PARK | BRADEN_PARK_4223 | 834223 | 2020-01-14 10:56 | 2020-01-14 12:41 | 105.47 | 1 | 1 | 105.4667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6200 W. Memorial Rd. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 128638 | 115906 | 3397 | 1781 | 0.00012259 | 1.1624e-06 | 105.4667 | 1 | 320 | Customer | 387518 | Load | Tran3phPadWye | REX R WILSON | 405-535-4507 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2022
J2001.005224 | PD-01142020-00244 | NORTHEAST | SAPULPA | 3218:BEGGS | BEGGS_1829 | 321829 | 2020-01-14 11:02 | 2020-01-14 14:15 | 193.3 | 1 | 1 | 173.45 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | MOUNDS | BETWN ROCKWOOD+ BLAND N.OF 8TH | CMI_NORMAL | NO | NO | NO | 860309 | 73950 | 40727 | 1833 | 896 | 0.00020161 | 1.1624e-06 | 173.45 | 1 | 320 | Customer | 42632 | Load | Tran1phOH | JOSHUA N MCKINNEY | 918-863-6313 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005238 | PD-01142020-00239 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-01-14 11:05 | 2020-01-14 12:22 | 77.22 | 208 | 91 | 13679.4667 | 13 | PREMATURE FAILURE | 23 | FUSE - PRIMARY | OKLAHOMA CITY | NW 23RD + MINNIE LANE | CMI_NORMAL | NO | NO | NO | 860309 | 168051 | 148248 | 9238 | 1940 | 0.015901 | 0.00024177 | 65.7667 | 1 | 310 | Mainline | 19827 | Fuse | FuseOH | STEVEN GILES | 405-227-2802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2021
J2001.005226 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-01-14 11:05 | 2020-01-14 11:05 | 0.07 | 1958 | 0 | 130.5333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 4431 NW 10TH ST | CMI_MOMENTARY | YES | NO | NO | 860309 | 168051 | 148248 | 9238 | 1940 | 0.00015173 | 0.0022759 | 0.066667 | 1 | 0 | Feeder | MERIDIAN_2128 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-14 | 2020 |  | OK - 2021
J2001.005246 | PD-01142020-00270 | METRO EAST | EAST | 8471:NE 30TH ST | NE_30TH_ST_7122 | 847122 | 2020-01-14 11:06 | 2020-01-14 11:59 | 52.97 | 1 | 2 | 47.0667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | FOREST PARK | 3708 KINGS-ROW | CMI_NORMAL | NO | NO | NO | 860309 | 114330 | 71183 | 2398 | 766 | 5.4709e-05 | 1.1624e-06 | 47.0667 | 1 | 310 | Customer | 18442 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | OK - 2022
J2001.005232 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4035 | 834035 | 2020-01-14 11:13 | 2020-01-14 11:18 | 5.48 | 1 | 1 | 5.4833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | *400 E MACARTHUR-400 N HEFNER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 128638 | 115906 | 10841 | 1423 | 6.3737e-06 | 1.1624e-06 | 5.4833 | 1 | 310 | Customer | 73182 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005247 | PD-01142020-00286 | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2923 | 812923 | 2020-01-14 11:21 | 2020-01-14 12:07 | 45.53 | 1 | 1 | 45.5333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2725 SW.56 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 159005 | 102090 | 6376 | 1633 | 5.2927e-05 | 1.1624e-06 | 45.5333 | 1 | 310 | Customer | 36476 | Load | Tran1phOH | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | #N/A
J2001.005251 | PD-01142020-00269 | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5631 | 865631 | 2020-01-14 11:27 | 2020-01-14 12:08 | 40.85 | 1 | 1 | 40.85 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 4924 SE.58 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 159005 | 102090 | 2747 | 374 | 4.7483e-05 | 1.1624e-06 | 40.85 | 1 | 310 | Customer | 25451 | Load | Tran1phPad | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005257 | PD-01142020-00304 | NORTHEAST | MUSKOGEE | 3312:CHECOTAH | CHECOTAH 22 | 331222 | 2020-01-14 11:42 | 2020-01-14 12:46 | 64.1 | 1 | 2 | 13.3833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ONAPA | 4-MANS COVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 73950 | 33223 | 2883 | 1527 | 1.5556e-05 | 1.1624e-06 | 13.3833 | 1 | 310 | Customer | 8797 | Load | Tran1phOH | NICHOLAS SELVIDGE | 918-652-1986 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005260 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2129 | 822129 | 2020-01-14 11:48 | 2020-01-14 12:49 | 61.07 | 1 | 1 | 22.5667 | 13 | PREMATURE FAILURE | 23 | FUSE - PRIMARY | OKLAHOMA CITY | 2223 N.MERIDIAN | CMI_NORMAL | NO | NO | NO | 860309 | 168051 | 148248 | 9238 | 1557 | 2.6231e-05 | 1.1624e-06 | 22.5667 | 1 | 310 | Customer | 20330 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005269 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2129 | 822129 | 2020-01-14 12:08 | 2020-01-14 12:50 | 41.1 | 1 | 1 | 2.1 | 13 | PREMATURE FAILURE | 23 | FUSE - PRIMARY | OKLAHOMA CITY | 2221 N.MERIDIAN | CMI_NORMAL | NO | NO | NO | 860309 | 168051 | 148248 | 9238 | 1557 | 2.441e-06 | 1.1624e-06 | 2.1 | 1 | 310 | Customer | 13286 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005275 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6963 | 846963 | 2020-01-14 12:28 | 2020-01-14 12:35 | 7.62 | 1 | 1 | 7.6167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 250 W-KEYSTONE CI,NS-VAIL CI | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 168051 | 148248 | 7717 | 1170 | 8.8534e-06 | 1.1624e-06 | 7.6167 | 1 | 310 | Customer | 69705 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005281 |  | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3722 | 913722 | 2020-01-14 12:45 | 2020-01-14 13:51 | 66.32 | 4 | 3 | 257.2 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 5700 GORDON LN | CMI_PLANNED | YES | NO | NO | 860309 | 82162 | 61154 | 4565 | 1438 | 0.00029896 | 4.6495e-06 | 64.3 | 1 | 308 | Load | 6925 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | Ark - Series 3
J2001.005283 | PD-01142020-00352 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6963 | 846963 | 2020-01-14 12:48 | 2020-01-14 13:24 | 36.33 | 1 | 1 | 36.3333 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 250 W-KEYSTONE CI,NS-VAIL CI | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 168051 | 148248 | 7717 | 1170 | 4.2233e-05 | 1.1624e-06 | 36.3333 | 1 | 310 | Customer | 69705 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005285 | PD-01142020-00354 | SOUTHERN | ADA | 5813:BYNG SPA | BYNG_SPA_1322 | 581322 | 2020-01-14 12:49 | 2020-01-14 14:44 | 115.23 | 1 | 1 | 115.2333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FRANCIS | FRANCIS #1 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 77559 | 11504 | 546 | 546 | 0.00013394 | 1.1624e-06 | 115.2333 | 1 | 310 | Customer | 8179 | Load | Tran1phOH | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | #N/A
J2001.005287 |  | ARKANSAS | FORT SMITH | 9111:MASSARD | MASSARD_1122 | 911122 | 2020-01-14 12:52 | 2020-01-14 13:49 | 56.88 | 4 | 4 | 122.0333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 2200 S 66th | CMI_PLANNED | YES | NO | NO | 860309 | 82162 | 61154 | 4983 | 947 | 0.00014185 | 4.6495e-06 | 30.5083 | 1 | 308 | Load | 6293 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-14 | 2020 |  | Ark - Series 3
J2001.005301 | PD-01142020-00367 | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1621 | 581621 | 2020-01-14 12:56 | 2020-01-14 14:16 | 79.77 | 3 | 5 | 214.3 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | ADA | 830 W.1 | CMI_NORMAL | NO | NO | NO | 860309 | 77559 | 11504 | 3454 | 1805 | 0.0002491 | 3.4871e-06 | 71.4333 | 1 | 310 | Load | 5268 | Load | Tran1phOH | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005293 | PD-01142020-00361 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3022 | 743022 | 2020-01-14 13:01 | 2020-01-14 14:27 | 86.38 | 1 | 1 | 86.3833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | SHAWNEE | 1501 N MARKET | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 114330 | 22093 | 6640 | 2163 | 0.00010041 | 1.1624e-06 | 86.3833 | 1 | 310 | Customer | 3458 | Load | Tran1phOH | BRYAN K TATUM | 405-659-0746 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005292 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-01-14 13:01 | 2020-01-14 13:07 | 6.02 | 1 | 1 | 6.0167 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 4730 NW.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 168051 | 148248 | 9238 | 1940 | 6.9936e-06 | 1.1624e-06 | 6.0167 | 1 | 310 | Customer | 42440 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2021
J2001.005304 | PD-01142020-00372 | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1024 | 311024 | 2020-01-14 13:04 | 2020-01-14 14:43 | 99.07 | 1 | 3 | 94.3833 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | MUSKOGEE | 1220 EDMOND | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860309 | 73950 | 33223 | 2899 | 1390 | 0.00010971 | 1.1624e-06 | 94.3833 | 1 | 310 | Customer | 11161 | Load | Tran1phOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005295 | PD-01142020-00366 | METRO WEST | EL RENO | 8908:ROMAN NOSE | ROMAN_NOSE_847 | 890847 | 2020-01-14 13:05 | 2020-01-14 16:38 | 212.65 | 1 | 1 | 212.65 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | GEARY | 3.4MN .25MW of Geary on HWY 281 | CMI_NORMAL | NO | NO | NO | 860309 | 128638 | 12732 | 524 | 214 | 0.00024718 | 1.1624e-06 | 212.65 | 1 | 310 | Load | 338751 | Load | Tran1phOH | BRANDON H SMITH | 405-371-4294 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005297 |  | ARKANSAS | OZARK | 9230:SHORT MTN | SHORT_MOUNTAIN_3061 | 923061 | 2020-01-14 13:06 | 2020-01-14 13:33 | 26.55 | 12 | 4 | 318.4 | 22 | WIND | 12 | POLE | SUBIACO | 7092 E AR HWY 22 | CMI_NORMAL | NO | NO | NO | 860309 | 82162 | 7536 | 367 | 367 | 0.0003701 | 1.3948e-05 | 26.5333 | 1 | 310 | Mainline | 409130 | Recloser | Rec3phElectronic | [7 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | #N/A
J2001.005306 | PD-01142020-00380 | METRO NORTH | GUTHRIE | 8819:LIBERTY LAKE | LIBERTY_LAKE_1923 | 881923 | 2020-01-14 13:07 | 2020-01-14 14:07 | 59.6 | 11 | 7 | 606.8333 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | GUTHRIE | .6 MN of Charter Oak Rd on ES of Kelly Ave | CMI_NORMAL | NO | NO | NO | 860309 | 168051 | 19803 | 3348 | 1824 | 0.00070537 | 1.2786e-05 | 55.1667 | 1 | 310 | Mainline | 337732 | Fuse | FuseRiser | KELLEY D WATSON | 405-763-8148 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005312 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-01-14 13:32 | 2020-01-14 14:14 | 42.83 | 1 | 1 | 42.8333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4730 NW.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 168051 | 148248 | 9238 | 1940 | 4.9788e-05 | 1.1624e-06 | 42.8333 | 1 | 315 | Customer | 42440 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2021
J2001.005314 | PD-01142020-00393 | METRO SOUTH | SOUTH | 8728:CHERRY CREEK | CHERRY_CREEK_2823 | 872823 | 2020-01-14 13:34 | 2020-01-14 14:38 | 63.75 | 1 | 1 | 63.75 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | WS I-35 1/2 M N OF ROBINSON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 159005 | 56915 | 7101 | 1298 | 7.4101e-05 | 1.1624e-06 | 63.75 | 1 | 310 | Customer | 78115 | Load | Tran1phPad | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005316 | PD-01142020-00401 | ARKANSAS | FORT SMITH | 9508:WHITESIDE | WHITESIDE_821 | 950821 | 2020-01-14 13:41 | 2020-01-14 14:44 | 63.08 | 1 | 1 | 63.0833 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | VAN BUREN | 1012 N 20TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 82162 | 61154 | 1919 | 1281 | 7.3326e-05 | 1.1624e-06 | 63.0833 | 1 | 310 | Customer | 11974 | Load | Tran1phOH | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-14 | 2020 |  | Ark - Series 2
J2001.005318 | PD-01142020-00409 | METRO EAST | CHANDLER | 7119:WARWICK | WARWICK_1942 | 711942 | 2020-01-14 13:48 | 2020-01-14 15:24 | 96.12 | 1 | 1 | 90.7 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | CARNEY | 112 COX ST | CMI_NORMAL | NO | NO | NO | 860309 | 114330 | 7458 | 2417 | 956 | 0.00010543 | 1.1624e-06 | 90.7 | 1 | 310 | Load | 12176 | Load | Tran1phOH | SCOTT C PERRY | 405-258-6044 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2022
J2001.005320 |  | ARKANSAS | FORT SMITH | 9111:MASSARD | MASSARD_1122 | 911122 | 2020-01-14 13:50 | 2020-01-14 14:19 | 29.73 | 6 | 4 | 125 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 6721 EUPER LN | CMI_PLANNED | YES | NO | NO | 860309 | 82162 | 61154 | 4983 | 947 | 0.0001453 | 6.9742e-06 | 20.8333 | 1 | 308 | Load | 15069 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-14 | 2020 |  | Ark - Series 3
J2001.005328 |  | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3724 | 913724 | 2020-01-14 14:05 | 2020-01-14 15:51 | 105.72 | 4 | 5 | 94.2 | 28 | OTHER (DESCRIBE) | 2 | TRANSFORMER OH | FORT SMITH | 400 N.49 | CMI_PLANNED | YES | NO | NO | 860309 | 82162 | 61154 | 4565 | 896 | 0.0001095 | 4.6495e-06 | 23.55 | 1 | 310 | Load | 12264 | Load | Tran1phOH | OGE | [6 empty] | Other | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | Ark - Series 3
J2001.005331 | PD-01142020-00448 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2022 | 862022 | 2020-01-14 14:10 | 2020-01-14 14:46 | 35.67 | 1 | 1 | 35.6667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 24 SE 26TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 159005 | 102090 | 4741 | 1550 | 4.1458e-05 | 1.1624e-06 | 35.6667 | 1 | 310 | Customer | 5710 | Load | TranOpenDelta | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005335 | PD-01142020-00449 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-01-14 14:18 | 2020-01-14 15:47 | 89.07 | 1 | 1 | 89.0667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1329 NW 23RD ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 168051 | 148248 | 11100 | 2036 | 0.00010353 | 1.1624e-06 | 89.0667 | 1 | 320 | Load | 2830 | Load | TranPad3phDelta | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2021
J2001.005336 |  | ARKANSAS | FORT SMITH | 9111:MASSARD | MASSARD_1122 | 911122 | 2020-01-14 14:20 | 2020-01-14 16:07 | 106.7 | 4 | 2 | 370.5333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 1214 S 74th | CMI_PLANNED | YES | NO | NO | 860309 | 82162 | 61154 | 4983 | 947 | 0.0004307 | 4.6495e-06 | 92.6333 | 1 | 308 | Load | 11573 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-14 | 2020 |  | Ark - Series 3
J2001.005343 | PD-01142020-00463 | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-01-14 14:25 | 2020-01-14 15:40 | 75.4 | 1 | 1 | 75.4 | 4 | DETERIORATION | 50 | CONNECTOR | CALUMET | .5MS 2ME SS R | CMI_NORMAL | NO | NO | NO | 860309 | 128638 | 12732 | 6934 | 1823 | 8.7643e-05 | 1.1624e-06 | 75.4 | 1 | 320 | Load | 34338 | Load | Tran1phOH | BRANDON H SMITH | 405-371-4294 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005341 | PD-01142020-00482 | ARKANSAS | OZARK | 9413:RAZORBACK | RAZORBACK_1362 | 941362 | 2020-01-14 14:25 | 2020-01-14 15:25 | 60.4 | 396 | 133 | 7769.5333 | 29 | TREES : GROW IN | 45 | SUBSTATION CIRCUIT | SUBIACO | 2426 E STATE HWY 288 | CMI_NORMAL | NO | NO | NO | 860309 | 82162 | 7536 | 396 | 396 | 0.0090311 | 0.0004603 | 19.62 | 1 | 310 | Feeder | RAZORBCK_1362 | Recloser | SubRecloser | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Vegetation | N | SUBSTATION | 69kV | 2020-01-14 | 2020 |  | Ark - Series 2
J2001.005342 | PD-01142020-00471 | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_421 | 710421 | 2020-01-14 14:26 | 2020-01-14 16:06 | 100.15 | 1 | 1 | 100.15 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | CHANDLER | BEHIND LOT 6 QUAIL RUN ADD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 114330 | 7458 | 2820 | 1172 | 0.00011641 | 1.1624e-06 | 100.15 | 1 | 310 | Customer | 18630 | Load | Tran1phPad | SCOTT C PERRY | 405-258-6044 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2021
J2001.005349 | PD-01142020-00494 | NORTHEAST | SAPULPA | 3218:BEGGS | BEGGS_1829 | 321829 | 2020-01-14 14:47 | 2020-01-14 16:12 | 85.42 | 1 | 2 | 85.4167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MOUNDS | L11 STAGG ACRES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 73950 | 40727 | 1833 | 896 | 9.9286e-05 | 1.1624e-06 | 85.4167 | 1 | 310 | Customer | 41987 | Load | Tran1phOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005353 | PD-01142020-00486 | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1373 | 831373 | 2020-01-14 14:49 | 2020-01-14 20:03 | 313.55 | 126 | 40 | 14601.3 | 4 | DETERIORATION | 1 | TRANSFORMER UG | YUKON | SKY TRAIL + NW 5R0TH | CMI_NORMAL | NO | NO | NO | 860309 | 128638 | 115906 | 7870 | 4095 | 0.016972 | 0.00014646 | 115.8833 | 1 | 310 | Mainline | 24772 | Fuse | FuseRiser | JESSE PHILLER | 405-512-8086 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005412 |  | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1373 | 831373 | 2020-01-14 14:49 | 2020-01-14 20:05 | 315.13 | 16 | 17 | 4925.3333 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | S OF NW 50TH - ES SARA | CMI_NORMAL | NO | NO | NO | 860309 | 128638 | 115906 | 7870 | 4095 | 0.0057251 | 1.8598e-05 | 307.8333 | 1 | 310 | Mainline | 27297 | Fuse | FuseRiser | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005359 | PD-01142020-00500 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_723 | 870723 | 2020-01-14 15:01 | 2020-01-14 17:09 | 127.52 | 3 | 4 | 382.55 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | Jenkins Ave. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 159005 | 56915 | 11831 | 2043 | 0.00044467 | 3.4871e-06 | 127.5167 | 1 | 310 | Secondary | 33749 | Load | Tran1phOH | THOMAS E COLE | 405-623-9338 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005358 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_823 | 870823 | 2020-01-14 15:01 | 2020-01-14 17:45 | 163.82 | 3 | 2 | 219.85 | 4 | DETERIORATION | 2 | TRANSFORMER OH | NORMAN | 1617 JENKINS AV | CMI_PLANNED | YES | NO | NO | 860309 | 159005 | 56915 | 6775 | 2380 | 0.00025555 | 3.4871e-06 | 73.2833 | 1 | 308 | Load | 33750 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005361 | PD-01142020-00511 | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2823 | 312823 | 2020-01-14 15:13 | 2020-01-14 16:59 | 106.45 | 1 | 1 | 106.45 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | MUSKOGEE | 2107 DELAWARE | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860309 | 73950 | 33223 | 5271 | 1391 | 0.00012373 | 1.1624e-06 | 106.45 | 1 | 310 | Customer | 9152 | Load | Tran1phOH | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-14 | 2020 |  | #N/A
J2001.005362 | PD-01142020-00499 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3925 | 833925 | 2020-01-14 15:14 | 2020-01-14 18:57 | 222.82 | 1 | 2 | 167.95 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | WARR ACRES | 6200 NORMAN RD | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860309 | 168051 | 148248 | 7847 | 2182 | 0.00019522 | 1.1624e-06 | 167.95 | 1 | 320 | Customer | 14246 | Load | Tran1phOH | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2022
J2001.005365 | PD-01142020-00512 | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1421 | 911421 | 2020-01-14 15:15 | 2020-01-14 16:32 | 76.78 | 1 | 2 | 76.7833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 2301 N.30 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 82162 | 61154 | 4737 | 1746 | 8.9251e-05 | 1.1624e-06 | 76.7833 | 1 | 310 | Customer | 8576 | Load | Tran1phOH | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-14 | 2020 |  | Ark - Series 1
J2001.005363 | PD-01142020-00503 | METRO NORTH | GUTHRIE | 8807:CRESCENT | CRESCENT_723 | 880723 | 2020-01-14 15:23 | 2020-01-14 18:23 | 179.57 | 1 | 1 | 179.5667 | 12 | POOR CONNECTION | 50 | CONNECTOR | CASHION | 306 S MAIN ST | CMI_NORMAL | NO | NO | NO | 860309 | 168051 | 19803 | 1762 | 890 | 0.00020872 | 1.1624e-06 | 179.5667 | 1 | 320 | Customer | 206243 | Load | Tran3phWye | SCOTT C PERRY | 405-258-6044 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005367 | PD-01142020-00507 | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_422 | 580422 | 2020-01-14 15:33 | 2020-01-14 16:27 | 54.12 | 1 | 1 | 52.2167 | 27 | TREE:NON PREVENTABLE | 21 | FUSE - TRANSFORMER | ADA | 911 S.BDWY | CMI_NORMAL | NO | NO | NO | 860309 | 77559 | 11504 | 3411 | 1426 | 6.0695e-05 | 1.1624e-06 | 52.2167 | 1 | 310 | Customer | 1971 | Load | Tran1phOH | JORDAN HERBERT-BLUE | 918-839-1152 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005368 | PD-01142020-00515 | METRO SOUTH | SOUTH CENTRAL | 8723:INDIAN HILL | INDIAN_HILL_2323 | 872323 | 2020-01-14 15:37 | 2020-01-14 16:51 | 73.85 | 1 | 1 | 73.85 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MOORE | L17B2 ESTELL S CC ESTATES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 159005 | 102090 | 3189 | 1452 | 8.5841e-05 | 1.1624e-06 | 73.85 | 1 | 320 | Customer | 79647 | Load | Tran1phPad | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005372 | PD-01142020-00519 | SOUTHERN | ADA | 5808:HARDEN CITY | HARDEN_CITY_823 | 580823 | 2020-01-14 15:47 | 2020-01-14 17:19 | 91.53 | 1 | 1 | 91.5333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | STONEWALL | HARDEN CITY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 77559 | 11504 | 106 | 104 | 0.0001064 | 1.1624e-06 | 91.5333 | 1 | 310 | Load | 15203 | Load | Tran1phOH | JORDAN HERBERT-BLUE | 918-839-1152 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005373 |  | METRO WEST | WEST | 8323:RICHARDS | RICHARDS_2324 | 832324 | 2020-01-14 15:49 | 2020-01-14 16:07 | 18.1 | 1 | 1 | 18.1 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7516 NW 131st Street | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 128638 | 115906 | 5002 | 1589 | 2.1039e-05 | 1.1624e-06 | 18.1 | 1 | 310 | Customer | 178209 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005382 | PD-01142020-00538 | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1424 | 911424 | 2020-01-14 16:02 | 2020-01-14 16:48 | 45.6 | 1 | 1 | 45.6 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | FORT SMITH | 5100 MIDLAND BL | CMI_NORMAL | NO | NO | NO | 860309 | 82162 | 61154 | 4737 | 255 | 5.3004e-05 | 1.1624e-06 | 45.6 | 1 | 320 | Customer | 6506 | Load | TranOpenDelta | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-14 | 2020 |  | Ark - Series 1
J2001.005391 |  | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3722 | 913722 | 2020-01-14 16:17 | 2020-01-14 16:51 | 34.33 | 1 | 1 | 34.3333 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | FORT SMITH | 6708 FERN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 82162 | 61154 | 4565 | 1438 | 3.9908e-05 | 1.1624e-06 | 34.3333 | 1 | 308 | Customer | 9126 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | Ark - Series 3
J2001.005385 | PD-01142020-00558 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7424 | 847424 | 2020-01-14 16:21 | 2020-01-14 17:23 | 61.7 | 1 | 1 | 61.7 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4900 N.LINCOLN BLVD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 168051 | 148248 | 6152 | 2197 | 7.1718e-05 | 1.1624e-06 | 61.7 | 1 | 310 | Load | 69594 | Load | Tran1phOH | LESLIE L FILSON JR | 405-623-7508 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005386 |  | NORTHWEST | ENID | 4157:NE ENID | NE_ENID_5723 | 415723 | 2020-01-14 16:23 | 2020-01-14 16:45 | 21.98 | 1 | 1 | 21.9833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWAY | QUAIL MDWS N L2 B3 ENID | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 53506 | 37572 | 1554 | 1308 | 2.5553e-05 | 1.1624e-06 | 21.9833 | 1 | 310 | Customer | 11056 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005394 | PD-01142020-00581 | ARKANSAS | OZARK | 9410:IGO | IGO_1024 | 941024 | 2020-01-14 16:40 | 2020-01-14 17:37 | 57.05 | 1 | 1 | 57.05 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | CLARKSVILLE | 1/4M SW- GOOSE CAMP | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 82162 | 7536 | 1504 | 304 | 6.6313e-05 | 1.1624e-06 | 57.05 | 1 | 310 | Customer | 2742 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-14 | 2020 |  | Ark - Series 2
J2001.005397 |  | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8124 | 838124 | 2020-01-14 16:48 | 2020-01-14 17:03 | 15.5 | 1 | 1 | 15.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 10522 HARVEST-MOON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 128638 | 115906 | 8954 | 1638 | 1.8017e-05 | 1.1624e-06 | 15.5 | 1 | 310 | Customer | 58733 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005401 |  | METRO EAST | SHAWNEE | 7433:ROCK CREEK | ROCK_CREEK_3322 | 743322 | 2020-01-14 16:56 | 2020-01-14 16:56 | 0 | 1032 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | SHAWNEE | 41873 WESTECH RD | CMI_MOMENTARY | YES | NO | NO | 860309 | 114330 | 22093 | 1799 | 1032 | 0 | 0.0011996 | 0 | 1 | 0 | Feeder | ROCK CRK_3322 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005402 |  | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5429 | 865429 | 2020-01-14 16:57 | 2020-01-14 18:00 | 63.2 | 1 | 1 | 63.2 | 1 | CANCELLED | 57 | CANCELLED | MOORE | LOT 4 BLK 25 GOLD MEDAL ADDN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 159005 | 102090 | 9806 | 1661 | 7.3462e-05 | 1.1624e-06 | 63.2 | 1 | 310 | Customer | 74271 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005403 |  | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4823 | 824823 | 2020-01-14 16:58 | 2020-01-14 17:08 | 9.97 | 1 | 1 | 9.9667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3016 SW.14 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 168051 | 148248 | 4189 | 1795 | 1.1585e-05 | 1.1624e-06 | 9.9667 | 1 | 310 | Customer | 11489 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2021
J2001.005405 |  | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1823 | 931823 | 2020-01-14 17:06 | 2020-01-14 19:14 | 128.4 | 1 | 1 | 128.4 | 1 | CANCELLED | 57 | CANCELLED | ALMA | HWY 71 3/4 M N. OF I-40 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 82162 | 61154 | 2834 | 1227 | 0.00014925 | 1.1624e-06 | 128.4 | 1 | 310 | Customer | 13410 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | Ark - Series 2
J2001.005406 |  | METRO EAST | SHAWNEE | 7433:ROCK CREEK | ROCK_CREEK_3322 | 743322 | 2020-01-14 17:08 | 2020-01-14 17:28 | 19.97 | 1 | 1 | 19.9667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | SHAWNEE | 4 DUNLOP | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 114330 | 22093 | 1799 | 1032 | 2.3209e-05 | 1.1624e-06 | 19.9667 | 1 | 310 | Customer | 14125 | Load | TranPad3phDelta | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005408 | PD-01142020-00604 | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8124 | 838124 | 2020-01-14 17:16 | 2020-01-14 21:17 | 241.02 | 1 | 1 | 241.0167 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 10522 HARVEST-MOON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 128638 | 115906 | 8954 | 1638 | 0.00028015 | 1.1624e-06 | 241.0167 | 1 | 310 | Customer | 58733 | Load | Tran1phPad | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005409 | PD-01142020-00599 | METRO EAST | SHAWNEE | 7433:ROCK CREEK | ROCK_CREEK_3322 | 743322 | 2020-01-14 17:19 | 2020-01-14 23:55 | 395.82 | 6 | 4 | 2292.6 | 4 | DETERIORATION | 1 | TRANSFORMER UG | SHAWNEE | E OF HARRSON ON DUNLOP | CMI_NORMAL | NO | NO | NO | 860309 | 114330 | 22093 | 1799 | 1032 | 0.0026649 | 6.9742e-06 | 382.1 | 1 | 320 | Mainline | 5041 | Fuse | FuseRiser | JEREMIAH D WALKER | 405-974-0464 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005416 | PD-01142020-00603 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2021 | 822021 | 2020-01-14 17:36 | 2020-01-14 18:50 | 74.27 | 12 | 17 | 826.8 | 27 | TREE:NON PREVENTABLE | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2940 NW.12 | CMI_NORMAL | NO | NO | NO | 860309 | 168051 | 148248 | 6034 | 1113 | 0.00096105 | 1.3948e-05 | 68.9 | 1 | 311 | Load | 13245 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005417 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1229 | 831229 | 2020-01-14 17:47 | 2020-01-14 20:02 | 134.98 | 6 | 9 | 736.6 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 2049 NW.48 | CMI_PLANNED | YES | NO | NO | 860309 | 168051 | 148248 | 7738 | 787 | 0.0008562 | 6.9742e-06 | 122.7667 | 1 | 310 | Load | 12370 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2022
J2001.005419 |  | NORTHWEST | ENID | 4123:KREMLIN TAP | KREMLIN TAP 21 | 412321 | 2020-01-14 17:50 | 2020-01-14 20:14 | 144.47 | 1 | 0 | 107.6 | 5 | ELECTRICAL TRACKING | 17 | JUMPER | 0 | 2.5ME 1.25MN OF KREMLIN WS | CMI_PLANNED | YES | NO | NO | 860309 | 53506 | 37572 | 432 | 414 | 0.00012507 | 1.1624e-06 | 107.6 | 1 | 0 | Load | 90155 | Load | 0 | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | #N/A
J2001.005420 |  | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1223 | 911223 | 2020-01-14 18:02 | 2020-01-14 18:36 | 33.45 | 1 | 1 | 33.45 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 518 LECTA AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 82165 | 61156 | 6593 | 1769 | 3.8881e-05 | 1.1624e-06 | 33.45 | 1 | 310 | Customer | 10404 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | Ark - Series 1
J2001.005424 |  | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1926 | 851926 | 2020-01-14 18:26 | 2020-01-14 18:27 | 1.1 | 6 | 0 | 6.4874 | 1 | CANCELLED | 57 | CANCELLED | 0 | 0 | CMI_MOMENTARY | YES | NO | NO | 860309 | 114331 | 71184 | 12434 | 2126 | 7.5408e-06 | 6.9742e-06 | 1.0812 | 1 | 0 | Mainline | 61521-1 | Switch | SwitchDefault | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2021
J2001.005431 |  | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1724 | 861724 | 2020-01-14 18:52 | 2020-01-14 19:01 | 9.3 | 1 | 1 | 9.3 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6212 SE.51 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 114331 | 71184 | 6938 | 2054 | 1.081e-05 | 1.1624e-06 | 9.3 | 1 | 310 | Customer | 40753 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | #N/A
J2001.005433 | PD-01142020-00608 | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1621 | 581621 | 2020-01-14 18:56 | 2020-01-14 20:11 | 75.47 | 1 | 1 | 75.4667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ADA | 124 N.OAK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 77558 | 11504 | 3454 | 1805 | 8.772e-05 | 1.1624e-06 | 75.4667 | 1 | 310 | Customer | 14675 | Load | TranOH3phDelta | JORDAN HERBERT-BLUE | 918-839-1152 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005437 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6124 | 836124 | 2020-01-14 19:42 | 2020-01-14 19:42 | 0 | 1765 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 1121 NW 30TH ST | CMI_MOMENTARY | YES | NO | NO | 860309 | 168052 | 148249 | 11100 | 1765 | 0 | 0.0020516 | 0 | 1 | 0 | Feeder | WESTR AV_6124 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-14 | 2020 |  | OK - 2020
J2001.005439 | PD-01142020-00609 | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1724 | 861724 | 2020-01-14 19:55 | 2020-01-14 20:55 | 60.4 | 1 | 1 | 60.4 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6212 SE.51 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 114331 | 71184 | 6938 | 2054 | 7.0207e-05 | 1.1624e-06 | 60.4 | 1 | 315 | Customer | 40753 | Load | Tran1phPad | ADAM CLARK | 580-310-8924 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | #N/A
J2001.005441 |  | METRO EAST | EAST | 8416:DUNJEE | DUNJEE_1623 | 841623 | 2020-01-14 19:58 | 2020-01-14 20:21 | 23.08 | 1 | 1 | 23.0833 | 1 | CANCELLED | 57 | CANCELLED | SPENCER | 3915 N.SHADYNOOK WY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 114331 | 71184 | 3541 | 1988 | 2.6831e-05 | 1.1624e-06 | 23.0833 | 1 | 310 | Customer | 18492 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005452 | PD-01142020-00617 | METRO EAST | EAST | 8471:NE 30TH ST | NE_30TH_ST_7122 | 847122 | 2020-01-14 20:22 | 2020-01-14 22:24 | 122.23 | 4 | 5 | 479.4667 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 21 | FUSE - TRANSFORMER | FOREST PARK | 3001 NORCREST DR | CMI_NORMAL | NO | NO | NO | 860309 | 114331 | 71184 | 2398 | 766 | 0.00055732 | 4.6495e-06 | 119.8667 | 1 | 310 | Load | 18918 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | OK - 2022
J2001.005453 |  | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1373 | 831373 | 2020-01-14 20:37 | 2020-01-14 20:46 | 8.42 | 1 | 1 | 8.4167 | 1 | CANCELLED | 57 | CANCELLED | YUKON | 1416 VIOLA DRIVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 128640 | 115906 | 7870 | 4096 | 9.7833e-06 | 1.1624e-06 | 8.4167 | 1 | 310 | Customer | 70906 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | #N/A
J2001.005461 | PD-01142020-00620 | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1022 | 311022 | 2020-01-14 21:35 | 2020-01-15 02:38 | 303.15 | 2 | 2 | 602.4333 | 5 | ELECTRICAL TRACKING | 27 | CUTOUT | MUSKOGEE | LOT 7 BLK 1 RIVEROAKS II | CMI_NORMAL | NO | NO | NO | 860309 | 73956 | 33227 | 2899 | 1093 | 0.00070025 | 2.3247e-06 | 301.2167 | 1 | 310 | Load | 19080 | Load | Tran1phPad | BRUCE A PAULUS | 479-220-7661 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-14 | 2020 |  | #N/A
J2001.005463 |  | METRO WEST | WEST | 8342:BRADEN PARK | BRADEN_PARK_4223 | 834223 | 2020-01-14 21:51 | 2020-01-14 22:06 | 15.17 | 1 | 1 | 15.1667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6612 NW 135th Street | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860309 | 128640 | 115906 | 3397 | 1781 | 1.7629e-05 | 1.1624e-06 | 15.1667 | 1 | 310 | Customer | 84920 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-14 | 2020 |  | OK - 2022
J2001.005472 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_631 | 460631 | 2020-01-15 00:24 | 2020-01-15 00:26 | 2.3 | 2589 | 7 | 5954.7 | 17 | TRANSMISSION OPERATION | 45 | SUBSTATION CIRCUIT | WOODWARD | 1005 CEDAR AVE | CMI_MOMENTARY | YES | NO | NO | 860309 | 53506 | 10416 | 5680 | 0 | 0.0069216 | 0.0030094 | 2.3 | 1 | 310 | Substation | CEDAR_AVE_23 | Breaker | 0 | [6 empty] | 06/02/2020 note from burchamc. Reference J2001.005472 in iDashboard report OSI_Job_Detail_Viewer. The job references Device CEDAR_AVE_629 and CEDAR_AVE_23. Probably should have been two jobs. Used Lead Device ID CEDAR_AVE_23 to Manually completed blank Job Region, Job Area, etc. | Equipment | N | TRANSMISSION | 69kV | 2020-01-15 | 2020 |  | #N/A
J2001.005474 |  | METRO WEST | WEST | 8158:SARA | SARA_5864 | 815864 | 2020-01-15 00:34 | 2020-01-15 04:17 | 223.13 | 20 | 24 | 2475.3333 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | MUSTANG | 1/2MN 152 4/10W MUST. | CMI_NORMAL | NO | NO | NO | 860309 | 128640 | 115906 | 18215 | 4810 | 0.0028773 | 2.3247e-05 | 123.7667 | 1 | 310 | Mainline | 28673 | Fuse | FuseRiser | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2022
J2001.005475 | PD-01152020-00003 | METRO WEST | WEST | 8158:SARA | SARA_5864 | 815864 | 2020-01-15 00:34 | 2020-01-15 04:18 | 223.52 | 7 | 9 | 743.6333 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | MUSTANG | 717 N. WILLOW BRANCH WAY | CMI_NORMAL | NO | NO | NO | 860309 | 128640 | 115906 | 18215 | 4810 | 0.00086438 | 8.1366e-06 | 106.2333 | 1 | 310 | Load | 73729 | Load | Tran1phPad | BAD ORDER PRIMARY RES COORD | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2022
J2001.005479 |  | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-15 01:08 | 2020-01-15 04:18 | 189.62 | 1 | 1 | 89.5833 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | MUSTANG | 322 W.MAPLEBRNCH WY | CMI_NORMAL | NO | NO | NO | 860309 | 128640 | 115906 | 18215 | 4429 | 0.00010413 | 1.1624e-06 | 89.5833 | 1 | 310 | Customer | 65363 | Load | Tran1phPad | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2022
J2001.005480 |  | NORTHEAST | SAPULPA | 3214:LONE STAR | LONE_STAR_1422 | 321422 | 2020-01-15 01:24 | 2020-01-15 01:24 | 0 | 1093 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | SAPULPA | 11511 W LONE STAR RD | CMI_MOMENTARY | YES | NO | NO | 860309 | 73956 | 40729 | 2654 | 1095 | 0 | 0.0012705 | 0 | 1 | 0 | Feeder | LONE STR_1422 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-15 | 2020 |  | OK - 2020
J2001.005492 | PD-01152020-00010 | SOUTHERN | DURANT | 5504:BUTTERFIELD | BUTTERFIELD_422 | 550422 | 2020-01-15 01:41 | 2020-01-15 13:07 | 686.13 | 1 | 2 | 516.5 | 13 | PREMATURE FAILURE | 2 | TRANSFORMER OH | ACHILLE | 300 BLK LOUISIANA ST NS | CMI_NORMAL | NO | NO | NO | 860309 | 77558 | 15478 | 3484 | 561 | 0.00060037 | 1.1624e-06 | 516.5 | 1 | 310 | Customer | 15881 | Load | Tran1phOH | JEREMY L MULLENS | 580-775-3134 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005491 | PD-01152020-00012 | METRO EAST | CHANDLER | 7118:KEY WEST | KEY_WEST_1847 | 711847 | 2020-01-15 05:09 | 2020-01-15 07:50 | 160.62 | 1 | 1 | 147.9667 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 21 | FUSE - TRANSFORMER | CHANDLER | 1MS 1ME DAVENPORT | CMI_NORMAL | NO | NO | NO | 860523 | 114331 | 7457 | 1210 | 741 | 0.00017195 | 1.1621e-06 | 147.9667 | 1 | 310 | Customer | 14578 | Load | Tran1phOH | SCOTT C PERRY | 405-258-6044 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2021
J2001.005505 | PD-01152020-00033 | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-01-15 07:39 | 2020-01-15 08:15 | 35.52 | 1 | 1 | 31.3333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MOORE | BELMARE CT LOT 7 EAST SIDE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 159005 | 56915 | 4204 | 3066 | 3.6412e-05 | 1.1621e-06 | 31.3333 | 1 | 310 | Customer | 322026 | Load | Tran1phPad | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005508 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-15 07:51 | 2020-01-15 15:06 | 434.97 | 1 | 1 | 350.1333 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | SEATON PL. & WAREHOUSE ST. | CMI_PLANNED | YES | NO | NO | 860523 | 82165 | 61156 | 2733 | 2121 | 0.00040688 | 1.1621e-06 | 350.1333 | 1 | 308 | Load | 202374 | Load | Tran3phWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | Ark - Series 2
J2001.005514 | PD-01152020-00043 | METRO EAST | SHAWNEE | 7432:ST GREGORY | ST_GREGORY_3229 | 743229 | 2020-01-15 08:06 | 2020-01-15 09:22 | 75.52 | 1 | 1 | 75.5167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SHAWNEE | ACME RD.+HWY 177 1\2 BLOCK S. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 114331 | 22094 | 4092 | 795 | 8.7757e-05 | 1.1621e-06 | 75.5167 | 1 | 310 | Load | 20214 | Load | TranOpenDelta | BRYAN K TATUM | 405-659-0746 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005515 |  | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3721 | 913721 | 2020-01-15 08:09 | 2020-01-15 08:44 | 34.63 | 23 | 24 | 664.3167 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 4812 ROGERS AV 114 | CMI_PLANNED | YES | NO | NO | 860523 | 82165 | 61156 | 4565 | 1497 | 0.00077199 | 2.6728e-05 | 28.8833 | 1 | 310 | Load | 9346 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | Ark - Series 3
J2001.005517 |  | NORTHEAST | MUSKOGEE | 3312:CHECOTAH | CHECOTAH 22 | 331222 | 2020-01-15 08:19 | 2020-01-15 08:38 | 19.25 | 1 | 2 | 19.25 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ONAPA | 4-MANS COVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 73956 | 33227 | 2886 | 1528 | 2.237e-05 | 1.1621e-06 | 19.25 | 1 | 320 | Customer | 8797 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | OK - 2020
J2001.005518 | PD-01152020-00071 | METRO WEST | WEST | 8158:SARA | SARA_5864 | 815864 | 2020-01-15 08:24 | 2020-01-15 08:59 | 34.98 | 1 | 1 | 34.9833 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 2608 TRAILS HEAD DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 128640 | 115906 | 18215 | 4810 | 4.0654e-05 | 1.1621e-06 | 34.9833 | 1 | 310 | Customer | 356904 | Load | Tran1phPad | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2022
J2001.005523 |  | ARKANSAS | FORT SMITH | 9508:WHITESIDE | WHITESIDE_822 | 950822 | 2020-01-15 08:30 | 2020-01-15 13:30 | 299.6 | 2 | 0 | 583.3333 | 4 | DETERIORATION | 12 | POLE | VAN BUREN | 2708 INDUSTRIAL PARK RD | CMI_PLANNED | YES | NO | NO | 860523 | 82165 | 61156 | 1919 | 209 | 0.00067788 | 2.3242e-06 | 291.6667 | 1 | 0 | Load | 16537 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-15 | 2020 |  | Ark - Series 2
J2001.005529 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-15 08:31 | 2020-01-15 13:39 | 307.82 | 3 | 1 | 917.55 | 4 | DETERIORATION | 12 | POLE | ARKOMA | 421 SUMNER | CMI_PLANNED | YES | NO | NO | 860523 | 82165 | 61156 | 2931 | 874 | 0.0010663 | 3.4863e-06 | 305.85 | 1 | 308 | Load | 782 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-15 | 2020 |  | Ark - Series 2
J2001.005526 | PD-01152020-00075 | SOUTHERN | MADILL | 5906:TISHOMINGO | TISHOMINGO_621 | 590621 | 2020-01-15 08:33 | 2020-01-15 10:09 | 96.45 | 1 | 2 | 86.5667 | 5 | ELECTRICAL TRACKING | 47 | ARRESTOR OH | TISHOMINGO | S MURRAY + WILSON | CMI_NORMAL | NO | NO | NO | 860523 | 77558 | 7201 | 967 | 916 | 0.0001006 | 1.1621e-06 | 86.5667 | 1 | 320 | Load | 28977 | Load | Tran3phWye | ROBERT J BEARDSLEE | 580-618-2506 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2021
J2001.005527 | PD-01152020-00143 | NORTHWEST | ENID | 4135:SO 4TH ST | SO_4TH_ST_3524 | 413524 | 2020-01-15 08:34 | 2020-01-15 09:46 | 71.88 | 1 | 1 | 71.8833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ENID | 824 W.NAGLE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 53506 | 37572 | 3094 | 1611 | 8.3534e-05 | 1.1621e-06 | 71.8833 | 1 | 310 | Customer | 4560 | Load | Tran1phOH | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005530 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2122 | 822122 | 2020-01-15 08:42 | 2020-01-15 10:20 | 97.98 | 171 | 139 | 14609.1 | 4 | DETERIORATION | 28 | CROSSARM | OKLAHOMA CITY | TULSA AVE + NW.21 TERR | CMI_PLANNED | YES | NO | NO | 860523 | 168052 | 148249 | 9238 | 2013 | 0.016977 | 0.00019872 | 85.4333 | 1 | 310 | Mainline | 16914 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2020
J2001.005534 |  | NORTHEAST | SAPULPA | 3210:HICKORY HILL | HICKORY_HILL_1021 | 321021 | 2020-01-15 08:58 | 2020-01-15 15:16 | 378.37 | 29 | 31 | 2745.8167 | 28 | OTHER (DESCRIBE) | 1 | TRANSFORMER UG | SAPULPA | 1106 N MOCASSIN ST | CMI_PLANNED | YES | NO | NO | 860523 | 73956 | 40729 | 2683 | 1437 | 0.0031909 | 3.37e-05 | 94.6833 | 1 | 310 | Mainline | 62294 | Fuse | FuseRiser | OGE | [6 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2022
J2001.005535 |  | NORTHWEST | ENID | 4109:WAUKOMIS | WAUKOMIS 23 | 410923 | 2020-01-15 09:01 | 2020-01-15 13:19 | 258.23 | 1 | 0 | 247.5 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | 0 | 3130 E. REED, WAUKOMIS, OK | CMI_PLANNED | YES | NO | NO | 860523 | 53506 | 37572 | 1556 | 572 | 0.00028762 | 1.1621e-06 | 247.5 | 1 | 0 | Load | 365184 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005545 | PD-01152020-00134 | NORTHEAST | SAPULPA | 3213:BOWDEN | BOWDEN_1329 | 321329 | 2020-01-15 09:08 | 2020-01-15 10:12 | 64.43 | 1 | 2 | 58.7167 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | SAPULPA | 6445 SO. 103 W. AV. | CMI_NORMAL | NO | NO | NO | 860523 | 73956 | 40729 | 3371 | 1516 | 6.8234e-05 | 1.1621e-06 | 58.7167 | 1 | 310 | Load | 196829 | Load | Tran1phPad | CGI ADMIN | 918-261-6802 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2020
J2001.005541 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_722 | 870722 | 2020-01-15 09:10 | 2020-01-15 15:10 | 359.62 | 128 | 11 | 418.1333 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | NORMAN | 84TH AV SE & ST HWY 9 | CMI_PLANNED | YES | NO | NO | 860523 | 159005 | 56915 | 11831 | 1582 | 0.00048591 | 0.00014875 | 3.2667 | 1 | 310 | Mainline | 34116 | Switch | SwitchOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005542 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_722 | 870722 | 2020-01-15 09:11 | 2020-01-15 17:42 | 511.32 | 2 | 1 | 727.4 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | NORMAN | E.84TH AV + HWY 9 | CMI_PLANNED | YES | NO | NO | 860523 | 159005 | 56915 | 11831 | 1582 | 0.0008453 | 2.3242e-06 | 363.7 | 1 | 308 | Tap | 22017 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005544 | PD-01152020-00151 | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_624 | 460624 | 2020-01-15 09:11 | 2020-01-15 10:32 | 80.77 | 1 | 1 | 80.7667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | WOODWARD | 1000 Hankis Trail | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 53506 | 10416 | 5680 | 488 | 9.3858e-05 | 1.1621e-06 | 80.7667 | 1 | 310 | Load | 346159 | Load | Tran1phOH | ROY L THRASH | 580-334-5371 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | #N/A
J2001.005546 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-01-15 09:14 | 2020-01-15 10:26 | 72.5 | 1 | 1 | 64.2 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | FORT SMITH | TEXAS RD. S.-SCHOOL ST | CMI_PLANNED | YES | NO | NO | 860523 | 82165 | 61156 | 1455 | 1237 | 7.4606e-05 | 1.1621e-06 | 64.2 | 1 | 308 | Mainline | 2865 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | Ark - Series 2
J2001.005549 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2229 | 852229 | 2020-01-15 09:22 | 2020-01-15 11:30 | 127.88 | 1 | 1 | 73.1333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | HARRAH | 8500 N Luther Rd | CMI_PLANNED | YES | NO | NO | 860523 | 114331 | 71184 | 11623 | 1387 | 8.4987e-05 | 1.1621e-06 | 73.1333 | 1 | 308 | Load | 15031 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005551 | PD-01152020-00164 | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_422 | 580422 | 2020-01-15 09:24 | 2020-01-15 09:34 | 10.62 | 1 | 2 | 10.6167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ADA | 1104 S.STOCKTON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 77558 | 11504 | 3411 | 1426 | 1.2337e-05 | 1.1621e-06 | 10.6167 | 1 | 310 | Customer | 1996 | Load | Tran1phOH | JORDAN HERBERT-BLUE | 918-839-1152 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005552 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-15 09:26 | 2020-01-15 12:18 | 172.02 | 4 | 3 | 672.8 | 4 | DETERIORATION | 12 | POLE | HARTMAN | LINE STREET | CMI_PLANNED | YES | NO | NO | 860523 | 82165 | 7536 | 1504 | 1200 | 0.00078185 | 4.6483e-06 | 168.2 | 1 | 308 | Load | 9386 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-15 | 2020 |  | Ark - Series 2
J2001.005554 | PD-01152020-00189 | NORTHWEST | ENID | 4112:CHESTNUT | CHESTNUT_1222 | 411222 | 2020-01-15 09:33 | 2020-01-15 10:53 | 80.1 | 1 | 1 | 80.1 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ENID | 1910 E. MAINE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 53506 | 37572 | 2858 | 1746 | 9.3083e-05 | 1.1621e-06 | 80.1 | 1 | 310 | Customer | 5427 | Load | Tran1phOH | KEVIN N PERRYMAN | 601-528-2473 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | #N/A
J2001.005557 | PD-01152020-00165 | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5429 | 865429 | 2020-01-15 09:35 | 2020-01-15 14:36 | 301.08 | 26 | 27 | 7292.5667 | 4 | DETERIORATION | 25 | ELBOW | MOORE | 0 | CMI_NORMAL | NO | NO | NO | 860523 | 159005 | 102090 | 9806 | 1661 | 0.0084746 | 3.0214e-05 | 280.4833 | 1 | 310 | Mainline | 78191-2 | Switch | SwitchDefault | BRANDON ALLEN | 405-464-9954 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005562 |  | ARKANSAS | FORT SMITH | 9111:MASSARD | MASSARD_1124 | 911124 | 2020-01-15 09:45 | 2020-01-15 13:06 | 200.87 | 11 | 11 | 441.2833 | 4 | DETERIORATION | 1 | TRANSFORMER UG | FORT SMITH | MASSARD RD. S. MARK LN | CMI_PLANNED | YES | NO | NO | 860523 | 82165 | 61156 | 4983 | 543 | 0.00051281 | 1.2783e-05 | 40.1167 | 1 | 310 | Mainline | 1464 | Fuse | FuseRiser | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-15 | 2020 |  | Ark - Series 3
J2001.005561 |  | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_624 | 410624 | 2020-01-15 09:47 | 2020-01-15 15:47 | 360.15 | 2 | 1 | 715.9333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | ENID | 2202 N.VANBUREN | CMI_PLANNED | YES | NO | NO | 860523 | 53506 | 37572 | 6013 | 1861 | 0.00083197 | 2.3242e-06 | 357.9667 | 1 | 308 | Load | 5967 | Load | TranOpenDelta | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | #N/A
J2001.005563 | PD-01152020-00199 | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_629 | 460629 | 2020-01-15 09:48 | 2020-01-15 10:54 | 65.62 | 1 | 2 | 65.6167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | WOODWARD | 917 21ST-WOODWARD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 53506 | 10416 | 5680 | 931 | 7.6252e-05 | 1.1621e-06 | 65.6167 | 1 | 310 | Customer | 11076 | Load | Tran1phOH | ROY L THRASH | 580-334-5371 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | #N/A
J2001.005567 | PD-01152020-00180 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1522 | 811522 | 2020-01-15 09:54 | 2020-01-15 10:49 | 54.68 | 1 | 1 | 54.6833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2327.5 SW.22 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 159005 | 102090 | 6056 | 1940 | 6.3547e-05 | 1.1621e-06 | 54.6833 | 1 | 310 | Customer | 1269 | Load | Tran1phOH | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | OK - 2022
J2001.005571 | PD-01152020-00198 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-01-15 10:03 | 2020-01-15 11:05 | 62.5 | 1 | 1 | 62.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3918 S.RANCHO DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 159005 | 102090 | 7598 | 2455 | 7.263e-05 | 1.1621e-06 | 62.5 | 1 | 310 | Customer | 15695 | Load | Tran1phOH | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | #N/A
J2001.005573 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-15 10:06 | 2020-01-15 13:00 | 173.93 | 1 | 0 | 173.916 | 4 | DETERIORATION | 2 | TRANSFORMER OH | ARKOMA | 416 SHERMAN | CMI_PLANNED | YES | NO | NO | 860523 | 82165 | 61156 | 2931 | 874 | 0.00020211 | 1.1621e-06 | 173.916 | 1 | 0 | Load | 11252 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-15 | 2020 |  | Ark - Series 2
J2001.005574 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3831 | 913831 | 2020-01-15 10:08 | 2020-01-15 12:00 | 111.87 | 11 | 10 | 1153.9 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 3920 S.18, 3 POLE S-JACKSON | CMI_PLANNED | YES | NO | NO | 860523 | 82165 | 61156 | 2931 | 484 | 0.0013409 | 1.2783e-05 | 104.9 | 1 | 308 | Load | 5540 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-15 | 2020 |  | Ark - Series 2
J2001.005576 | PD-01152020-00205 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1929 | 851929 | 2020-01-15 10:09 | 2020-01-15 11:47 | 98.4 | 7 | 7 | 667.8 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MIDWEST CITY | 3402 OAKHURST DR | CMI_NORMAL | NO | NO | NO | 860523 | 114331 | 71184 | 12434 | 827 | 0.00077604 | 8.1346e-06 | 95.4 | 1 | 310 | Load | 16528 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2022
J2001.005579 |  | SOUTHERN | SULPHUR | 5705:SULPHUR | SULPHUR_531 | 570531 | 2020-01-15 10:23 | 2020-01-15 12:08 | 105.25 | 8 | 4 | 810.1333 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | SULPHUR | W 14TH + WILLIAMS | CMI_PLANNED | YES | NO | NO | 860523 | 77558 | 6809 | 3630 | 602 | 0.00094144 | 9.2967e-06 | 101.2667 | 1 | 308 | Load | 14232 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005582 | PD-01152020-00214 | NORTHEAST | MUSKOGEE | 3312:CHECOTAH | CHECOTAH 21 | 331221 | 2020-01-15 10:26 | 2020-01-15 11:51 | 84.62 | 1 | 1 | 84.6167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | CHECOTAH | 514 SW.1ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 73956 | 33227 | 2886 | 1358 | 9.8332e-05 | 1.1621e-06 | 84.6167 | 1 | 310 | Customer | 7716 | Load | Tran1phOH | NICHOLAS SELVIDGE | 918-652-1986 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | OK - 2020
J2001.005583 |  | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_647 | 890647 | 2020-01-15 10:29 | 2020-01-15 10:39 | 9.87 | 1 | 1 | 9.8667 | 1 | CANCELLED | 57 | CANCELLED | CANTON | 305 W.CEDAR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 128640 | 12734 | 1366 | 1069 | 1.1466e-05 | 1.1621e-06 | 9.8667 | 1 | 310 | Customer | 38979 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005601 | PD-01152020-00294 | NORTHEAST | SAPULPA | 7611:MORRISON TAP | MORRISON_TAP_1122 | 761122 | 2020-01-15 10:43 | 2020-01-15 12:39 | 116.63 | 157 | 79 | 18311.1167 | 13 | PREMATURE FAILURE | 23 | FUSE - PRIMARY | GLENCOE | 11\8ME OF MORRISON TAP | CMI_NORMAL | NO | NO | NO | 860523 | 73956 | 40729 | 892 | 427 | 0.021279 | 0.00018245 | 116.6313 | 1 | 310 | Mainline | 8110 | Fuse | FuseOH | BRAD WRIGHT | 918-629-1747 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2021
J2001.005598 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7429 | 847429 | 2020-01-15 10:53 | 2020-01-15 11:19 | 26.55 | 14 | 11 | 327.8333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 2112 NE.22 | CMI_PLANNED | YES | NO | NO | 860523 | 168052 | 148249 | 6152 | 680 | 0.00038097 | 1.6269e-05 | 23.4167 | 1 | 310 | Load | 14146 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2022
J2001.005599 |  | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5429 | 865429 | 2020-01-15 10:54 | 2020-01-15 10:54 | 0 | 527 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MOORE | MORGAN AND NE 4TH, SW CORNER | CMI_MOMENTARY | YES | NO | NO | 860523 | 159005 | 102090 | 9806 | 1661 | 0 | 0.00061242 | 0 | 1 | 0 | Mainline | 351940 | Recloser | Rec3phElectronic | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005602 | PD-01152020-00264 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_724 | 870724 | 2020-01-15 10:55 | 2020-01-15 13:50 | 175.05 | 1 | 1 | 175.05 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 215 EMELYN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 159005 | 56915 | 11831 | 2411 | 0.00020342 | 1.1621e-06 | 175.05 | 1 | 310 | Customer | 44538 | Load | Tran1phOH | THOMAS E COLE | 405-623-9338 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005621 | PD-01152020-00295 | ARKANSAS | POTEAU | 3514:HEAVENER | HEAVENER 22 | 351422 | 2020-01-15 10:59 | 2020-01-15 12:03 | 64.15 | 275 | 84 | 17444.1667 | 5 | ELECTRICAL TRACKING | 23 | FUSE - PRIMARY | HEAVENER | WEST 5 NORTH OF AVE I | CMI_NORMAL | NO | NO | NO | 860523 | 82165 | 13473 | 1768 | 1305 | 0.020272 | 0.00031957 | 63.4333 | 1 | 310 | Mainline | 29218 | Fuse | FuseOH | TOBY C MEAD | 918-658-5596 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | OK - 2021
J2001.005637 |  | ARKANSAS | POTEAU | 3514:HEAVENER | HEAVENER 22 | 351422 | 2020-01-15 10:59 | 2020-01-15 12:16 | 77.08 | 1 | 4 | 63.5 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | HEAVENER | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 0 | 0 | 0 | 0 | 7.3792e-05 | 1.1621e-06 | 63.5 | 1 | 310 | Customer |  | 0 | 0 | [6 empty] | 06/02/2020 note from burchamc. Reference J2001.005637 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | OK - 2021
J2001.005616 | PD-01152020-00299 | NORTHWEST | ENID | 4109:WAUKOMIS | WAUKOMIS 23 | 410923 | 2020-01-15 11:01 | 2020-01-15 12:03 | 62.07 | 1 | 1 | 62.0667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | WAUKOMIS | 3-3/4 E WAUK ON BT, 3/8N-INTO | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 53506 | 37572 | 1556 | 572 | 7.2127e-05 | 1.1621e-06 | 62.0667 | 1 | 310 | Load | 12854 | Load | Tran3phWye | RONALD K GOSE | 580-541-3131 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005622 | PD-01152020-00280 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-01-15 11:05 | 2020-01-15 12:01 | 56.27 | 1 | 1 | 56.2667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DEL CITY | 3224 SE.21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 159005 | 102090 | 7413 | 2238 | 6.5387e-05 | 1.1621e-06 | 56.2667 | 1 | 310 | Customer | 22285 | Load | TranOHDeltaSplitBank | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2022
J2001.005634 | PD-01152020-00296 | METRO EAST | SHAWNEE | 7433:ROCK CREEK | ROCK_CREEK_3328 | 743328 | 2020-01-15 11:07 | 2020-01-15 12:17 | 69.77 | 1 | 2 | 57.8333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | SHAWNEE | 5MN MACARTHUR ON ACME,1\4E | CMI_NORMAL | NO | NO | NO | 860523 | 114331 | 22094 | 1799 | 765 | 6.7207e-05 | 1.1621e-06 | 57.8333 | 1 | 310 | Load | 18131 | Load | Tran1phOH | BRYAN K TATUM | 405-659-0746 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005632 | PD-01152020-00285 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5121 | 815121 | 2020-01-15 11:10 | 2020-01-15 18:20 | 430.13 | 1 | 1 | 429.4167 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | OKLAHOMA CITY | LOT 8 BLK 3 SW. 96 + LAND | CMI_NORMAL | NO | NO | NO | 860523 | 159005 | 102090 | 13935 | 1998 | 0.00049902 | 1.1621e-06 | 429.4167 | 1 | 310 | Customer | 74251 | Load | Tran1phPad | CARL BILYEU | 405-820-9246 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005645 | PD-01152020-00301 | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2724 | 872724 | 2020-01-15 11:25 | 2020-01-15 13:37 | 132.32 | 1 | 1 | 57.0322 | 22 | WIND | 23 | FUSE - PRIMARY | NORMAN | 2214 RESEARCH PARK BLVD | CMI_NORMAL | NO | NO | NO | 860523 | 159005 | 56915 | 6459 | 1255 | 6.6276e-05 | 1.1621e-06 | 57.0322 | 1 | 310 | Load | 56938 | Load | Tran3phWye | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005644 | PD-01152020-00314 | NORTHEAST | MUSKOGEE | 3312:CHECOTAH | CHECOTAH 22 | 331222 | 2020-01-15 11:25 | 2020-01-15 12:56 | 90.73 | 1 | 1 | 90.7333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ONAPA | 4-MANS COVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 73956 | 33227 | 2886 | 1528 | 0.00010544 | 1.1621e-06 | 90.7333 | 1 | 310 | Customer | 8797 | Load | Tran1phOH | NICHOLAS SELVIDGE | 918-652-1986 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | OK - 2020
J2001.005647 | PD-01152020-00302 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-01-15 11:27 | 2020-01-15 16:13 | 286.2 | 1 | 1 | 279.55 | 11 | OVERLOAD | 2 | TRANSFORMER OH | HARRAH | 2507 S HARRAH RD | CMI_NORMAL | NO | NO | NO | 860523 | 114331 | 71184 | 11623 | 3534 | 0.00032486 | 1.1621e-06 | 279.55 | 1 | 310 | Load | 89691 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005646 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-15 11:27 | 2020-01-15 16:51 | 324.32 | 1 | 1 | 299.5667 | 4 | DETERIORATION | 12 | POLE | HARTMAN | COUNTY ROAD 14 | CMI_PLANNED | YES | NO | NO | 860523 | 82165 | 7536 | 1504 | 1200 | 0.00034812 | 1.1621e-06 | 299.5667 | 1 | 308 | Load | 225906 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-15 | 2020 |  | Ark - Series 2
J2001.005654 | PD-01152020-00332 | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2729 | 872729 | 2020-01-15 11:40 | 2020-01-15 13:43 | 123.1 | 1 | 1 | 41.7054 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | 2306 RESEARCH-PK BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 159005 | 56915 | 6459 | 1262 | 4.8465e-05 | 1.1621e-06 | 41.7054 | 1 | 310 | Customer | 67638 | Load | Tran1phPad | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005658 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-01-15 11:55 | 2020-01-15 14:48 | 173.22 | 15 | 9 | 2640 | 4 | DETERIORATION | 28 | CROSSARM | OKLAHOMA CITY | .1MN OF SE 149TH ST ON S DOUGLAS BL | CMI_NORMAL | NO | NO | NO | 860523 | 159005 | 56915 | 4204 | 3066 | 0.0030679 | 1.7431e-05 | 176 | 1 | 310 | Mainline | 30884 | Switch | SwitchOH | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005664 | PD-01152020-00357 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-01-15 12:25 | 2020-01-15 14:22 | 116.52 | 1 | 1 | 28.0865 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1836 CAREY PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 168052 | 148249 | 11100 | 2036 | 3.2639e-05 | 1.1621e-06 | 28.0865 | 1 | 310 | Customer | 9993 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2021
J2001.005667 | PD-01152020-00362 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2031 | 862031 | 2020-01-15 12:35 | 2020-01-15 13:17 | 41.65 | 1 | 1 | 41.65 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2520 S.HIGH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 159005 | 102090 | 4741 | 1440 | 4.8401e-05 | 1.1621e-06 | 41.65 | 1 | 310 | Load | 14327 | Load | TranOpenDelta | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2021
J2001.005672 |  | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3721 | 913721 | 2020-01-15 12:53 | 2020-01-15 15:17 | 143.38 | 5 | 6 | 479.75 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 1409 S.40 | CMI_PLANNED | YES | NO | NO | 860523 | 82165 | 61156 | 4565 | 1497 | 0.00055751 | 5.8104e-06 | 95.95 | 1 | 310 | Load | 3122 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | Ark - Series 3
J2001.005680 |  | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-01-15 13:08 | 2020-01-15 13:43 | 34.92 | 3 | 2 | 90.2 | 1 | CANCELLED | 37 | CONDUCTOR PRIMARY - OH | EL RENO | 1/8W-HWY 81 + JONES RD | CMI_PLANNED | YES | NO | NO | 860523 | 128640 | 12734 | 6935 | 1823 | 0.00010482 | 3.4863e-06 | 30.0667 | 1 | 308 | Tap | 19403 | Fuse | FuseOH | Crew | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005682 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1325 | 911325 | 2020-01-15 13:10 | 2020-01-15 15:51 | 161.33 | 2 | 2 | 294.2167 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | FORT SMITH | 1215 S.ZERO | CMI_PLANNED | YES | NO | NO | 860523 | 82165 | 61156 | 1455 | 216 | 0.0003419 | 2.3242e-06 | 147.1083 | 1 | 308 | Load | 9804 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | Ark - Series 2
J2001.005686 | PD-01152020-00399 | NORTHEAST | SAPULPA | 7611:MORRISON TAP | MORRISON_TAP_1122 | 761122 | 2020-01-15 13:16 | 2020-01-15 14:06 | 49.82 | 1 | 1 | 23.2626 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | GLENCOE | W OF RR ON SHELL 1/4S GLENCOE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 73956 | 40729 | 892 | 427 | 2.7033e-05 | 1.1621e-06 | 23.2626 | 1 | 310 | Load | 22287 | Load | Tran1phOH | BRAD WRIGHT | 918-629-1747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2021
J2001.005695 |  | METRO NORTH | NORTH | 8506:PARK PLACE | PARK_PLACE_623 | 850623 | 2020-01-15 13:37 | 2020-01-15 15:49 | 131.73 | 1 | 1 | 131.7333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 136 NW 16TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 168052 | 148249 | 830 | 266 | 0.00015309 | 1.1621e-06 | 131.7333 | 1 | 310 | Customer | 11505 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005704 |  | METRO NORTH | GUTHRIE | 8814:PINE STREET | PINE_STREET_1424 | 881424 | 2020-01-15 14:02 | 2020-01-15 15:00 | 58.1 | 15 | 5 | 684 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | GUTHRIE | 1207 PIN OAK | CMI_PLANNED | YES | NO | NO | 860523 | 168052 | 19803 | 3097 | 1236 | 0.00079487 | 1.7431e-05 | 45.6 | 1 | 308 | Load | 43572 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005706 |  | ARKANSAS | FORT SMITH | 9508:WHITESIDE | WHITESIDE_822 | 950822 | 2020-01-15 14:11 | 2020-01-15 17:38 | 207.18 | 7 | 7 | 1326.0333 | 4 | DETERIORATION | 12 | POLE | VAN BUREN | 605 S.6 | CMI_PLANNED | YES | NO | NO | 860523 | 82165 | 61156 | 1919 | 209 | 0.001541 | 8.1346e-06 | 189.4333 | 1 | 308 | Load | 11989 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-15 | 2020 |  | Ark - Series 2
J2001.005711 | PD-01152020-00463 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3628 | 833628 | 2020-01-15 14:32 | 2020-01-15 15:57 | 85.28 | 1 | 1 | 85.2833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 12113 GREYSTONE CI | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 168052 | 148249 | 8784 | 1313 | 9.9106e-05 | 1.1621e-06 | 85.2833 | 1 | 320 | Customer | 35341 | Load | Tran1phOH | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005718 |  | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9869 | 839869 | 2020-01-15 14:36 | 2020-01-15 16:43 | 127.68 | 12 | 6 | 1349.7 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | OKLAHOMA CITY | 1/4N-NW 164TH, WS-PENN | CMI_PLANNED | YES | NO | NO | 860523 | 168052 | 148249 | 10653 | 2995 | 0.0015685 | 1.3945e-05 | 112.475 | 1 | 310 | Load | 16722 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2022
J2001.005719 |  | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5222 | 835222 | 2020-01-15 14:45 | 2020-01-15 14:45 | 0.03 | 1353 | 0 | 45.1 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 11813 N PORTLAND AVE | CMI_MOMENTARY | YES | NO | NO | 860523 | 168052 | 148249 | 6517 | 1353 | 5.241e-05 | 0.0015723 | 0.033333 | 1 | 0 | Feeder | QUAIL CK_5222 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005723 |  | ARKANSAS | POTEAU | 3514:HEAVENER | HEAVENER 22 | 351422 | 2020-01-15 14:46 | 2020-01-15 15:50 | 63.65 | 2 | 2 | 47.2667 | 5 | ELECTRICAL TRACKING | 12 | POLE | HEAVENER | 305 WEST 2ND ST | CMI_PLANNED | YES | NO | NO | 860523 | 82165 | 13473 | 1768 | 1305 | 5.4928e-05 | 2.3242e-06 | 23.6333 | 1 | 308 | Load | 14439 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | OK - 2021
J2001.005721 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7021 | 817021 | 2020-01-15 14:52 | 2020-01-15 15:05 | 12.92 | 1 | 1 | 12.9167 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 6404 S.HARVEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 159005 | 102090 | 9938 | 1789 | 1.501e-05 | 1.1621e-06 | 12.9167 | 1 | 310 | Customer | 19432 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005735 | PD-01152020-00504 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4033 | 834033 | 2020-01-15 15:16 | 2020-01-15 16:29 | 72.77 | 38 | 18 | 2594.1333 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | 10509 CONDOR TE | CMI_NORMAL | NO | NO | NO | 860523 | 128640 | 115906 | 10841 | 1115 | 0.0030146 | 4.4159e-05 | 68.2667 | 1 | 310 | Mainline | 20241 | Fuse | FuseRiser | BAD ORDER PRIMARY RES COORD | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005728 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4033 | 834033 | 2020-01-15 15:16 | 2020-01-15 15:16 | 0 | 1105 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 10135 ROCKWELL AVE | CMI_MOMENTARY | YES | NO | NO | 860523 | 128640 | 115906 | 10841 | 1115 | 0 | 0.0012841 | 0 | 1 | 0 | Feeder | SILVR LK_4033 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005729 | PD-01152020-00506 | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-15 15:19 | 2020-01-15 16:12 | 52.73 | 1 | 1 | 52.7333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ARKOMA | 1144 TULSA - MOFFETT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 82165 | 61156 | 2931 | 874 | 6.1281e-05 | 1.1621e-06 | 52.7333 | 1 | 310 | Customer | 11264 | Load | Tran1phOH | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-15 | 2020 |  | Ark - Series 2
J2001.005732 |  | METRO EAST | EAST | 8411:ACORN | ACORN_1172 | 841172 | 2020-01-15 15:21 | 2020-01-15 17:46 | 144.78 | 2 | 0 | 289.5384 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | 5213 NE 122nd St. | CMI_PLANNED | YES | NO | NO | 860523 | 114331 | 71184 | 1790 | 699 | 0.00033647 | 2.3242e-06 | 144.7692 | 1 | 0 | Load | 386959 | Load | Tran3phPadWye | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005734 |  | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_421 | 710421 | 2020-01-15 15:24 | 2020-01-15 15:40 | 16.03 | 1 | 1 | 16.0333 | 1 | CANCELLED | 57 | CANCELLED | CHANDLER | CHANDLER HS SOFTBALL FD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 114331 | 7457 | 2820 | 1172 | 1.8632e-05 | 1.1621e-06 | 16.0333 | 1 | 310 | Load | 159638 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2021
J2001.005741 | PD-01152020-00517 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2124 | 822124 | 2020-01-15 15:44 | 2020-01-15 17:18 | 94 | 1 | 1 | 40.3167 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | 4800 W.INTERSTA-40 | CMI_NORMAL | NO | NO | NO | 860523 | 168052 | 148249 | 9238 | 423 | 4.6851e-05 | 1.1621e-06 | 40.3167 | 1 | 310 | Customer | 63004 | Load | Tran3phWye | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2021
J2001.005745 | PD-01152020-00524 | NORTHWEST | ENID | 4105:ENID | ENID_521 | 410521 | 2020-01-15 15:54 | 2020-01-15 16:49 | 55.47 | 1 | 2 | 48.8333 | 22 | WIND | 31 | CONDUCTOR SERVICE - OH | ENID | 1302 W BROADWAY--ENID | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860523 | 53506 | 37572 | 1326 | 613 | 5.6748e-05 | 1.1621e-06 | 48.8333 | 1 | 310 | Customer | 231 | Load | TranOpenDelta | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | #N/A
J2001.005750 |  | NORTHEAST | SAPULPA | 3207:HILL TOP | HILL TOP 23 | 320723 | 2020-01-15 16:11 | 2020-01-15 17:39 | 87.9 | 1 | 1 | 87.9 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | GLENPOOL | 574 E.139 ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 73956 | 40729 | 992 | 411 | 0.00010215 | 1.1621e-06 | 87.9 | 1 | 310 | Customer | 40999 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | #N/A
J2001.005755 |  | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5221 | 835221 | 2020-01-15 16:12 | 2020-01-15 16:55 | 42.77 | 1 | 1 | 42.7667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 12223 BANYAN LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 168052 | 148249 | 6517 | 1500 | 4.9698e-05 | 1.1621e-06 | 42.7667 | 1 | 310 | Customer | 58346 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005753 | PD-01152020-00571 | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1223 | 911223 | 2020-01-15 16:13 | 2020-01-15 18:06 | 112.68 | 1 | 1 | 112.6833 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | FORT SMITH | 4201 KINKEAD AV 14 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 82165 | 61156 | 6593 | 1769 | 0.00013095 | 1.1621e-06 | 112.6833 | 1 | 310 | Customer | 9565 | Load | Tran1phPad | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | Ark - Series 1
J2001.005765 | PD-01152020-00589 | NORTHWEST | WOODWARD | 4611:DEWEY | DEWEY_1143 | 461143 | 2020-01-15 16:31 | 2020-01-15 18:52 | 140.98 | 1 | 1 | 140.9833 | 4 | DETERIORATION | 28 | CROSSARM | SEILING | 301 S ELM ST | CMI_NORMAL | NO | NO | NO | 860523 | 53506 | 10416 | 1319 | 677 | 0.00016383 | 1.1621e-06 | 140.9833 | 1 | 320 | Customer | 11350 | Load | Tran1phOH | HAYDEN BIERIG | 580-748-0538 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005767 | PD-01152020-00592 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7021 | 817021 | 2020-01-15 16:36 | 2020-01-15 17:25 | 49.13 | 11 | 11 | 540.4667 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 6050 S.HARVEY | CMI_NORMAL | NO | NO | NO | 860523 | 159005 | 102090 | 9938 | 1789 | 0.00062807 | 1.2783e-05 | 49.1333 | 1 | 310 | Load | 31951 | Load | Tran1phPad | MIKE MITCHELL | 405-996-8178 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005772 |  | METRO EAST | EAST | 8417:ROUND BARN | ROUND_BARN_1723 | 841723 | 2020-01-15 17:00 | 2020-01-15 17:30 | 30.7 | 1 | 1 | 30.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ARCADIA | 24475 N. DOUGLAS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 114331 | 71184 | 1008 | 1008 | 3.5676e-05 | 1.1621e-06 | 30.7 | 1 | 310 | Load | 223237 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005774 |  | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5023 | 865023 | 2020-01-15 17:21 | 2020-01-15 17:35 | 13.82 | 1 | 1 | 13.8167 | 1 | CANCELLED | 57 | CANCELLED | MIDWEST CITY | 2705 DIMICK CT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 114331 | 71184 | 8622 | 1267 | 1.6056e-05 | 1.1621e-06 | 13.8167 | 1 | 310 | Customer | 26458 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2022
J2001.005775 |  | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_647 | 730647 | 2020-01-15 17:23 | 2020-01-15 17:39 | 15.52 | 1 | 1 | 15.5167 | 1 | CANCELLED | 57 | CANCELLED | PRAGUE | 1.7ME OF HWY 99 & CENTERVIEW SS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 114331 | 13596 | 4059 | 72 | 1.8032e-05 | 1.1621e-06 | 15.5167 | 1 | 310 | Customer | 255481 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005779 | PD-01152020-00593 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9931 | 829931 | 2020-01-15 17:26 | 2020-01-15 19:01 | 95.08 | 2 | 2 | 64.5 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 6047 NW.10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 128640 | 115906 | 9218 | 2192 | 7.4954e-05 | 2.3242e-06 | 32.25 | 1 | 310 | Secondary | 34746 | Load | Tran1phPad | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005780 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5121 | 815121 | 2020-01-15 17:40 | 2020-01-15 18:38 | 57.83 | 3 | 5 | 105.75 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | LOT 8 BLK 3 SW. 96 + LAND | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860523 | 159005 | 102090 | 13935 | 1998 | 0.00012289 | 3.4863e-06 | 35.25 | 1 | 310 | Secondary | 74251 | Load | Tran1phPad | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005782 | PD-01152020-00595 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7021 | 817021 | 2020-01-15 18:01 | 2020-01-15 19:19 | 77.7 | 2 | 2 | 110.9167 | 13 | PREMATURE FAILURE | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | 6050 S.HARVEY | CMI_NORMAL | NO | NO | NO | 860523 | 159030 | 102108 | 9938 | 1789 | 0.00012889 | 2.3242e-06 | 55.4583 | 1 | 310 | Secondary | 31951 | Load | Tran1phPad | MIKE MITCHELL | 405-996-8178 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005789 | PD-01152020-00596 | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_621 | 550621 | 2020-01-15 18:51 | 2020-01-15 20:43 | 112.05 | 1 | 1 | 109.5 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | DURANT | 100 BLK S 34th es | CMI_NORMAL | NO | NO | NO | 860523 | 77575 | 15479 | 6735 | 901 | 0.00012725 | 1.1621e-06 | 109.5 | 1 | 310 | Load | 7656 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005793 | PD-01152020-00597 | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5629 | 865629 | 2020-01-15 19:21 | 2020-01-15 20:16 | 54.77 | 1 | 1 | 54.7667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 5009 S.RHODE-ISL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 159030 | 102108 | 2749 | 731 | 6.3643e-05 | 1.1621e-06 | 54.7667 | 1 | 320 | Customer | 11205 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005801 |  | ARKANSAS | FORT SMITH | 9512:ADABELL ROAD | ADABELL_ROAD_1222 | 951222 | 2020-01-15 19:41 | 2020-01-15 22:11 | 149.23 | 3 | 4 | 433.05 | 3 | DAMAGED BY PUBLIC | 32 | CONDUCTOR SECONDARY - UG | VAN BUREN | 209 ELFEN-GLEN CI | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 82173 | 61157 | 3122 | 1088 | 0.00050324 | 3.4863e-06 | 144.35 | 1 | 310 | Secondary | 13680 | Load | Tran1phPad | Contractor | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-15 | 2020 |  | Ark - Series 1, Ark - Series 2
J2001.005797 | PD-01152020-00598 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1222 | 831222 | 2020-01-15 19:43 | 2020-01-15 23:38 | 235.47 | 1 | 1 | 228.0167 | 22 | WIND | 17 | JUMPER | OKLAHOMA CITY | 2237 DAWN-MARIE DR | CMI_NORMAL | NO | NO | NO | 860523 | 168081 | 148276 | 7739 | 1009 | 0.00026497 | 1.1621e-06 | 228.0167 | 1 | 310 | Secondary | 13964 | Load | TranOpenDelta | DENNY J MORGAN | 405-501-1556 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2021
J2001.005807 |  | METRO EAST | CHANDLER | 7119:WARWICK | WARWICK_1941 | 711941 | 2020-01-15 20:20 | 2020-01-15 21:00 | 39.47 | 1 | 1 | 36.8 | 4 | DETERIORATION | 12 | POLE | LUTHER | 504 S.MAIN, LUTHER | CMI_PLANNED | YES | NO | NO | 860523 | 114345 | 7458 | 2416 | 1460 | 4.2765e-05 | 1.1621e-06 | 36.8 | 1 | 308 | Load | 6716 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2021
J2001.005806 |  | METRO EAST | CHANDLER | 7119:WARWICK | WARWICK_1941 | 711941 | 2020-01-15 20:25 | 2020-01-15 21:00 | 34.62 | 7 | 6 | 207.0833 | 4 | DETERIORATION | 12 | POLE | LUTHER | 403 S.ASH, LUTHER | CMI_PLANNED | YES | NO | NO | 860523 | 114345 | 7458 | 2416 | 1460 | 0.00024065 | 8.1346e-06 | 29.5833 | 1 | 310 | Load | 4597 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2021
J2001.005810 | PD-01152020-00601 | NORTHEAST | SAPULPA | 3220:KELLYVILLE | KELLYVILLE_2029 | 322029 | 2020-01-15 20:28 | 2020-01-15 22:02 | 93.93 | 5 | 6 | 445.9167 | 22 | WIND | 21 | FUSE - TRANSFORMER | KELLYVILLE | 100 BLK E ALLEN | CMI_NORMAL | NO | NO | NO | 860523 | 73979 | 40741 | 2551 | 971 | 0.00051819 | 5.8104e-06 | 89.1833 | 1 | 310 | Load | 44138 | Load | Tran1phOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2022
J2001.005816 | PD-01152020-00606 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-01-15 20:51 | 2020-01-15 22:34 | 103 | 4 | 6 | 360.3 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 3920 S.AGNEW PL | CMI_NORMAL | NO | NO | NO | 860523 | 159030 | 102108 | 7601 | 2458 | 0.0004187 | 4.6483e-06 | 90.075 | 1 | 310 | Load | 9867 | Load | Tran1phOH | THOMAS E COLE | 405-623-9338 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-15 | 2020 |  | #N/A
J2001.005814 |  | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-01-15 20:57 | 2020-01-15 23:02 | 124.87 | 1 | 1 | 98.4333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | TISHOMINGO | MAIN ST. AND MCLISH AVE | CMI_PLANNED | YES | NO | NO | 860523 | 77575 | 7202 | 2192 | 1673 | 0.00011439 | 1.1621e-06 | 98.4333 | 1 | 308 | Load | 23473 | Load | Tran3phWye | OGE | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | #N/A
J2001.005819 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1222 | 831222 | 2020-01-15 21:21 | 2020-01-15 23:30 | 128.58 | 1008 | 351 | 22535.5333 | 4 | DETERIORATION | 17 | JUMPER | OKLAHOMA CITY | 5529 CLASSEN BLVD | CMI_NORMAL | NO | NO | NO | 860523 | 168081 | 148276 | 7739 | 1009 | 0.026188 | 0.0011714 | 22.3567 | 1 | 310 | Feeder | BEL ISLE_1222 | Recloser | SubRecloser | [7 empty] | Equipment | N | SUBSTATION | 138kV | 2020-01-15 | 2020 |  | OK - 2021
J2001.005823 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1222 | 831222 | 2020-01-15 21:46 | 2020-01-15 21:48 | 2.22 | 1 | 1 | 2.2167 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 2505 NW.59 | CMI_MOMENTARY | YES | NO | NO | 860523 | 168081 | 148276 | 7739 | 1009 | 2.576e-06 | 1.1621e-06 | 2.2167 | 1 | 310 | Customer | 23667 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2021
J2001.005825 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1222 | 831222 | 2020-01-15 22:05 | 2020-01-15 22:12 | 7.78 | 1 | 1 | 7.7833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2915 UNTD-FDRS BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 168081 | 148276 | 7739 | 1009 | 9.0449e-06 | 1.1621e-06 | 7.7833 | 1 | 310 | Load | 27164 | Load | Tran3phWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-15 | 2020 |  | OK - 2021
J2001.005833 |  | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1724 | 911724 | 2020-01-15 22:47 | 2020-01-16 06:39 | 472.03 | 1 | 1 | 401.2167 | 28 | OTHER (DESCRIBE) | 2 | TRANSFORMER OH | BARLING | 607 FORT STREET, BARLING | CMI_PLANNED | YES | NO | NO | 860523 | 82173 | 61157 | 4239 | 611 | 0.00046625 | 1.1621e-06 | 401.2167 | 1 | 308 | Load | 220487 | Load | Tran3phWye | Contractor | [6 empty] | Other | N | DISTRIBUTION | 161kV | 2020-01-15 | 2020 |  | #N/A
J2001.005840 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-16 00:18 | 2020-01-16 00:31 | 12.65 | 2172 | 211 | 27475.8 | 1 | CANCELLED | 57 | CANCELLED | FT SMITH | 4699 S ZERO ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 82173 | 61157 | 2735 | 2123 | 0.031929 | 0.002524 | 12.65 | 1 | 310 | Feeder | CARNALL_2564 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-16 | 2020 |  | Ark - Series 2
J2001.005842 |  | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1723 | 911723 | 2020-01-16 00:22 | 2020-01-16 00:58 | 35.72 | 1 | 1 | 35.7167 | 4 | DETERIORATION | 18 | INSULATOR | BARLING | 1403 H | CMI_NORMAL | NO | NO | NO | 860523 | 82173 | 61157 | 4239 | 1624 | 4.1506e-05 | 1.1621e-06 | 35.7167 | 1 | 310 | Customer | 9714 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-16 | 2020 |  | #N/A
J2001.005843 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-16 00:22 | 2020-01-16 00:39 | 16.4 | 1 | 1 | 8.3667 | 1 | CANCELLED | 57 | CANCELLED | LAVACA | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860523 | 0 | 0 | 0 | 0 | 9.7228e-06 | 1.1621e-06 | 8.3667 | 1 | 310 | Customer |  | 0 | 0 | [6 empty] | 06/02/2020 note from burchamc. Reference J2001.005843 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | Ark - Series 2
J2001.005849 |  | METRO EAST | SEMINOLE | 7312:JUMPER CREEK | JUMPER_CREEK_1225 | 731225 | 2020-01-16 00:45 | 2020-01-16 01:55 | 69.7 | 7 | 2 | 475.65 | 4 | DETERIORATION | 12 | POLE | KONAWA | 2 SL W VAMOOSA CEM | CMI_PLANNED | YES | NO | NO | 860523 | 114345 | 13599 | 1216 | 331 | 0.00055275 | 8.1346e-06 | 67.95 | 1 | 310 | Mainline | 381606 | Switch | SwitchOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | OK - 2021
J2001.005850 | PD-01162020-00008 | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_721 | 510721 | 2020-01-16 01:00 | 2020-01-16 02:38 | 98.07 | 1 | 1 | 13.0167 | 4 | DETERIORATION | 50 | CONNECTOR | ARDMORE | 1410 9 NW. | CMI_NORMAL | NO | NO | NO | 860523 | 77575 | 23581 | 4510 | 684 | 1.5126e-05 | 1.1621e-06 | 13.0167 | 1 | 320 | Customer | 8307 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | #N/A
J2001.005870 | PD-01162020-00021 | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1371 | 831371 | 2020-01-16 04:31 | 2020-01-16 10:06 | 335.42 | 10 | 5 | 2525 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | YUKON | 1BLKS 1E RICH CH | CMI_NORMAL | NO | NO | NO | 860600 | 128678 | 115944 | 7876 | 3779 | 0.002934 | 1.162e-05 | 252.5 | 1 | 310 | Load | 42832 | Load | Tran1phOH | CURTIS W PINKERTON | 405-464-8500 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.005877 | PD-01162020-00025 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_871 | 830871 | 2020-01-16 05:21 | 2020-01-16 08:30 | 188.92 | 9 | 1 | 1513.05 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 18432 Camborne Av | CMI_NORMAL | NO | NO | NO | 860600 | 168081 | 148276 | 19362 | 4239 | 0.0017581 | 1.0458e-05 | 168.1167 | 1 | 310 | Load | 363261 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | OK - 2021
J2001.005880 | PD-01162020-00027 | METRO EAST | CHANDLER | 7119:WARWICK | WARWICK_1941 | 711941 | 2020-01-16 05:56 | 2020-01-16 10:00 | 243.5 | 1 | 1 | 243.5 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | LUTHER | SE 2ND,CEDAR-LUTH HIGH SCHOOL | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860600 | 114345 | 7458 | 2416 | 1460 | 0.00028294 | 1.162e-06 | 243.5 | 1 | 320 | Customer | 22724 | Load | Tran3phWye | JOSEPH WAYNE POOL | 405-919-2253 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | OK - 2021
J2001.005894 | PD-01162020-00040 | NORTHWEST | ALVA | 4707:KNOBHILL | KNOBHILL_730 | 470730 | 2020-01-16 07:26 | 2020-01-16 08:35 | 68.73 | 1 | 1 | 65.4667 | 12 | POOR CONNECTION | 50 | CONNECTOR | ALVA | 808 NOBLE--ALVA | CMI_NORMAL | NO | NO | NO | 860600 | 53509 | 5518 | 1742 | 526 | 7.6071e-05 | 1.162e-06 | 65.4667 | 1 | 310 | Customer | 9288 | Load | Tran1phOH | DENNIS PEARSON | 580-541-4106 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | #N/A
J2001.005897 | PD-01162020-00044 | METRO EAST | EAST | 8542:RENO | RENO_4224 | 854224 | 2020-01-16 07:37 | 2020-01-16 09:14 | 96.83 | 1 | 1 | 87.9833 | 4 | DETERIORATION | 50 | CONNECTOR | MIDWEST CITY | 3205 GLENVALLY DR | CMI_NORMAL | NO | NO | NO | 860600 | 114345 | 71192 | 5213 | 1221 | 0.00010223 | 1.162e-06 | 87.9833 | 1 | 310 | Customer | 16728 | Load | TranOpenDelta | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | OK - 2022
J2001.005898 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-16 07:44 | 2020-01-16 08:22 | 37.28 | 1 | 0 | 30.6333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | 0 | 1M E-HARTMAN,N-HL41/1 | CMI_PLANNED | YES | NO | NO | 860600 | 82173 | 7540 | 1504 | 1200 | 3.5595e-05 | 1.162e-06 | 30.6333 | 1 | 0 | Load | 4236 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-16 | 2020 |  | Ark - Series 2
J2001.005903 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-16 08:01 | 2020-01-16 11:58 | 236.88 | 1 | 1 | 233.5167 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | COLLIER ST. | CMI_PLANNED | YES | NO | NO | 860600 | 82173 | 61157 | 2735 | 2123 | 0.00027134 | 1.162e-06 | 233.5167 | 1 | 308 | Load | 201641 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | Ark - Series 2
J2001.005906 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-01-16 08:10 | 2020-01-16 14:01 | 350.98 | 3 | 1 | 985.55 | 4 | DETERIORATION | 28 | CROSSARM | BIXBY | 141ST + MEMORIAL-WS | CMI_PLANNED | YES | NO | NO | 860600 | 73979 | 40741 | 2749 | 1439 | 0.0011452 | 3.4859e-06 | 328.5167 | 1 | 308 | Mainline | 62946 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | OK - 2021
J2001.005910 |  | NORTHWEST | ENID | 4119:GLENWOOD | GLENWOOD_1929 | 411929 | 2020-01-16 08:19 | 2020-01-16 08:28 | 8.5 | 1 | 1 | 8.5 | 1 | CANCELLED | 57 | CANCELLED | ENID | CIVITAN HOMES, BLD A & B | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 53509 | 37573 | 5413 | 1453 | 9.8768e-06 | 1.162e-06 | 8.5 | 1 | 310 | Customer | 206296 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.005912 |  | METRO EAST | EAST | 8690:WILD MARY | WILD_MARY_9021 | 869021 | 2020-01-16 08:25 | 2020-02-05 11:26 | 28980.98 | 10 | 9 | 3869.55 | 23 | CUSTOMER EQUIPMENT | 1 | TRANSFORMER UG | OKLAHOMA CITY | 5200 E INTERSTATE 240 SERVICE RD | CMI_PLANNED | YES | NO | NO | 860600 | 114345 | 71192 | 4021 | 1774 | 0.0044963 | 1.162e-05 | 386.955 | 1 | 308 | Mainline | 409113 | Fuse | 0 | Crew | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.005914 | PD-01162020-00084 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1926 | 851926 | 2020-01-16 08:30 | 2020-01-16 10:03 | 93.3 | 1 | 1 | 93.3 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | MIDWEST CITY | 1516 MCDONALD DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 114345 | 71192 | 12434 | 2125 | 0.00010841 | 1.162e-06 | 93.3 | 1 | 310 | Customer | 21598 | Load | Tran1phOH | REX R WILSON | 405-535-4507 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | OK - 2021
J2001.005920 |  | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-16 08:38 | 2020-01-16 08:49 | 11.33 | 1 | 1 | 11.3333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSTANG | 423 MARYELLA TR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 128678 | 115944 | 18227 | 4429 | 1.3169e-05 | 1.162e-06 | 11.3333 | 1 | 310 | Load | 47034 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | OK - 2022
J2001.005924 | PD-01162020-00095 | SOUTHERN | HEALDTON | 5322:DUNDEE | DUNDEE 22 | 532222 | 2020-01-16 08:42 | 2020-01-16 10:20 | 98.13 | 1 | 3 | 54.45 | 4 | DETERIORATION | 50 | CONNECTOR | RINGLING | ALLEY N K WEST OF 8TH-RINGLING | CMI_NORMAL | NO | NO | NO | 860600 | 77575 | 6795 | 1012 | 1001 | 6.327e-05 | 1.162e-06 | 54.45 | 1 | 310 | Customer | 14258 | Load | Tran1phOH | CHAD A DOTSON | 405-488-5658 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.005925 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6126 | 836126 | 2020-01-16 08:47 | 2020-01-16 08:52 | 4.4 | 1 | 1 | 4.4 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 711 NW.32 | CMI_MOMENTARY | YES | NO | NO | 860600 | 168081 | 148276 | 11102 | 456 | 5.1127e-06 | 1.162e-06 | 4.4 | 1 | 310 | Customer | 18084 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | OK - 2022
J2001.005927 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-16 08:51 | 2020-01-16 08:57 | 6.37 | 1 | 1 | 6.3667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | LAVACA | 2400 WESTHILLS DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 82173 | 61157 | 2735 | 2123 | 7.3979e-06 | 1.162e-06 | 6.3667 | 1 | 310 | Customer | 18146 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | Ark - Series 2
J2001.005929 |  | ARKANSAS | FORT SMITH | 9508:WHITESIDE | WHITESIDE_822 | 950822 | 2020-01-16 08:59 | 2020-01-16 12:44 | 225.1 | 6 | 0 | 1297.1 | 4 | DETERIORATION | 12 | POLE | VAN BUREN | 312 VINE | CMI_PLANNED | YES | NO | NO | 860600 | 82173 | 61157 | 1919 | 209 | 0.0015072 | 6.9719e-06 | 216.1833 | 1 | 0 | Load | 12412 | Load | TranOpenDelta | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-16 | 2020 |  | Ark - Series 2
J2001.005930 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-01-16 09:00 | 2020-01-16 10:01 | 60.52 | 9 | 7 | 494.4 | 4 | DETERIORATION | 23 | FUSE - PRIMARY | FORT SMITH | 250 S CAVANAUGH,JOSEPH | CMI_PLANNED | YES | NO | NO | 860600 | 82173 | 61157 | 1455 | 1237 | 0.00057448 | 1.0458e-05 | 54.9333 | 1 | 308 | Mainline | 5548 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | Ark - Series 2
J2001.005931 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-16 09:04 | 2020-01-16 12:01 | 177.55 | 14 | 4 | 1968.4 | 4 | DETERIORATION | 12 | POLE | HARTMAN | 0 | CMI_PLANNED | YES | NO | NO | 860600 | 82173 | 7540 | 1504 | 1200 | 0.0022872 | 1.6268e-05 | 140.6 | 1 | 308 | Mainline |  | 0 | 0 | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-16 | 2020 |  | Ark - Series 2
J2001.005932 |  | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1371 | 831371 | 2020-01-16 09:04 | 2020-01-16 09:18 | 14.22 | 1 | 1 | 14.2167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | YUKON | 16516 WESTGATE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 128678 | 115944 | 7876 | 3779 | 1.6519e-05 | 1.162e-06 | 14.2167 | 1 | 310 | Load | 373219 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.005933 | PD-01162020-00143 | METRO EAST | SHAWNEE | 7433:ROCK CREEK | ROCK_CREEK_3328 | 743328 | 2020-01-16 09:07 | 2020-01-16 13:10 | 242.72 | 1 | 1 | 242.7167 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | SHAWNEE | 3-3/4 MN OBU ON KICK-SHAWNEE | CMI_NORMAL | NO | NO | NO | 860600 | 114345 | 22096 | 1799 | 765 | 0.00028203 | 1.162e-06 | 242.7167 | 1 | 310 | Load | 18360 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.005934 | PD-01162020-00165 | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-16 09:16 | 2020-01-16 10:27 | 71.12 | 1 | 1 | 71.1167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | LAVACA | LAVACA-N.2 + HOUSTON ST. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 82173 | 61157 | 2735 | 2123 | 8.2636e-05 | 1.162e-06 | 71.1167 | 1 | 310 | Customer | 8206 | Load | Tran1phOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | Ark - Series 2
J2001.005938 | PD-01162020-00151 | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-16 09:21 | 2020-01-16 11:06 | 105.35 | 1 | 1 | 40.8251 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MUSTANG | 423 MARYELLA TR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 128678 | 115944 | 18227 | 4429 | 4.7438e-05 | 1.162e-06 | 40.8251 | 1 | 310 | Load | 47034 | Load | Tran1phOH | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | OK - 2022
J2001.005939 | PD-01162020-00158 | NORTHEAST | SAPULPA | 3218:BEGGS | BEGGS_1829 | 321829 | 2020-01-16 09:23 | 2020-01-16 11:54 | 151.33 | 1 | 1 | 148.2667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MOUNDS | L11 STAGG ACRES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 73979 | 40741 | 1834 | 897 | 0.00017228 | 1.162e-06 | 148.2667 | 1 | 310 | Customer | 41987 | Load | Tran1phOH | JOSHUA N MCKINNEY | 918-863-6313 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | OK - 2020
J2001.005949 | PD-01162020-00159 | METRO EAST | SEMINOLE | 7208:CYPRESS | CYPRESS_822 | 720822 | 2020-01-16 09:24 | 2020-01-16 15:25 | 360.97 | 132 | 80 | 47227.4 | 3 | DAMAGED BY PUBLIC | 37 | CONDUCTOR PRIMARY - OH | HOLDENVILLE | 316 N OLIPHANT ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 114345 | 13599 | 2519 | 1431 | 0.054877 | 0.00015338 | 357.7833 | 1 | 311 | Mainline | 2133 | Fuse | FuseOH | AUSTIN WELLIVER | 405-221-0200 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | OK - 2020
J2001.005941 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1023 | 541023 | 2020-01-16 09:26 | 2020-01-16 09:26 | 0 | 842 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MADILL | 12537 HIGHWAY 199 | CMI_MOMENTARY | YES | NO | NO | 860600 | 77575 | 7202 | 2378 | 843 | 0 | 0.00097839 | 0 | 1 | 0 | Feeder | GLASSES_1023 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.005944 | PD-01162020-00156 | SOUTHERN | HEALDTON | 5322:DUNDEE | DUNDEE 22 | 532222 | 2020-01-16 09:29 | 2020-01-16 10:50 | 80.83 | 1 | 1 | 80.8333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | RINGLING | 0.6 miles West from Barley Rd + S. Dundee Rd | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 77575 | 6795 | 1012 | 1001 | 9.3927e-05 | 1.162e-06 | 80.8333 | 1 | 310 | Load | 28058 | Load | Tran1phOH | CHAD A DOTSON | 405-488-5658 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.005945 | PD-01162020-00162 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6322 | 816322 | 2020-01-16 09:29 | 2020-01-16 10:31 | 61.8 | 1 | 1 | 61.8 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 224 SW 132ND PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 159030 | 102108 | 11822 | 1816 | 7.181e-05 | 1.162e-06 | 61.8 | 1 | 310 | Customer | 179478 | Load | Tran1phPad | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.005955 |  | METRO NORTH | GUTHRIE | 8813:FITZGERALD CR | FITZGERALD_CR_1342 | 881342 | 2020-01-16 09:34 | 2020-01-16 10:27 | 53.7 | 1 | 1 | 49.75 | 4 | DETERIORATION | 2 | TRANSFORMER OH | GUTHRIE | 6200 N WESTMINISTER | CMI_PLANNED | YES | NO | NO | 860600 | 168081 | 19805 | 1044 | 808 | 5.7809e-05 | 1.162e-06 | 49.75 | 1 | 308 | Load | 221367 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.005965 |  | ARKANSAS | FORT SMITH | 9111:MASSARD | MASSARD_1122 | 911122 | 2020-01-16 10:03 | 2020-01-16 10:44 | 41.1 | 3 | 1 | 69.2 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 2221 S 74th St | CMI_PLANNED | YES | NO | NO | 860600 | 82173 | 61157 | 4984 | 947 | 8.0409e-05 | 3.4859e-06 | 23.0667 | 1 | 308 | Load | 9883 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-16 | 2020 |  | Ark - Series 3
J2001.005968 | PD-01162020-00195 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-01-16 10:11 | 2020-01-16 11:27 | 75.73 | 1 | 1 | 69.75 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 2606 N.SHARTEL | CMI_NORMAL | NO | NO | NO | 860600 | 168081 | 148276 | 11102 | 2337 | 8.1048e-05 | 1.162e-06 | 69.75 | 1 | 320 | Customer | 49976 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | OK - 2020
J2001.005971 |  | ARKANSAS | FORT SMITH | 9111:MASSARD | MASSARD_1122 | 911122 | 2020-01-16 10:20 | 2020-01-16 14:44 | 264.33 | 5 | 0 | 1321.6724 | 4 | DETERIORATION | 12 | POLE | 0 | 0 | CMI_PLANNED | YES | NO | NO | 860600 | 82173 | 61157 | 4984 | 947 | 0.0015358 | 5.8099e-06 | 264.3345 | 1 | 0 | Mainline |  | 0 | 0 | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-16 | 2020 |  | Ark - Series 3
J2001.005973 | PD-01162020-00200 | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2521 | 512521 | 2020-01-16 10:21 | 2020-01-16 12:26 | 124.42 | 1 | 1 | 118.65 | 4 | DETERIORATION | 27 | CUTOUT | LONE GROVE | 1S ON MER LN 1BK E | CMI_NORMAL | NO | NO | NO | 860600 | 77575 | 23581 | 3304 | 784 | 0.00013787 | 1.162e-06 | 118.65 | 1 | 310 | Load | 22186 | Load | Tran1phOH | CHRIS CLOSE | 405-238-0419 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.005980 | PD-01162020-00214 | ARKANSAS | FORT SMITH | 9340:TWIN BRIDGES | TWIN_BRIDGES_4021 | 934021 | 2020-01-16 10:31 | 2020-01-16 11:30 | 59.32 | 1 | 1 | 59.3167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | VAN BUREN | 4004 ALMA-HWY,350 S-HL9/16 1/2 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 82173 | 61157 | 1037 | 1037 | 6.8925e-05 | 1.162e-06 | 59.3167 | 1 | 310 | Customer | 3677 | Load | Tran1phOH | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-16 | 2020 |  | Ark - Series 1
J2001.005984 |  | SOUTHERN | DURANT | 5512:COLBERT | COLBERT_1222 | 551222 | 2020-01-16 10:35 | 2020-01-16 11:03 | 27.82 | 21 | 6 | 469.35 | 3 | DAMAGED BY PUBLIC | 12 | POLE | COLBERT | 1 BLK W-CLLNS ON SNIDR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 77575 | 15479 | 2165 | 1270 | 0.00054538 | 2.4402e-05 | 22.35 | 1 | 310 | Mainline | 876 | Fuse | FuseOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.005991 | PD-01162020-00237 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6923 | 846923 | 2020-01-16 10:54 | 2020-01-16 10:59 | 5.02 | 3 | 1 | 160.05 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | NE. 122ND ST | CMI_NORMAL | NO | NO | NO | 860600 | 168081 | 148276 | 7718 | 1132 | 0.00018597 | 3.4859e-06 | 53.35 | 1 | 310 | Mainline | 164023 | Fuse | FuseOH | ADAM COX | 405-328-8938 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.005993 | PD-01162020-00263 | NORTHEAST | SAPULPA | 3220:KELLYVILLE | KELLYVILLE_2024 | 322024 | 2020-01-16 11:05 | 2020-01-16 12:41 | 96.05 | 1 | 1 | 96.05 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SAPULPA | LOT 71-LAKE SAHOMA ESTATES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 73979 | 40741 | 2551 | 1580 | 0.00011161 | 1.162e-06 | 96.05 | 1 | 320 | Customer | 44332 | Load | Tran1phOH | GREGORY R HOOVER | 918-261-6803 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | OK - 2020
J2001.005996 | PD-01162020-00255 | METRO EAST | CHANDLER | 7118:KEY WEST | KEY_WEST_1846 | 711846 | 2020-01-16 11:11 | 2020-01-16 18:09 | 417.7 | 1 | 1 | 417.7 | 25 | LIGHTNING | 2 | TRANSFORMER OH | BRISTOW | 1/2MW,1/4MS-DEPEW | CMI_NORMAL | NO | NO | NO | 860600 | 114345 | 7458 | 1210 | 469 | 0.00048536 | 1.162e-06 | 417.7 | 1 | 310 | Load | 16881 | Load | Tran1phOH | DWAYNE FOX | 405-695-8501 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | OK - 2021
J2001.006000 | PD-01162020-00269 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2024 | 862024 | 2020-01-16 11:23 | 2020-01-16 12:47 | 84.12 | 1 | 1 | 76.7333 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 2801 S.HARVEY | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860600 | 159030 | 102108 | 4742 | 769 | 8.9163e-05 | 1.162e-06 | 76.7333 | 1 | 320 | Customer | 15723 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006006 | PD-01162020-00276 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6522 | 836522 | 2020-01-16 11:34 | 2020-01-16 12:42 | 68.33 | 1 | 1 | 10.5784 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6905 LONDON WY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 128678 | 115944 | 7419 | 1861 | 1.2292e-05 | 1.162e-06 | 10.5784 | 1 | 310 | Customer | 42728 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | OK - 2021
J2001.006018 | PD-01162020-00328 | ARKANSAS | FORT SMITH | 9111:MASSARD | MASSARD_1122 | 911122 | 2020-01-16 12:14 | 2020-01-16 13:32 | 77.68 | 42 | 45 | 2657.2 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | FORT SMITH | EUPER LN + S. 66 | CMI_NORMAL | NO | NO | NO | 860600 | 82173 | 61157 | 4984 | 947 | 0.0030876 | 4.8803e-05 | 63.2667 | 1 | 310 | Mainline | 4810 | Fuse | FuseOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-16 | 2020 |  | Ark - Series 3
J2001.006015 | PD-01162020-00323 | NORTHWEST | ALVA | 4528:SALINE | SALINE 23 | 452823 | 2020-01-16 12:17 | 2020-01-16 13:27 | 69.53 | 1 | 1 | 69.5333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | HELENA | HELENA W-HINKLEY,N-FOURTH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 53509 | 5518 | 668 | 318 | 8.0796e-05 | 1.162e-06 | 69.5333 | 1 | 310 | Customer | 2372 | Load | Tran1phOH | RANDY D MASON | 580-977-8823 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | #N/A
J2001.006020 | PD-01162020-00324 | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5822 | 845822 | 2020-01-16 12:24 | 2020-01-16 13:25 | 60.67 | 1 | 1 | 53.1833 | 4 | DETERIORATION | 20 | FUSE BARREL | SPENCER | 3925 SUNSET TR | CMI_NORMAL | NO | NO | NO | 860600 | 114345 | 71192 | 2985 | 934 | 6.1798e-05 | 1.162e-06 | 53.1833 | 1 | 310 | Load | 26344 | Load | Tran1phOH | BRADLEY SUDBECK | 405-999-6850 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | #N/A
J2001.006028 | PD-01162020-00353 | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-16 12:26 | 2020-01-16 14:12 | 105.88 | 6 | 3 | 595.7167 | 5 | ELECTRICAL TRACKING | 23 | FUSE - PRIMARY | STONE HILL | N.-HWY 22 W.-HWY 252 | CMI_NORMAL | NO | NO | NO | 860600 | 82173 | 61157 | 2735 | 2123 | 0.00069221 | 6.9719e-06 | 99.2861 | 1 | 310 | Tap | 3490 | Fuse | FuseOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | Ark - Series 2
J2001.006023 | PD-01162020-00341 | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_523 | 530523 | 2020-01-16 12:29 | 2020-01-16 15:59 | 210.4 | 1 | 1 | 202.4 | 25 | LIGHTNING | 2 | TRANSFORMER OH | HEALDTON | 1104 E.CHEROKEE ST | CMI_NORMAL | NO | NO | NO | 860600 | 77575 | 6795 | 2127 | 868 | 0.00023518 | 1.162e-06 | 202.4 | 1 | 310 | Customer | 8655 | Load | Tran1phOH | CHRIS CLOSE | 405-238-0419 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | #N/A
J2001.006024 | PD-01162020-00340 | SOUTHERN | HEALDTON | 5311:RATLIFF | RATLIFF_1127 | 531127 | 2020-01-16 12:29 | 2020-01-16 15:00 | 150.82 | 1 | 1 | 157.5333 | 25 | LIGHTNING | 34 | CONDUCTOR SECONDARY - OH | RATLIFF CITY | GRAY LEASE PUMP | CMI_NORMAL | NO | NO | NO | 860600 | 77575 | 6795 | 449 | 108 | 0.00018305 | 1.162e-06 | 157.5333 | 1 | 320 | Customer | 9789 | Load | TranOpenDelta | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006022 | PD-01162020-00327 | SOUTHERN | HEALDTON | 5321:WILDHORSE | WILDHORSE_2122 | 532122 | 2020-01-16 12:29 | 2020-01-16 12:35 | 5.65 | 1 | 1 | 5.65 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | RATLIFF CITY | 7 + 76,4N,.3W,NS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 77575 | 6795 | 155 | 35 | 6.5652e-06 | 1.162e-06 | 5.65 | 1 | 320 | Customer | 27233 | Load | TranOpenDelta | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | #N/A
J2001.006035 | PD-01162020-00364 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6326 | 816326 | 2020-01-16 13:10 | 2020-01-16 14:41 | 90.82 | 1 | 1 | 90.8167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1232 SW 154th Terr | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 159030 | 102108 | 11822 | 1259 | 0.00010553 | 1.162e-06 | 90.8167 | 1 | 310 | Customer | 415205 | Load | Tran1phPad | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006040 |  | METRO WEST | WEST | 8335:BETHANY | BETHANY_3526 | 833526 | 2020-01-16 13:34 | 2020-01-16 13:44 | 10.1 | 1 | 1 | 10.1 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BETHANY | 6702.5 NW.32 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 128678 | 115944 | 7867 | 2060 | 1.1736e-05 | 1.162e-06 | 10.1 | 1 | 310 | Customer | 34185 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | #N/A
J2001.006041 | PD-01162020-00377 | NORTHEAST | SAPULPA | 3213:BOWDEN | BOWDEN_1323 | 321323 | 2020-01-16 13:37 | 2020-01-16 14:34 | 56.55 | 1 | 1 | 56.55 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | TULSA | L 3 B 3 ROLLINGS MH PARK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 73979 | 40741 | 3372 | 912 | 6.571e-05 | 1.162e-06 | 56.55 | 1 | 310 | Customer | 44018 | Load | Tran1phPad | CGI ADMIN | 918-261-6802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | OK - 2020
J2001.006044 | PD-01162020-00380 | SOUTHERN | MADILL | 5409:LITTLE CITY | LITTLE CITY 21 | 540921 | 2020-01-16 13:40 | 2020-01-16 14:28 | 48.45 | 1 | 1 | 48.45 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | BRIDGEVIEW | HWY199/TIMBER HILL 2.3S WS | CMI_NORMAL | NO | NO | NO | 860600 | 77575 | 7202 | 610 | 591 | 5.6298e-05 | 1.162e-06 | 48.45 | 1 | 310 | Load | 351404 | Load | Tran3phWye | DAVID TAYLOR | 580-574-4517 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006043 | PD-01162020-00384 | SOUTHERN | MADILL | 5409:LITTLE CITY | LITTLE CITY 21 | 540921 | 2020-01-16 13:40 | 2020-01-16 15:24 | 104.35 | 1 | 1 | 104.35 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | BRIDGEVIEW | 1W 3S LITTLE CITY W SIDE | CMI_NORMAL | NO | NO | NO | 860600 | 77575 | 7202 | 610 | 591 | 0.00012125 | 1.162e-06 | 104.35 | 1 | 310 | Load | 28802 | Load | Tran3phWye | DAVID TAYLOR | 580-574-4517 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006047 | PD-01162020-00390 | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_624 | 550624 | 2020-01-16 13:57 | 2020-01-16 15:06 | 68.68 | 1 | 1 | 68.6833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DURANT | 1002 & 1004 W. MULBERRY - DURANT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 77575 | 15479 | 6735 | 1154 | 7.9809e-05 | 1.162e-06 | 68.6833 | 1 | 320 | Customer | 370496 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006050 | PD-01162020-00398 | SOUTHERN | HEALDTON | 5306:COUNTY LINE | COUNTY LINE 22 | 530622 | 2020-01-16 14:04 | 2020-01-16 14:54 | 49.67 | 1 | 1 | 49.6667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | HENNEPIN | 7/I-35 7.5W 1S 1.5W SS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 77575 | 6795 | 755 | 413 | 5.7712e-05 | 1.162e-06 | 49.6667 | 1 | 320 | Customer | 31247 | Load | Tran1phOH | CHAD A DOTSON | 405-488-5658 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | #N/A
J2001.006053 |  | METRO WEST | WEST | 8321:PIEDMONT | PIEDMONT_2164 | 832164 | 2020-01-16 14:13 | 2020-01-16 14:27 | 14.68 | 1 | 1 | 14.6833 | 11 | OVERLOAD | 5 | SWITCH - AIR | PIEDMONT | .5 Mile N of 178th & N. Piedmont | CMI_NORMAL | NO | NO | NO | 860600 | 128678 | 115944 | 6287 | 3004 | 1.7062e-05 | 1.162e-06 | 14.6833 | 1 | 310 | Customer | 389807 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006059 | PD-01162020-00407 | METRO WEST | WEST | 8321:PIEDMONT | PIEDMONT_2164 | 832164 | 2020-01-16 14:26 | 2020-01-16 15:58 | 92.32 | 1 | 1 | 68.2167 | 4 | DETERIORATION | 21 | FUSE - TRANSFORMER | PIEDMONT | 117 BRIDAL PATH - PIEDMONT | CMI_NORMAL | NO | NO | NO | 860600 | 128678 | 115944 | 6287 | 3004 | 7.9266e-05 | 1.162e-06 | 68.2167 | 1 | 310 | Load | 84668 | Load | Tran1phOH | STEVEN GILES | 405-227-2802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006060 | PD-01162020-00406 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-01-16 14:27 | 2020-01-16 15:10 | 42.92 | 1 | 1 | 31.3833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ARDMORE | 1MS ON DGWD WS | CMI_NORMAL | NO | NO | NO | 860600 | 77575 | 23581 | 2206 | 1000 | 3.6467e-05 | 1.162e-06 | 31.3833 | 1 | 310 | Customer | 17607 | Load | Tran1phOH | [7 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006071 |  | METRO EAST | SEMINOLE | 7208:CYPRESS | CYPRESS_822 | 720822 | 2020-01-16 15:12 | 2020-01-16 15:27 | 15.08 | 1 | 1 | 15.0833 | 1 | CANCELLED | 57 | CANCELLED | HOLDENVILLE | 617 E 8TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 114345 | 13599 | 2519 | 1431 | 1.7527e-05 | 1.162e-06 | 15.0833 | 1 | 310 | Customer | 4001 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | OK - 2020
J2001.006072 |  | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4821 | 824821 | 2020-01-16 15:15 | 2020-01-16 15:21 | 6.55 | 1 | 1 | 6.55 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2800 W. RENO | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 168081 | 148276 | 4192 | 242 | 7.611e-06 | 1.162e-06 | 6.55 | 1 | 310 | Customer | 83097 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | OK - 2022
J2001.006075 | PD-01162020-00444 | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_624 | 730624 | 2020-01-16 15:22 | 2020-01-16 16:23 | 60.63 | 1 | 1 | 53.2333 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | SEMINOLE | 822 E ST | CMI_NORMAL | NO | NO | NO | 860600 | 114345 | 13599 | 4061 | 1221 | 6.1856e-05 | 1.162e-06 | 53.2333 | 1 | 310 | Load | 361836 | Load | Tran1phOH | DELBERT HISAW | 405-683-1721 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | OK - 2020
J2001.006081 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-16 15:24 | 2020-01-16 16:00 | 36.33 | 4 | 3 | 120.9 | 4 | DETERIORATION | 12 | POLE | ARKOMA | 2005 Main | CMI_PLANNED | YES | NO | NO | 860600 | 82173 | 61157 | 2934 | 875 | 0.00014048 | 4.6479e-06 | 30.225 | 1 | 308 | Mainline | 4223 | Fuse | FuseOH | Contractor | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-16 | 2020 |  | Ark - Series 2
J2001.006077 | PD-01162020-00446 | NORTHEAST | SAPULPA | 3208:TIBBENS ROAD | TIBBENS_RD_824 | 320824 | 2020-01-16 15:26 | 2020-01-16 17:01 | 95.3 | 1 | 1 | 81 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | JENKS | W 110TH ST S | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860600 | 73979 | 40741 | 3141 | 1401 | 9.412e-05 | 1.162e-06 | 81 | 1 | 310 | Customer | 249890 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | OK - 2020
J2001.006084 | PD-01162020-00450 | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8121 | 838121 | 2020-01-16 15:33 | 2020-01-16 16:58 | 85.22 | 1 | 1 | 85.2167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | NW 80TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 128678 | 115944 | 8956 | 2258 | 9.902e-05 | 1.162e-06 | 85.2167 | 1 | 310 | Customer | 375002 | Load | Tran1phPad | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006086 | PD-01162020-00468 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1928 | 851928 | 2020-01-16 15:36 | 2020-01-16 16:22 | 46.25 | 1 | 1 | 46.25 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MIDWEST CITY | 8519 E.RENO | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 114345 | 71192 | 12434 | 2018 | 5.3742e-05 | 1.162e-06 | 46.25 | 1 | 310 | Customer | 51301 | Load | Tran1phPad | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006087 |  | METRO EAST | SHAWNEE | 7410:MAUD TAP | MAUD_TAP_1021 | 741021 | 2020-01-16 15:36 | 2020-01-16 15:36 | 0.02 | 760 | 0 | 12.6667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | 0 | 0 | CMI_MOMENTARY | YES | NO | NO | 860600 | 114345 | 22096 | 1017 | 760 | 1.4718e-05 | 0.0008831 | 0.016667 | 1 | 0 | Feeder | MAUD_TAP_1021 | Breaker | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006089 | PD-01162020-00469 | METRO WEST | WEST | 8297:MORGAN ROAD | MORGAN_ROAD_9722 | 829722 | 2020-01-16 15:39 | 2020-01-16 18:09 | 150.22 | 1 | 1 | 138.9667 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 619 N.MORGAN RD | CMI_NORMAL | NO | NO | NO | 860600 | 128678 | 115944 | 2498 | 664 | 0.00016148 | 1.162e-06 | 138.9667 | 1 | 310 | Customer | 65357 | Load | TranOpenDelta | TONY J ILG | 405-714-7441 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006092 |  | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1621 | 581621 | 2020-01-16 15:45 | 2020-01-16 16:05 | 19.53 | 1 | 1 | 19.5333 | 1 | CANCELLED | 57 | CANCELLED | ADA | 501 W.3 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 77575 | 11504 | 3454 | 1805 | 2.2697e-05 | 1.162e-06 | 19.5333 | 1 | 310 | Customer | 13423 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006098 | PD-01162020-00473 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4821 | 824821 | 2020-01-16 15:52 | 2020-01-16 18:00 | 127.57 | 1 | 2 | 127.5667 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 2800 W. RENO | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 168081 | 148276 | 4192 | 242 | 0.00014823 | 1.162e-06 | 127.5667 | 1 | 310 | Customer | 83097 | Load | TranOpenDelta | THOMAS E COLE | 405-623-9338 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | OK - 2022
J2001.006111 | PD-01162020-00498 | NORTHEAST | MUSKOGEE | 3313:ILLINOIS RIVER | ILLINOIS_RIVER_1321 | 331321 | 2020-01-16 16:13 | 2020-01-16 18:00 | 107.37 | 1 | 2 | 103.7667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | GORE | 2905 KEETOOWAH 3 | CMI_NORMAL | NO | NO | NO | 860600 | 73979 | 33238 | 791 | 791 | 0.00012057 | 1.162e-06 | 103.7667 | 1 | 310 | Load | 12367 | Load | Tran1phOH | NICHOLAS SELVIDGE | 918-652-1986 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | OK - 2020
J2001.006107 | PD-01162020-00495 | NORTHWEST | ENID | 4112:CHESTNUT | CHESTNUT_1221 | 411221 | 2020-01-16 16:15 | 2020-01-16 16:59 | 43.68 | 1 | 1 | 43.6833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ENID | 1322 ORLEANS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 53509 | 37573 | 2858 | 1112 | 5.0759e-05 | 1.162e-06 | 43.6833 | 1 | 310 | Customer | 707 | Load | Tran1phPad | WILLIAM R PETHICK | 580-278-8129 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | #N/A
J2001.006108 |  | NORTHEAST | SAPULPA | 3218:BEGGS | BEGGS_1824 | 321824 | 2020-01-16 16:19 | 2020-01-16 16:31 | 11.7 | 1 | 1 | 11.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BEGGS | 401 N CREEK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 73979 | 40741 | 1834 | 937 | 1.3595e-05 | 1.162e-06 | 11.7 | 1 | 310 | Customer | 42017 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | OK - 2020
J2001.006112 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_863 | 830863 | 2020-01-16 16:24 | 2020-01-16 17:24 | 59.05 | 1 | 1 | 59.05 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 14300 N. MAY AVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 168081 | 148276 | 19362 | 1672 | 6.8615e-05 | 1.162e-06 | 59.05 | 1 | 320 | Customer | 189613 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006122 | PD-01162020-00503 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_623 | 870623 | 2020-01-16 16:36 | 2020-01-16 19:29 | 172.63 | 1 | 1 | 172.6333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | NORMAN | 738 S.LAHOMA AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 159030 | 56922 | 7363 | 1898 | 0.0002006 | 1.162e-06 | 172.6333 | 1 | 310 | Customer | 36513 | Load | Tran1phOH | THOMAS E COLE | 405-623-9338 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | OK - 2021
J2001.006124 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_861 | 830861 | 2020-01-16 16:40 | 2020-01-16 16:45 | 5.42 | 1 | 1 | 5.4167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | Montague Sec 1 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 168081 | 148276 | 19362 | 3932 | 6.2941e-06 | 1.162e-06 | 5.4167 | 1 | 310 | Customer | 239148 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006126 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7021 | 817021 | 2020-01-16 16:45 | 2020-01-16 16:58 | 12.92 | 1 | 1 | 12.9167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 9147 S.SHARTEL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 159030 | 102108 | 9938 | 1789 | 1.5009e-05 | 1.162e-06 | 12.9167 | 1 | 310 | Customer | 2032 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006132 | PD-01162020-00513 | SOUTHERN | HEALDTON | 5306:COUNTY LINE | COUNTY LINE 22 | 530622 | 2020-01-16 17:07 | 2020-01-16 19:33 | 146.42 | 1 | 2 | 137.7 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | HENNEPIN | 7/I-35 7.5W 1S 1.5W SS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 77575 | 6795 | 755 | 413 | 0.00016 | 1.162e-06 | 137.7 | 1 | 310 | Customer | 31247 | Load | Tran1phOH | JUSTIN B MARSHALL | 580-221-5051 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | #N/A
J2001.006136 |  | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2024 | 822024 | 2020-01-16 17:38 | 2020-01-16 17:43 | 5.53 | 1 | 1 | 5.5333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2819 NW.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 168081 | 148276 | 6035 | 1775 | 6.4296e-06 | 1.162e-06 | 5.5333 | 1 | 310 | Customer | 13401 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | OK - 2020
J2001.006137 | PD-01162020-00517 | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_721 | 510721 | 2020-01-16 17:40 | 2020-01-16 20:40 | 180.2 | 1 | 1 | 1.8167 | 4 | DETERIORATION | 50 | CONNECTOR | ARDMORE | 1410 9 NW. | CMI_NORMAL | NO | NO | NO | 860600 | 77575 | 23581 | 4510 | 684 | 2.1109e-06 | 1.162e-06 | 1.8167 | 1 | 320 | Customer | 8307 | Load | Tran1phOH | JUSTIN B MARSHALL | 580-221-5051 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | #N/A
J2001.006139 |  | METRO EAST | SHAWNEE | 7432:ST GREGORY | ST_GREGORY_3229 | 743229 | 2020-01-16 17:46 | 2020-01-16 17:46 | 0.02 | 795 | 0 | 13.25 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | SHAWNEE | 13501 ACME RD | CMI_MOMENTARY | YES | NO | NO | 860600 | 114345 | 22096 | 4093 | 795 | 1.5396e-05 | 0.00092377 | 0.016667 | 1 | 0 | Feeder | ST_GREGORY_3229 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006141 | PD-01162020-00519 | METRO EAST | SHAWNEE | 7432:ST GREGORY | ST_GREGORY_3229 | 743229 | 2020-01-16 17:56 | 2020-01-16 20:11 | 135.07 | 795 | 338 | 76110.25 | 5 | ELECTRICAL TRACKING | 18 | INSULATOR | SHAWNEE | 13501 ACME RD | CMI_NORMAL | NO | NO | NO | 860600 | 114345 | 22096 | 4093 | 795 | 0.088439 | 0.00092377 | 95.7362 | 1 | 310 | Feeder | ST_GREGORY_3229 | Recloser | 0 | [7 empty] | Equipment | N | SUBSTATION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006156 | PD-01162020-00521 | METRO EAST | SHAWNEE | 7407:REMINGTON | REMINGTON 21 | 740721 | 2020-01-16 18:19 | 2020-01-16 20:09 | 109.68 | 1 | 1 | 109.6833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SHAWNEE | Seth Ln | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 114361 | 22098 | 3665 | 2020 | 0.00012745 | 1.162e-06 | 109.6833 | 1 | 310 | Customer | 350481 | Load | Tran1phPad | ADAM CLARK | 580-310-8924 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | OK - 2021
J2001.006161 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-01-16 18:27 | 2020-01-16 18:37 | 9.5 | 1 | 1 | 9.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 8300 NW 10TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 128705 | 115970 | 3405 | 2036 | 1.1039e-05 | 1.162e-06 | 9.5 | 1 | 310 | Customer | 70830 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006167 | PD-01162020-00523 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9929 | 829929 | 2020-01-16 18:34 | 2020-01-16 20:19 | 105.33 | 1 | 1 | 105.3333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | BETHANY | 2514 N.ROCKWELL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 128705 | 115970 | 9222 | 2206 | 0.0001224 | 1.162e-06 | 105.3333 | 1 | 310 | Customer | 47676 | Load | Tran1phPad | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006314 |  | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1524 | 811524 | 2020-01-16 18:52 | 2020-01-17 03:51 | 538.55 | 1 | 1 | 538.55 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1528 SW BINKLEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 159043 | 102116 | 6059 | 2072 | 0.00062578 | 1.162e-06 | 538.55 | 1 | 310 | Customer | 54794 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | OK - 2022
J2001.006185 | PD-01162020-00525 | METRO SOUTH | SOUTH | 8722:MILLENNIUM | MILLENNIUM_2231 | 872231 | 2020-01-16 18:56 | 2020-01-16 21:27 | 150.63 | 44 | 37 | 6664.5333 | 27 | TREE:NON PREVENTABLE | 17 | JUMPER | NORMAN | TECUMSEH AND 24 | CMI_NORMAL | NO | NO | NO | 860600 | 159043 | 56927 | 4205 | 2053 | 0.0077441 | 5.1127e-05 | 151.4667 | 1 | 310 | Mainline | 12132 | Fuse | FuseOH | CURTIS W PINKERTON | 405-464-8500 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006260 |  | METRO SOUTH | SOUTH | 8722:MILLENNIUM | MILLENNIUM_2231 | 872231 | 2020-01-16 18:59 | 2020-01-17 00:40 | 340.47 | 2 | 1 | 648.8667 | 29 | TREES : GROW IN | 17 | JUMPER | NORMAN | 4023 24 AV NE. | CMI_NORMAL | NO | NO | NO | 860600 | 159043 | 56927 | 4205 | 2053 | 0.00075397 | 2.324e-06 | 324.4333 | 1 | 310 | Load | 15870 | Load | Tran1phOH | CURTIS W PINKERTON | 405-464-8500 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006228 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-01-16 19:43 | 2020-01-16 19:43 | 0 | 1951 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 2204 HEFNER RD | CMI_MOMENTARY | YES | NO | NO | 860600 | 168094 | 148284 | 8786 | 1951 | 0 | 0.002267 | 0 | 1 | 0 | Feeder | TENNESSE_3635 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-16 | 2020 |  | OK - 2021
J2001.006229 |  | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2821 | 312821 | 2020-01-16 19:45 | 2020-01-16 20:01 | 15.3 | 1 | 1 | 15.3 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 3300 HANCOCK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 73992 | 33245 | 5273 | 1151 | 1.7778e-05 | 1.162e-06 | 15.3 | 1 | 310 | Customer | 15538 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-16 | 2020 |  | #N/A
J2001.006233 | PD-01162020-00529 | SOUTHERN | DURANT | 5505:DURANT | DURANT 22 | 550522 | 2020-01-16 19:49 | 2020-01-16 21:45 | 116.37 | 32 | 17 | 3547.2 | 5 | ELECTRICAL TRACKING | 27 | CUTOUT | DURANT | 4185 OLD HWY 70 | CMI_NORMAL | NO | NO | NO | 860600 | 77586 | 15483 | 1317 | 797 | 0.0041218 | 3.7183e-05 | 110.85 | 1 | 310 | Mainline | 5660 | Fuse | FuseOH | MICHAEL N STROHL | 903-821-1619 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006238 |  | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2222 | 832222 | 2020-01-16 19:58 | 2020-01-16 20:22 | 23.5 | 1 | 1 | 23.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1819 NW.38 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 168094 | 148284 | 9169 | 1556 | 2.7307e-05 | 1.162e-06 | 23.5 | 1 | 310 | Customer | 26603 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | OK - 2022
J2001.006239 | PD-01162020-00530 | METRO EAST | SEMINOLE | 7312:JUMPER CREEK | JUMPER_CREEK_1227 | 731227 | 2020-01-16 20:00 | 2020-01-16 21:07 | 67.1 | 1 | 1 | 17.2599 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | KONAWA | 321 SO MADISON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 114361 | 13599 | 1217 | 885 | 2.0056e-05 | 1.162e-06 | 17.2599 | 1 | 310 | Customer | 7144 | Load | TranOpenDelta | DELBERT HISAW | 405-683-1721 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | OK - 2021
J2001.006243 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6922 | 846922 | 2020-01-16 20:15 | 2020-01-16 20:27 | 12.12 | 1 | 1 | 12.1167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1304 NW.96 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 168094 | 148284 | 7718 | 1486 | 1.4079e-05 | 1.162e-06 | 12.1167 | 1 | 310 | Customer | 13086 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006264 |  | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-01-16 22:34 | 2020-01-16 22:34 | 0 | 1001 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 3623 RED CEDAR RD | CMI_MOMENTARY | YES | NO | NO | 860600 | 77586 | 23583 | 2207 | 1001 | 0 | 0.0011631 | 0 | 1 | 0 | Feeder | DRIPPING_SPRI_1129 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-16 | 2020 |  | #N/A
J2001.006265 |  | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1524 | 811524 | 2020-01-16 22:35 | 2020-01-16 22:41 | 5.57 | 1 | 1 | 5.5667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1212 SW.26 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 159043 | 102116 | 6059 | 2072 | 6.4684e-06 | 1.162e-06 | 5.5667 | 1 | 310 | Customer | 1660 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | OK - 2022
J2001.006277 | PD-01162020-00553 | METRO EAST | SEMINOLE | 7208:CYPRESS | CYPRESS_821 | 720821 | 2020-01-16 23:24 | 2020-01-17 01:38 | 133.58 | 17 | 14 | 2001.75 | 3 | DAMAGED BY PUBLIC | 23 | FUSE - PRIMARY | HOLDENVILLE | 900 W AGMKTRD N OLD270 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 114361 | 13599 | 2520 | 1088 | 0.002326 | 1.9754e-05 | 117.75 | 1 | 310 | Mainline | 5513 | Fuse | FuseRiser | DELBERT HISAW | 405-683-1721 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-16 | 2020 |  | #N/A
J2001.006292 | PD-01172020-00005 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6922 | 846922 | 2020-01-17 01:26 | 2020-01-17 02:33 | 66.7 | 1 | 1 | 66.7 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 736 1/2 W.HEFNER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 168094 | 148284 | 7718 | 1486 | 7.7504e-05 | 1.162e-06 | 66.7 | 1 | 310 | Customer | 85054 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006306 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3628 | 833628 | 2020-01-17 03:09 | 2020-01-17 03:09 | 0 | 1325 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 2204 HEFNER RD | CMI_MOMENTARY | YES | NO | NO | 860600 | 168094 | 148284 | 8786 | 1313 | 0 | 0.0015396 | 0 | 1 | 0 | Feeder | TENNESSE_3628 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006307 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3628 | 833628 | 2020-01-17 03:10 | 2020-01-17 03:57 | 47.07 | 1 | 1 | 47.0667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 2304 NW.112 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860600 | 168094 | 148284 | 8786 | 1313 | 5.4691e-05 | 1.162e-06 | 47.0667 | 1 | 310 | Customer | 27296 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006310 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6324 | 816324 | 2020-01-17 03:29 | 2020-01-17 03:29 | 0.07 | 429 | 0 | 0 | 16 | SUBSTATION OPERATION | 16 | LINE RECLOSER | MOORE | NW 12TH ST BTWN JANEWAY AND GALE ST | CMI_MOMENTARY | YES | NO | NO | 860600 | 159043 | 102116 | 11822 | 2048 | 0 | 0.00049849 | 0 | 1 | 0 | Mainline | 347960 | Recloser | Rec3phElectronic | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-17 | 2020 |  | OK - 2021
J2001.006311 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6324 | 816324 | 2020-01-17 03:29 | 2020-01-17 03:29 | 0 | 1644 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 241 SW 134TH ST | CMI_MOMENTARY | YES | NO | NO | 860600 | 159043 | 102116 | 11822 | 2048 | 0 | 0.0019103 | 0 | 1 | 0 | Feeder | SOUTHGAT_6324 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-17 | 2020 |  | OK - 2021
J2001.006317 |  | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1722 | 831722 | 2020-01-17 03:46 | 2020-01-17 03:47 | 0.07 | 1203 | 0 | 80.2 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 1327 NW 122ND ST | CMI_MOMENTARY | YES | NO | NO | 860693 | 168094 | 148284 | 6643 | 1203 | 9.3181e-05 | 0.0013977 | 0.066667 | 1 | 0 | Feeder | SKYLINE_1722 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006325 | PD-01172020-00010 | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_521 | 320521 | 2020-01-17 04:06 | 2020-01-17 07:50 | 223.68 | 18 | 19 | 3861 | 5 | ELECTRICAL TRACKING | 27 | CUTOUT | SAPULPA | W OF HICKORY ON LEE | CMI_NORMAL | NO | NO | NO | 860693 | 73992 | 40747 | 3840 | 1608 | 0.0044859 | 2.0913e-05 | 214.5 | 1 | 310 | Tap | 60146 | Fuse | FuseOH | DWAYNE FOX | 405-695-8501 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006321 | PD-01172020-00008 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6324 | 816324 | 2020-01-17 04:06 | 2020-01-17 07:25 | 198.58 | 3 | 3 | 583.7 | 4 | DETERIORATION | 18 | INSULATOR | MOORE | 105 LEVERICH CT | CMI_NORMAL | NO | NO | NO | 860693 | 159043 | 102116 | 11822 | 2048 | 0.00067817 | 3.4856e-06 | 194.5667 | 1 | 310 | Load | 20450 | Load | Tran1phOH | BRENTON DOWNES | 580-450-0056 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2021
J2001.006323 | PD-01172020-00009 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1222 | 831222 | 2020-01-17 04:11 | 2020-01-17 10:29 | 377.63 | 1 | 1 | 370.5833 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | 5600 N.MAY AV | CMI_NORMAL | NO | NO | NO | 860693 | 168094 | 148284 | 7742 | 1009 | 0.00043056 | 1.1619e-06 | 370.5833 | 1 | 310 | Load | 59871 | Load | Tran3phPadWye | JASON CLARK | 405-420-5186 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2021
J2001.006324 | PD-01172020-00013 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-17 04:15 | 2020-01-17 11:15 | 420.38 | 1 | 1 | 391.7333 | 29 | TREES : GROW IN | 37 | CONDUCTOR PRIMARY - OH | WINSLOW | RURAL WINSLOW | CMI_NORMAL | NO | NO | NO | 860693 | 82178 | 61159 | 3788 | 2584 | 0.00045514 | 1.1619e-06 | 391.7333 | 1 | 311 | Load | 3861 | Load | Tran1phOH | DWAIN C CAUGHERN | 479-459-0231 | [5 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-17 | 2020 |  | Ark - Series 2
J2001.006333 | PD-01172020-00022 | METRO EAST | SHAWNEE | 7433:ROCK CREEK | ROCK_CREEK_3328 | 743328 | 2020-01-17 05:03 | 2020-01-17 08:03 | 180.07 | 1 | 1 | 153.2667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | SHAWNEE | 1/3MN AYDLTE SUB WS | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860693 | 114361 | 22098 | 1799 | 765 | 0.00017807 | 1.1619e-06 | 153.2667 | 1 | 320 | Customer | 16395 | Load | Tran1phOH | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006334 | PD-01172020-00021 | ARKANSAS | POTEAU | 3506:CAVANAL MTN | CAVANAL MTN 22 | 350622 | 2020-01-17 05:07 | 2020-01-17 07:11 | 123.65 | 8 | 9 | 947.6 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | POTEAU | 309 N AVE | CMI_NORMAL | NO | NO | NO | 860693 | 82178 | 13479 | 2050 | 1061 | 0.001101 | 9.2948e-06 | 118.45 | 1 | 310 | Load | 4604 | Load | Tran1phOH | TOBY C MEAD | 918-658-5596 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | #N/A
J2001.006338 | PD-01172020-00020 | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_724 | 510724 | 2020-01-17 05:23 | 2020-01-17 09:56 | 272.97 | 32 | 30 | 8677.3333 | 25 | LIGHTNING | 27 | CUTOUT | ARDMORE | ALY E I ON 4TH SW | CMI_NORMAL | NO | NO | NO | 860693 | 77586 | 23583 | 4510 | 1626 | 0.010082 | 3.7179e-05 | 271.1667 | 1 | 310 | Tap | 5436 | Fuse | FuseOH | CHRIS CLOSE | 405-238-0419 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | #N/A
J2001.006345 | PD-01172020-00025 | NORTHEAST | SAPULPA | 3210:HICKORY HILL | HICKORY_HILL_1024 | 321024 | 2020-01-17 06:17 | 2020-01-17 10:06 | 229.02 | 1 | 1 | 229.0167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SAPULPA | 1025 E.TAFT 125A | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 73992 | 40747 | 2683 | 1246 | 0.00026608 | 1.1619e-06 | 229.0167 | 1 | 310 | Customer | 44756 | Load | TranOH3phDelta | JOSHUA N MCKINNEY | 918-863-6313 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006352 | PD-01172020-00030 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4821 | 824821 | 2020-01-17 07:04 | 2020-01-17 09:59 | 175.43 | 1 | 1 | 175.4333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2109 W. SHERIDAN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 168094 | 148284 | 4193 | 243 | 0.00020383 | 1.1619e-06 | 175.4333 | 1 | 310 | Customer | 1037 | Load | TranOpenDelta | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006354 |  | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2163 | 892163 | 2020-01-17 07:19 | 2020-01-17 07:52 | 33.1 | 1 | 1 | 33.1 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | UNION CITY | .5MS SW29 .5ME BAN RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 128705 | 12735 | 3177 | 1133 | 3.8457e-05 | 1.1619e-06 | 33.1 | 1 | 310 | Load | 63915 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2021
J2001.006357 | PD-01172020-00031 | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_622 | 880622 | 2020-01-17 07:24 | 2020-01-17 11:38 | 254.37 | 88 | 41 | 21376.6667 | 4 | DETERIORATION | 28 | CROSSARM | GUTHRIE | .9MN PINE + INDUSTRIAL | CMI_NORMAL | NO | NO | NO | 860693 | 168094 | 19810 | 5163 | 1164 | 0.024837 | 0.00010224 | 242.9167 | 1 | 310 | Mainline | 12046 | Fuse | FuseOH | HOWARD GETCHELL | 530-410-8920 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006356 |  | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_622 | 880622 | 2020-01-17 07:24 | 2020-01-17 07:24 | 0 | 1164 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | GUTHRIE | 800 W INDUSTRIAL RD | CMI_MOMENTARY | YES | NO | NO | 860693 | 168094 | 19810 | 5163 | 1164 | 0 | 0.0013524 | 0 | 1 | 0 | Feeder | COTWD CK_622 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006371 |  | NORTHEAST | MUSKOGEE | 3117:THREE RIVERS | THREE_RIVERS_1721 | 311721 | 2020-01-17 07:54 | 2020-01-17 08:17 | 23.7 | 1 | 1 | 23.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 2130 DAYTON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 73992 | 33245 | 2833 | 1047 | 2.7536e-05 | 1.1619e-06 | 23.7 | 1 | 310 | Customer | 3998 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-17 | 2020 |  | #N/A
J2001.006372 |  | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1221 | 911221 | 2020-01-17 07:57 | 2020-01-20 13:06 | 4629.47 | 1 | 0 | 1639.0167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | ON I BETWEEN 20 + 21 | CMI_PLANNED | YES | NO | NO | 860693 | 82178 | 61159 | 6594 | 1742 | 0.0019043 | 1.1619e-06 | 1639.0167 | 1 | 0 | Mainline | 132 | Fuse | FuseRiser | OGE | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | Ark - Series 1
J2001.006375 | PD-01172020-00043 | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2222 | 882222 | 2020-01-17 08:12 | 2020-01-17 15:01 | 409.38 | 1 | 2 | 167.5167 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | EDMOND | 19 BOB-WHITE TRL | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860693 | 168094 | 19810 | 5386 | 1160 | 0.00019463 | 1.1619e-06 | 167.5167 | 1 | 320 | Customer | 35324 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006377 | PD-01172020-00045 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-17 08:19 | 2020-01-17 10:24 | 125.22 | 1 | 1 | 125.4915 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | MOUNTAINBURG | LAKE FT SMITH VISITOR CENTER | CMI_NORMAL | NO | NO | NO | 860693 | 82178 | 61159 | 3788 | 2584 | 0.0001458 | 1.1619e-06 | 125.4915 | 1 | 321 | Load | 251225 | Load | Tran3phPadWye | KRIS L HALMES | 479-430-9447 | [5 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-17 | 2020 |  | Ark - Series 2
J2001.006378 | PD-01172020-00048 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-17 08:28 | 2020-01-17 10:51 | 142.9 | 1 | 2 | 132.4833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | MOUNTAINBURG | OLD SHEPHERD SPRINGS RD | CMI_NORMAL | NO | NO | NO | 860693 | 82178 | 61159 | 3788 | 2584 | 0.00015393 | 1.1619e-06 | 132.4833 | 1 | 310 | Load | 220489 | Load | TranOH3phDelta | ANTHONY SELF | 479-719-0734 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-17 | 2020 |  | Ark - Series 2
J2001.006381 | PD-01172020-00087 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1521 | 811521 | 2020-01-17 08:36 | 2020-01-17 10:02 | 86.48 | 1 | 1 | 56.749 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1236 SW.18 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 159043 | 102116 | 6059 | 1241 | 6.5934e-05 | 1.1619e-06 | 56.749 | 1 | 310 | Customer | 17846 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006384 | PD-01172020-00080 | NORTHEAST | MUSKOGEE | 3117:THREE RIVERS | THREE_RIVERS_1721 | 311721 | 2020-01-17 08:47 | 2020-01-17 09:40 | 52.55 | 1 | 1 | 52.55 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 2130 DAYTON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 73992 | 33245 | 2833 | 1047 | 6.1055e-05 | 1.1619e-06 | 52.55 | 1 | 310 | Customer | 3998 | Load | Tran1phOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-17 | 2020 |  | #N/A
J2001.006394 | PD-01172020-00099 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2222 | 832222 | 2020-01-17 09:00 | 2020-01-17 10:50 | 110.07 | 1 | 2 | 60.2333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2531 NW.42 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 168094 | 148284 | 9169 | 1556 | 6.9982e-05 | 1.1619e-06 | 60.2333 | 1 | 320 | Customer | 8916 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006390 | PD-01172020-00097 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3722 | 833722 | 2020-01-17 09:05 | 2020-01-17 10:01 | 56.03 | 1 | 1 | 27.0833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1206 NW.83 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 168094 | 148284 | 5759 | 1109 | 3.1467e-05 | 1.1619e-06 | 27.0833 | 1 | 310 | Customer | 8996 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006396 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6922 | 846922 | 2020-01-17 09:20 | 2020-01-17 09:49 | 29.32 | 1 | 1 | 29.3167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 736 1/2 W.HEFNER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 168094 | 148284 | 7718 | 1486 | 3.4062e-05 | 1.1619e-06 | 29.3167 | 1 | 310 | Customer | 85054 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006398 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6922 | 846922 | 2020-01-17 09:25 | 2020-01-17 09:45 | 19.88 | 1 | 1 | 19.8833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1132 NW.105 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 168094 | 148284 | 7718 | 1486 | 2.3102e-05 | 1.1619e-06 | 19.8833 | 1 | 310 | Customer | 23229 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006397 | PD-01172020-00091 | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_423 | 710423 | 2020-01-17 09:26 | 2020-01-17 10:44 | 78.18 | 1 | 1 | 78.1833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | CHANDLER | 927 E 1ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 114361 | 7459 | 2821 | 975 | 9.0838e-05 | 1.1619e-06 | 78.1833 | 1 | 310 | Customer | 8343 | Load | Tran1phOH | CAMERON PITTS | 405-537-6633 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006401 |  | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1421 | 311421 | 2020-01-17 09:35 | 2020-01-17 09:41 | 5.9 | 1 | 1 | 5.9 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 230 N 40 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 73992 | 33245 | 4563 | 1103 | 6.8549e-06 | 1.1619e-06 | 5.9 | 1 | 310 | Customer | 229841 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | #N/A
J2001.006402 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2122 | 822122 | 2020-01-17 09:36 | 2020-01-17 09:54 | 17.97 | 1 | 1 | 17.9667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4041 NW.14 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 168094 | 148284 | 9244 | 1837 | 2.0875e-05 | 1.1619e-06 | 17.9667 | 1 | 320 | Customer | 4222 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2020
J2001.006407 | PD-01172020-00119 | METRO EAST | SHAWNEE | 7432:ST GREGORY | ST_GREGORY_3224 | 743224 | 2020-01-17 09:49 | 2020-01-17 14:28 | 279.3 | 2 | 1 | 441.3667 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | SHAWNEE | 1900 W.MACARTHUR | CMI_NORMAL | NO | NO | NO | 860693 | 114361 | 22098 | 4092 | 1372 | 0.0005128 | 2.3237e-06 | 220.6833 | 1 | 310 | Load | 90217 | Load | 0 | JEREMIAH D WALKER | 405-974-0464 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006409 | PD-01172020-00115 | SOUTHERN | SULPHUR | 5705:SULPHUR | SULPHUR_523 | 570523 | 2020-01-17 09:54 | 2020-01-17 10:32 | 38.37 | 1 | 1 | 8.6321 | 25 | LIGHTNING | 1 | TRANSFORMER UG | SULPHUR | SEWAGE DISP + PLANT | CMI_NORMAL | NO | NO | NO | 860693 | 77586 | 6811 | 3631 | 1088 | 1.0029e-05 | 1.1619e-06 | 8.6321 | 1 | 310 | Load | 12966 | Load | Tran3phWye | CHRIS CLOSE | 405-238-0419 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2021
J2001.006412 | PD-01172020-00131 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1524 | 811524 | 2020-01-17 10:02 | 2020-01-17 11:15 | 72.57 | 1 | 1 | 50.7405 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1528 SW BINKLEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 159043 | 102116 | 6059 | 2072 | 5.8953e-05 | 1.1619e-06 | 50.7405 | 1 | 310 | Customer | 54794 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006415 | PD-01172020-00130 | NORTHEAST | SAPULPA | 3213:BOWDEN | BOWDEN_1329 | 321329 | 2020-01-17 10:05 | 2020-01-17 13:07 | 182.03 | 1 | 1 | 164.3 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | SAPULPA | 1/4 E HWY 97 ON 71ST 1/4 SO. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 73992 | 40747 | 3372 | 1517 | 0.00019089 | 1.1619e-06 | 164.3 | 1 | 320 | Customer | 43851 | Load | Tran1phOH | CGI ADMIN | 918-261-6802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2020
J2001.006417 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2123 | 822123 | 2020-01-17 10:11 | 2020-01-17 10:29 | 17.93 | 1 | 1 | 17.9333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3844 NW.20 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 168094 | 148284 | 9244 | 1668 | 2.0836e-05 | 1.1619e-06 | 17.9333 | 1 | 310 | Customer | 7579 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2020
J2001.006420 |  | METRO WEST | WEST | 8222:CZECH HALL | CZECH_HALL_2222 | 822222 | 2020-01-17 10:18 | 2020-01-17 10:47 | 29.27 | 1 | 1 | 29.2667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 11501 LOCHWOOD DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 128705 | 115970 | 8599 | 2027 | 3.4004e-05 | 1.1619e-06 | 29.2667 | 1 | 310 | Customer | 76447 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006421 |  | METRO WEST | WEST | 8342:BRADEN PARK | BRADEN_PARK_4223 | 834223 | 2020-01-17 10:19 | 2020-01-17 10:50 | 31.5 | 1 | 1 | 31.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1/2MN NW.122 + MAC ARTHUR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 128705 | 115970 | 3399 | 1782 | 3.6598e-05 | 1.1619e-06 | 31.5 | 1 | 310 | Customer | 70868 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006423 | PD-01172020-00139 | METRO SOUTH | SOUTH | 8722:MILLENNIUM | MILLENNIUM_2231 | 872231 | 2020-01-17 10:22 | 2020-01-17 12:24 | 121.62 | 1 | 1 | 9.8169 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | 2920 Misty Ridge Dr | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 159043 | 56927 | 4205 | 2053 | 1.1406e-05 | 1.1619e-06 | 9.8169 | 1 | 310 | Customer | 100175 | Load | Tran1phPad | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006433 |  | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3621 | 853621 | 2020-01-17 10:38 | 2020-01-17 11:08 | 29.87 | 1 | 1 | 29.8667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1519 NE.9 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 168094 | 148284 | 5920 | 2165 | 3.4701e-05 | 1.1619e-06 | 29.8667 | 1 | 310 | Customer | 22146 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006437 |  | METRO WEST | WEST | 8158:SARA | SARA_5864 | 815864 | 2020-01-17 10:48 | 2020-01-17 11:28 | 40.6 | 1 | 1 | 40.6 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 12521 SWEETWATER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 128705 | 115970 | 18232 | 4810 | 4.7171e-05 | 1.1619e-06 | 40.6 | 1 | 310 | Customer | 70259 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006439 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6124 | 836124 | 2020-01-17 10:49 | 2020-01-17 11:31 | 42.4 | 1 | 1 | 42.4 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1729 NW.30 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 168094 | 148284 | 11100 | 1764 | 4.9263e-05 | 1.1619e-06 | 42.4 | 1 | 310 | Customer | 1330 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2020
J2001.006449 |  | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3722 | 833722 | 2020-01-17 11:04 | 2020-01-17 11:33 | 28.82 | 1 | 2 | 28.8167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1206 NW.83 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 168094 | 148284 | 5759 | 1109 | 3.3481e-05 | 1.1619e-06 | 28.8167 | 1 | 310 | Customer | 8996 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006444 | PD-01172020-00167 | NORTHWEST | ENID | 4107:CLEVELAND AVE | CLEVELAND_AVE_723 | 410723 | 2020-01-17 11:07 | 2020-01-17 11:44 | 37.22 | 1 | 1 | 37.2167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ENID | 2206 W BROADWAY AVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 53513 | 37577 | 4460 | 1418 | 4.324e-05 | 1.1619e-06 | 37.2167 | 1 | 320 | Customer | 345635 | Load | Tran1phOH | WILLIAM R PETHICK | 580-278-8129 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | #N/A
J2001.006451 |  | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1423 | 311423 | 2020-01-17 11:21 | 2020-01-17 11:48 | 27.15 | 1 | 1 | 27.15 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 562 N.10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 73992 | 33245 | 4563 | 1493 | 3.1544e-05 | 1.1619e-06 | 27.15 | 1 | 310 | Customer | 5110 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | OK - 2020
J2001.006452 | PD-01172020-00185 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-17 11:23 | 2020-01-17 12:36 | 72.88 | 1 | 1 | 72.8833 | 5 | ELECTRICAL TRACKING | 18 | INSULATOR | MOUNTAINBURG | HWY 71 NW OF HL17/6 500 | CMI_NORMAL | NO | NO | NO | 860693 | 82178 | 61159 | 3788 | 2584 | 8.468e-05 | 1.1619e-06 | 72.8833 | 1 | 310 | Customer | 16542 | Load | Tran3phWye | DWAIN C CAUGHERN | 479-459-0231 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-17 | 2020 |  | Ark - Series 2
J2001.006457 | PD-01172020-00188 | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2524 | 512524 | 2020-01-17 11:37 | 2020-01-17 12:23 | 45.77 | 1 | 1 | 45.7667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | LONE GROVE | MER/70: .5S, ES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 77586 | 23583 | 3304 | 998 | 5.3174e-05 | 1.1619e-06 | 45.7667 | 1 | 310 | Load | 30547 | Load | Tran1phOH | RANDAL G CALLAWAY | 580-220-8449 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006469 | PD-01172020-00207 | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2822 | 312822 | 2020-01-17 11:42 | 2020-01-17 13:16 | 94.33 | 1 | 2 | 94.3333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 09 RODMAN CI | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 73992 | 33245 | 5273 | 1107 | 0.0001096 | 1.1619e-06 | 94.3333 | 1 | 310 | Customer | 6581 | Load | Tran1phOH | REID R WILLIAMS | 512-618-8800 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-17 | 2020 |  | OK - 2020
J2001.006464 | PD-01172020-00205 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3729 | 833729 | 2020-01-17 11:48 | 2020-01-17 15:54 | 246.03 | 1 | 1 | 246.0333 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 313 NW.90 | CMI_NORMAL | NO | NO | NO | 860693 | 168094 | 148284 | 5759 | 1401 | 0.00028585 | 1.1619e-06 | 246.0333 | 1 | 320 | Customer | 24304 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2021
J2001.006476 |  | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2024 | 822024 | 2020-01-17 12:18 | 2020-01-17 12:39 | 21.57 | 1 | 1 | 21.5667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 2115 NW 19TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 168094 | 148284 | 6034 | 1775 | 2.5057e-05 | 1.1619e-06 | 21.5667 | 1 | 310 | Customer | 6910 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | OK - 2020
J2001.006477 | PD-01172020-00224 | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_521 | 560521 | 2020-01-17 12:24 | 2020-01-17 12:57 | 32.85 | 1 | 1 | 32.85 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | PAULS VALLEY | 803 E.AVENUE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 77586 | 6206 | 2457 | 468 | 3.8167e-05 | 1.1619e-06 | 32.85 | 1 | 320 | Customer | 3331 | Load | TranOpenDelta | BRUCE E BEAM | 405-626-0490 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006482 | PD-01172020-00226 | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_724 | 510724 | 2020-01-17 12:34 | 2020-01-17 14:16 | 101.73 | 2 | 3 | 166.4667 | 4 | DETERIORATION | 50 | CONNECTOR | ARDMORE | 522 H SW. | CMI_NORMAL | NO | NO | NO | 860693 | 77586 | 23583 | 4510 | 1626 | 0.00019341 | 2.3237e-06 | 83.2333 | 1 | 310 | Secondary | 7064 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | #N/A
J2001.006490 | PD-01172020-00238 | NORTHWEST | ALVA | 4705:ALVA | ALVA_522 | 470522 | 2020-01-17 12:51 | 2020-01-17 13:53 | 61.93 | 1 | 1 | 61.9333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ALVA | 710 BARNES AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 53513 | 5518 | 2438 | 1120 | 7.1958e-05 | 1.1619e-06 | 61.9333 | 1 | 310 | Customer | 9034 | Load | Tran1phOH | DENNIS PEARSON | 580-541-4106 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | #N/A
J2001.006491 | PD-01172020-00250 | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_624 | 880624 | 2020-01-17 12:52 | 2020-01-17 14:59 | 127.12 | 1 | 1 | 127.1167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | GUTHRIE | 110 W HARRISON AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 168094 | 19810 | 5163 | 707 | 0.00014769 | 1.1619e-06 | 127.1167 | 1 | 320 | Customer | 43648 | Load | Tran3phWye | JOSEPH WAYNE POOL | 405-919-2253 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006492 | PD-01172020-00237 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5121 | 815121 | 2020-01-17 12:54 | 2020-01-17 13:29 | 35.17 | 1 | 1 | 35.1667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2608 SW.84 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 159043 | 102116 | 13933 | 1998 | 4.0859e-05 | 1.1619e-06 | 35.1667 | 1 | 310 | Customer | 25047 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006497 | PD-01172020-00241 | ARKANSAS | OZARK | 9224:BRANCH | BRANCH_2462 | 922462 | 2020-01-17 13:03 | 2020-01-17 14:37 | 93.93 | 1 | 1 | 93.9333 | 12 | POOR CONNECTION | 50 | CONNECTOR | CHARLESTON | 316 LOGAN | CMI_NORMAL | NO | NO | NO | 860693 | 82178 | 7540 | 1792 | 972 | 0.00010914 | 1.1619e-06 | 93.9333 | 1 | 320 | Customer | 12594 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-17 | 2020 |  | Ark - Series 3
J2001.006505 | PD-01172020-00253 | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-17 13:03 | 2020-01-17 14:43 | 99.9 | 6 | 7 | 98.9 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MUSTANG | 309 W. APPLE BRANCH WAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 128705 | 115970 | 18232 | 4429 | 0.00011491 | 6.9711e-06 | 16.4833 | 1 | 310 | Secondary | 63880 | Load | Tran1phPad | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006499 | PD-01172020-00247 | NORTHEAST | MUSKOGEE | 3326:JAMESVILLE | JAMESVILLE_2623 | 332623 | 2020-01-17 13:10 | 2020-01-17 19:36 | 386.02 | 1 | 2 | 26.4162 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | HASKELL | 1.5 W.HWY64 AND HIGHSCHOOL RD | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860693 | 73992 | 33245 | 1548 | 402 | 3.0692e-05 | 1.1619e-06 | 26.4162 | 1 | 320 | Customer | 23177 | Load | Tran1phOH | GARY MICHAEL KNUPP | 918-577-8564 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | #N/A
J2001.006502 |  | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_624 | 550624 | 2020-01-17 13:14 | 2020-01-17 13:25 | 10.9 | 1 | 1 | 10.9 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DURANT | 1026 W.MAIN ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 77586 | 15483 | 6737 | 1155 | 1.2664e-05 | 1.1619e-06 | 10.9 | 1 | 310 | Customer | 741 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006509 |  | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3023 | 743023 | 2020-01-17 13:20 | 2020-01-17 13:20 | 0.23 | 1135 | 0 | 264.8333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | SHAWNEE | 318 S KENNEDY | CMI_MOMENTARY | YES | NO | NO | 860693 | 114361 | 22098 | 6641 | 1137 | 0.0003077 | 0.0013187 | 0.23333 | 1 | 0 | Feeder | INGLEWOOD_3023 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-17 | 2020 |  | OK - 2021
J2001.006511 | PD-01172020-00259 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3023 | 743023 | 2020-01-17 13:27 | 2020-01-17 17:07 | 220.58 | 20 | 10 | 3637.5 | 22 | WIND | 37 | CONDUCTOR PRIMARY - OH | SHAWNEE | COR OF LEO+CLRPOND WSD | CMI_NORMAL | NO | NO | NO | 860693 | 114361 | 22098 | 6641 | 1137 | 0.0042262 | 2.3237e-05 | 181.875 | 1 | 310 | Mainline | 958 | Fuse | FuseOH | DAVID M CLEMMONS | 405-777-8355 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2021
J2001.006512 | PD-01172020-00258 | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2721 | 872721 | 2020-01-17 13:28 | 2020-01-17 14:43 | 75.47 | 1 | 1 | 13.5662 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | 405 MIMOSA DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 159043 | 56927 | 6459 | 934 | 1.5762e-05 | 1.1619e-06 | 13.5662 | 1 | 310 | Customer | 54039 | Load | Tran1phOH | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006522 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-17 13:37 | 2020-01-17 14:04 | 27.07 | 2 | 1 | 47.9 | 4 | DETERIORATION | 18 | INSULATOR | MOUNTAINBURG | HWY 71 AT HL 17/6 | CMI_PLANNED | YES | NO | NO | 860693 | 82178 | 61159 | 3788 | 2584 | 5.5653e-05 | 2.3237e-06 | 23.95 | 1 | 308 | Tap | 6406 | Fuse | FuseOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-17 | 2020 |  | Ark - Series 2
J2001.006527 | PD-01172020-00276 | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4029 | 914029 | 2020-01-17 13:44 | 2020-01-17 15:16 | 91.58 | 1 | 1 | 91.5833 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | FORT SMITH | 7514 S.HWY-271 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860693 | 82178 | 61159 | 4756 | 1102 | 0.00010641 | 1.1619e-06 | 91.5833 | 1 | 310 | Customer | 6329 | Load | Tran1phOH | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-17 | 2020 |  | Ark - Series 2
J2001.006528 | PD-01172020-00277 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3925 | 833925 | 2020-01-17 13:45 | 2020-01-17 15:34 | 109.08 | 8 | 5 | 633.4667 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | WARR ACRES | 5956 NW.60 | CMI_NORMAL | NO | NO | NO | 860693 | 168094 | 148284 | 7849 | 2183 | 0.000736 | 9.2948e-06 | 79.1833 | 1 | 310 | Load | 23406 | Load | Tran1phOH | BRANDON H SMITH | 405-371-4294 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006532 |  | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3722 | 833722 | 2020-01-17 13:52 | 2020-01-17 15:15 | 83.1 | 1 | 1 | 83.1 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1206 NW.83 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 168094 | 148284 | 5759 | 1109 | 9.655e-05 | 1.1619e-06 | 83.1 | 1 | 310 | Customer | 8996 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006530 | PD-01172020-00286 | METRO WEST | EL RENO | 8908:ROMAN NOSE | ROMAN_NOSE_852 | 890852 | 2020-01-17 13:52 | 2020-01-17 18:59 | 307.1 | 1 | 1 | 307.1 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | LOYAL | 41/4MS LOYAL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 128705 | 12735 | 524 | 255 | 0.00035681 | 1.1619e-06 | 307.1 | 1 | 320 | Load | 70323 | Load | Tran1phOH | GRADY LYLE NELSON | 405-401-8829 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006531 | PD-01172020-00287 | METRO WEST | EL RENO | 8908:ROMAN NOSE | ROMAN_NOSE_852 | 890852 | 2020-01-17 13:52 | 2020-01-17 18:54 | 302.03 | 1 | 1 | 302.0333 | 4 | DETERIORATION | 50 | CONNECTOR | LOYAL | 4.5 MI S LOYAL ES | CMI_NORMAL | NO | NO | NO | 860693 | 128705 | 12735 | 524 | 255 | 0.00035092 | 1.1619e-06 | 302.0333 | 1 | 320 | Load | 65016 | Load | Tran3phWye | GRADY LYLE NELSON | 405-401-8829 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006534 | PD-01172020-00284 | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2923 | 812923 | 2020-01-17 13:54 | 2020-01-17 14:59 | 65.5 | 1 | 1 | 12.2109 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 6012 S.VILLA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 159043 | 102116 | 6377 | 1633 | 1.4187e-05 | 1.1619e-06 | 12.2109 | 1 | 310 | Customer | 25760 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | #N/A
J2001.006538 | PD-01172020-00293 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5121 | 815121 | 2020-01-17 14:19 | 2020-01-17 15:18 | 59.03 | 1 | 1 | 16.9475 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3RD L. S/97 ON ES BROOKLINE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 159043 | 102116 | 13933 | 1998 | 1.9691e-05 | 1.1619e-06 | 16.9475 | 1 | 310 | Customer | 74867 | Load | Tran1phPad | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006548 | PD-01172020-00312 | NORTHWEST | ENID | 4219:BUNCH CREEK | BUNCH CREEK 41 | 421941 | 2020-01-17 14:37 | 2020-01-17 18:46 | 249.53 | 18 | 5 | 4348.95 | 22 | WIND | 28 | CROSSARM | GARBER | 1/2 N 1/8 E GARBER | CMI_NORMAL | NO | NO | NO | 860693 | 53513 | 37577 | 911 | 911 | 0.0050528 | 2.0913e-05 | 241.6083 | 1 | 310 | Mainline | 2803 | Fuse | FuseOH | PATRICK R KIFER | 405-509-0114 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006549 | PD-01172020-00313 | METRO WEST | WEST | 8323:RICHARDS | RICHARDS_2323 | 832323 | 2020-01-17 14:40 | 2020-01-17 16:01 | 80.68 | 1 | 1 | 80.6833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 11209 CIMARRON ROAD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 128705 | 115970 | 5006 | 1670 | 9.3742e-05 | 1.1619e-06 | 80.6833 | 1 | 320 | Customer | 73109 | Load | Tran1phPad | BRADLEY SUDBECK | 405-999-6850 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006554 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-01-17 14:48 | 2020-01-17 15:13 | 25.72 | 1 | 1 | 25.7167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 8300 NW 10TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 128705 | 115970 | 3405 | 2036 | 2.9879e-05 | 1.1619e-06 | 25.7167 | 1 | 310 | Customer | 70830 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006555 | PD-01172020-00320 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-17 14:48 | 2020-01-17 16:05 | 77.05 | 1 | 1 | 77.05 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MOUNTAINBURG | % ROUTE 2 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 82178 | 61159 | 3788 | 2584 | 8.9521e-05 | 1.1619e-06 | 77.05 | 1 | 310 | Customer | 8910 | Load | Tran1phOH | KRIS L HALMES | 479-430-9447 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-17 | 2020 |  | Ark - Series 2
J2001.006562 | PD-01172020-00326 | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3422 | 843422 | 2020-01-17 15:02 | 2020-01-17 15:45 | 42.73 | 1 | 1 | 42.7333 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | OKLAHOMA CITY | 6700 N MARTIN LUTHER KING AV | CMI_NORMAL | NO | NO | NO | 860693 | 168094 | 148284 | 1224 | 726 | 4.965e-05 | 1.1619e-06 | 42.7333 | 1 | 320 | Load | 85348 | Load | Tran3phPadWye | JERRY CASNER | 405-620-0772 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | #N/A
J2001.006564 | PD-01172020-00330 | METRO EAST | SHAWNEE | 7407:REMINGTON | REMINGTON 21 | 740721 | 2020-01-17 15:13 | 2020-01-17 16:36 | 83.27 | 1 | 2 | 71.5833 | 12 | POOR CONNECTION | 50 | CONNECTOR | SHAWNEE | 1101 N.DRAPER | CMI_NORMAL | NO | NO | NO | 860693 | 114361 | 22098 | 3665 | 2020 | 8.3169e-05 | 1.1619e-06 | 71.5833 | 1 | 320 | Customer | 6408 | Load | Tran1phOH | ADAM CLARK | 580-310-8924 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | OK - 2021
J2001.006567 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7022 | 817022 | 2020-01-17 15:15 | 2020-01-17 15:29 | 14.43 | 1 | 1 | 14.4333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MOORE | 2612 NOTTINGHAM WY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 159043 | 102116 | 9938 | 2104 | 1.6769e-05 | 1.1619e-06 | 14.4333 | 1 | 310 | Customer | 48485 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006568 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_863 | 830863 | 2020-01-17 15:21 | 2020-01-17 15:32 | 10.72 | 1 | 1 | 10.7167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1/2 M.N.OF MEMORIAL ON PENN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 168094 | 148284 | 19362 | 1672 | 1.2451e-05 | 1.1619e-06 | 10.7167 | 1 | 310 | Customer | 69430 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006575 | PD-01172020-00357 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1524 | 811524 | 2020-01-17 15:49 | 2020-01-17 17:09 | 80.22 | 1 | 1 | 4.15 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1032 SW.32 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 159043 | 102116 | 6059 | 2072 | 4.8217e-06 | 1.1619e-06 | 4.15 | 1 | 320 | Customer | 17761 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006577 | PD-01172020-00368 | METRO NORTH | NORTH | 8209:CLASSEN | CLASSEN_923 | 820923 | 2020-01-17 16:00 | 2020-01-17 17:29 | 88.55 | 2 | 3 | 109.8167 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 1608 NW.16 | CMI_NORMAL | NO | NO | NO | 860693 | 168094 | 148284 | 3881 | 1146 | 0.00012759 | 2.3237e-06 | 54.9083 | 1 | 310 | Secondary | 27318 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006576 |  | NORTHWEST | ENID | 4112:CHESTNUT | CHESTNUT_1221 | 411221 | 2020-01-17 16:02 | 2020-01-17 16:17 | 14.58 | 1 | 1 | 14.5833 | 1 | CANCELLED | 57 | CANCELLED | ENID | 1302 N 16TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 53513 | 37577 | 2858 | 1112 | 1.6944e-05 | 1.1619e-06 | 14.5833 | 1 | 310 | Customer | 7552 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | #N/A
J2001.006582 |  | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2627 | 862627 | 2020-01-17 16:31 | 2020-01-17 16:42 | 11.63 | 1 | 1 | 11.6333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DEL CITY | 3325 LAZY LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 159043 | 102116 | 7415 | 2000 | 1.3516e-05 | 1.1619e-06 | 11.6333 | 1 | 310 | Customer | 52286 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006584 |  | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_863 | 550863 | 2020-01-17 16:41 | 2020-01-17 16:55 | 14.25 | 1 | 1 | 14.25 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MEAD | JAMES TRLR PARK W OF DURANT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 77586 | 15483 | 1103 | 622 | 1.6556e-05 | 1.1619e-06 | 14.25 | 1 | 310 | Customer | 13264 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006585 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2222 | 852222 | 2020-01-17 16:42 | 2020-01-17 16:56 | 13.87 | 1 | 1 | 13.8667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | HARRAH | 201 NAVARRE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 114361 | 71205 | 11626 | 2211 | 1.6111e-05 | 1.1619e-06 | 13.8667 | 1 | 310 | Customer | 9279 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006587 | PD-01172020-00384 | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1373 | 831373 | 2020-01-17 16:52 | 2020-01-17 20:32 | 220.2 | 1 | 2 | 192.5667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 11444 NW 130th St | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860693 | 128705 | 115970 | 7890 | 4111 | 0.00022373 | 1.1619e-06 | 192.5667 | 1 | 320 | Customer | 365859 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006588 |  | NORTHEAST | MUSKOGEE | 3117:THREE RIVERS | THREE_RIVERS_1721 | 311721 | 2020-01-17 16:54 | 2020-01-17 17:02 | 8.28 | 1 | 1 | 8.2833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 2130 DAYTON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 73992 | 33245 | 2833 | 1047 | 9.624e-06 | 1.1619e-06 | 8.2833 | 1 | 310 | Customer | 3998 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-17 | 2020 |  | #N/A
J2001.006590 | PD-01172020-00386 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2031 | 862031 | 2020-01-17 16:55 | 2020-01-17 18:36 | 101.03 | 1 | 1 | 86.6333 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 322 SE.19 | CMI_NORMAL | NO | NO | NO | 860693 | 159043 | 102116 | 4743 | 1440 | 0.00010066 | 1.1619e-06 | 86.6333 | 1 | 310 | Customer | 3692 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2021
J2001.006591 | PD-01172020-00387 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_864 | 830864 | 2020-01-17 17:02 | 2020-01-17 18:07 | 64.6 | 1 | 1 | 58.1 | 15 | SQUIRREL | 44 | METER - PRIMARY | EDMOND | 237TH AND N MACARTHUR | CMI_NORMAL | NO | NO | NO | 860693 | 168094 | 148284 | 19362 | 2752 | 6.7504e-05 | 1.1619e-06 | 58.1 | 1 | 310 | Load | 341845 | Load | 0 | ADAM COX | 405-328-8938 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2021
J2001.006595 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7022 | 817022 | 2020-01-17 17:16 | 2020-01-17 17:33 | 16.43 | 1 | 1 | 16.4333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MOORE | 2436 NOTTINGHAM WY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 159043 | 102116 | 9938 | 2104 | 1.9093e-05 | 1.1619e-06 | 16.4333 | 1 | 310 | Customer | 5493 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006596 | PD-01172020-00390 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_863 | 830863 | 2020-01-17 17:20 | 2020-01-17 18:41 | 80.88 | 1 | 1 | 52.1637 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1/2 M.N.OF MEMORIAL ON PENN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 168094 | 148284 | 19362 | 1672 | 6.0607e-05 | 1.1619e-06 | 52.1637 | 1 | 310 | Customer | 69430 | Load | Tran1phPad | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006599 |  | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8124 | 838124 | 2020-01-17 17:25 | 2020-01-17 17:34 | 8.62 | 1 | 1 | 8.6167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | PRARIE SPRINGS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 128705 | 115970 | 8955 | 1638 | 1.0011e-05 | 1.1619e-06 | 8.6167 | 1 | 310 | Customer | 88045 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006602 | PD-01172020-00392 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1926 | 851926 | 2020-01-17 17:34 | 2020-01-17 18:46 | 71.52 | 5 | 5 | 34.5 | 4 | DETERIORATION | 50 | CONNECTOR | MIDWEST CITY | 612 JUNIPER AV | CMI_NORMAL | NO | NO | NO | 860693 | 114361 | 71205 | 12440 | 2125 | 4.0084e-05 | 5.8093e-06 | 6.9 | 1 | 310 | Secondary | 20852 | Load | Tran1phOH | STEVEN CASKEY | 405-777-8855 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2021
J2001.006604 | PD-01172020-00395 | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_622 | 410622 | 2020-01-17 17:38 | 2020-01-17 18:38 | 60.5 | 1 | 1 | 60.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ENID | 563 N.9TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 53513 | 37577 | 6012 | 1502 | 7.0292e-05 | 1.1619e-06 | 60.5 | 1 | 310 | Customer | 379 | Load | Tran1phOH | WILLIAM R PETHICK | 580-278-8129 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | #N/A
J2001.006607 |  | NORTHEAST | SAPULPA | 3216:BEELINE | BEELINE_1629 | 321629 | 2020-01-17 17:50 | 2020-01-17 18:17 | 26.55 | 1 | 1 | 26.55 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | GLENPOOL | 810 W 137PL GLEN-PINES M/H PK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 73992 | 40747 | 5564 | 1251 | 3.0847e-05 | 1.1619e-06 | 26.55 | 1 | 310 | Customer | 43160 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006609 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_621 | 460621 | 2020-01-17 17:51 | 2020-01-17 18:12 | 21 | 1 | 1 | 21 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | WOODWARD | 1608 6th st | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 53513 | 10418 | 5680 | 787 | 2.4399e-05 | 1.1619e-06 | 21 | 1 | 310 | Customer | 11358 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | #N/A
J2001.006610 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7022 | 817022 | 2020-01-17 17:54 | 2020-01-17 18:01 | 6.87 | 1 | 1 | 6.8667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MOORE | 2436 NOTTINGHAM WY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 159043 | 102116 | 9938 | 2104 | 7.9781e-06 | 1.1619e-06 | 6.8667 | 1 | 310 | Customer | 5493 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006613 |  | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5023 | 865023 | 2020-01-17 17:58 | 2020-01-17 18:08 | 10.08 | 1 | 1 | 10.0833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 2827 DEBBIE LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 114361 | 71205 | 8623 | 1267 | 1.1715e-05 | 1.1619e-06 | 10.0833 | 1 | 310 | Customer | 29517 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006615 | PD-01172020-00400 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7022 | 817022 | 2020-01-17 18:05 | 2020-01-17 20:14 | 129.13 | 2 | 2 | 258.2667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MOORE | 2436 NOTTINGHAM WY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 159052 | 102121 | 9938 | 2104 | 0.00030007 | 2.3237e-06 | 129.1333 | 1 | 310 | Secondary | 5493 | Load | Tran1phOH | THOMAS E COLE | 405-623-9338 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006618 | PD-01172020-00398 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7022 | 817022 | 2020-01-17 18:09 | 2020-01-17 19:53 | 104.1 | 1 | 1 | 74.5 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MOORE | 2812 NOTTINGHAM WY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 159052 | 102121 | 9938 | 2104 | 8.6558e-05 | 1.1619e-06 | 74.5 | 1 | 310 | Customer | 22465 | Load | Tran1phOH | THOMAS E COLE | 405-623-9338 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006620 | PD-01172020-00401 | METRO WEST | WEST | 8323:RICHARDS | RICHARDS_2323 | 832323 | 2020-01-17 18:13 | 2020-01-18 00:11 | 358.4 | 1 | 1 | 27.8167 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | ROCKWELL/HEFNER .5W SS | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860693 | 128730 | 115984 | 5005 | 1670 | 3.2319e-05 | 1.1619e-06 | 27.8167 | 1 | 320 | Customer | 65969 | Load | Tran1phOH | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006621 |  | SOUTHERN | PAULS VALLEY | 5619:RUSH CREEK | RUSH_CREEK_1922 | 561922 | 2020-01-17 18:15 | 2020-01-17 18:29 | 13.52 | 1 | 1 | 13.5167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | PAULS VALLEY | #8 WS CHAPPEL RDG APT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 77588 | 6206 | 2072 | 1192 | 1.5704e-05 | 1.1619e-06 | 13.5167 | 1 | 310 | Customer | 141957 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | OK - 2021
J2001.006630 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9921 | 829921 | 2020-01-17 18:31 | 2020-01-17 19:51 | 79.97 | 13 | 3 | 743.8167 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | ALLAN LN. + NW.16TH | CMI_PLANNED | YES | NO | NO | 860693 | 128730 | 115984 | 9223 | 1635 | 0.00086421 | 1.5104e-05 | 57.2167 | 1 | 308 | Tap | 7609 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006626 | PD-01172020-00406 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2129 | 822129 | 2020-01-17 18:35 | 2020-01-17 20:03 | 87.93 | 2 | 3 | 32.872 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 4144 NW.23 | CMI_NORMAL | NO | NO | NO | 860693 | 168109 | 148298 | 9243 | 1558 | 3.8192e-05 | 2.3237e-06 | 16.436 | 1 | 310 | Secondary | 111 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2020
J2001.006629 | PD-01172020-00405 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1524 | 811524 | 2020-01-17 18:41 | 2020-01-17 22:56 | 255.27 | 1 | 2 | 223.1167 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 1032 SW.32 | CMI_NORMAL | NO | NO | NO | 860693 | 159052 | 102121 | 6061 | 2073 | 0.00025923 | 1.1619e-06 | 223.1167 | 1 | 320 | Customer | 17761 | Load | Tran1phOH | THOMAS E COLE | 405-623-9338 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006631 | PD-01172020-00410 | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1424 | 911424 | 2020-01-17 18:54 | 2020-01-17 19:51 | 56.65 | 1 | 1 | 22.4701 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | FORT SMITH | 4921 MIDLAND BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 82183 | 61162 | 4737 | 255 | 2.6107e-05 | 1.1619e-06 | 22.4701 | 1 | 310 | Customer | 7643 | Load | TranOpenDelta | MARK A. SAWYER | 479-462-4457 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-17 | 2020 |  | Ark - Series 1
J2001.006638 |  | METRO WEST | WEST | 8158:SARA | SARA_5871 | 815871 | 2020-01-17 19:19 | 2020-01-17 19:25 | 6.35 | 1 | 1 | 6.35 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | ABERDEEN DR + 900 W/CARDIFF PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 128730 | 115984 | 18234 | 5388 | 7.3778e-06 | 1.1619e-06 | 6.35 | 1 | 310 | Customer | 88368 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006637 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1023 | 541023 | 2020-01-17 19:19 | 2020-01-17 20:01 | 41.42 | 1 | 1 | 41.4167 | 1 | CANCELLED | 57 | CANCELLED | MADILL | 111 S.8 ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 77588 | 7201 | 2378 | 842 | 4.812e-05 | 1.1619e-06 | 41.4167 | 1 | 310 | Customer | 12259 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006647 | PD-01172020-00416 | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_624 | 550624 | 2020-01-17 19:36 | 2020-01-18 09:12 | 816.4 | 8 | 7 | 6697.4667 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | DURANT | WESTWOOD CONDOMINIUM | CMI_NORMAL | NO | NO | NO | 860693 | 77588 | 15483 | 6737 | 1155 | 0.0077815 | 9.2948e-06 | 837.1833 | 1 | 310 | Load | 21017 | Load | Tran1phPad | SOUTH SCHEDULAR | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006644 |  | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_624 | 550624 | 2020-01-17 19:36 | 2020-01-17 19:36 | 0 | 1155 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | DURANT | 1400 BRYAN DR | CMI_MOMENTARY | YES | NO | NO | 860693 | 77588 | 15483 | 6737 | 1155 | 0 | 0.0013419 | 0 | 1 | 0 | Feeder | BODLE ST_624 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006648 | PD-01172020-00417 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4821 | 824821 | 2020-01-17 19:43 | 2020-01-17 22:06 | 142.68 | 1 | 1 | 142.6833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2109 W. SHERIDAN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 168109 | 148298 | 4192 | 242 | 0.00016578 | 1.1619e-06 | 142.6833 | 1 | 310 | Customer | 1037 | Load | TranOpenDelta | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006653 | PD-01172020-00419 | METRO NORTH | GUTHRIE | 8807:CRESCENT | CRESCENT_721 | 880721 | 2020-01-17 19:51 | 2020-01-17 22:30 | 158.82 | 8 | 7 | 1222.1333 | 22 | WIND | 17 | JUMPER | CRESCENT | N HARMON TRAILER CT | CMI_NORMAL | NO | NO | NO | 860693 | 168109 | 19811 | 1764 | 872 | 0.0014199 | 9.2948e-06 | 152.7667 | 1 | 310 | Load | 37565 | Load | Tran1phOH | JOSEPH WAYNE POOL | 405-919-2253 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006659 |  | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_523 | 890523 | 2020-01-17 20:19 | 2020-01-17 20:28 | 8.97 | 1 | 1 | 8.9667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | EL RENO | 702 S.FOSTER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 128730 | 12746 | 6937 | 1252 | 1.0418e-05 | 1.1619e-06 | 8.9667 | 1 | 310 | Customer | 41686 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006660 | PD-01172020-00420 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6523 | 836523 | 2020-01-17 20:20 | 2020-01-17 21:24 | 64.33 | 1 | 1 | 64.3333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7305 LYREWOOD LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 128730 | 115984 | 7420 | 2257 | 7.4746e-05 | 1.1619e-06 | 64.3333 | 1 | 310 | Customer | 38608 | Load | Tran1phPad | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006661 |  | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3023 | 743023 | 2020-01-17 20:30 | 2020-01-17 20:55 | 25.35 | 20 | 8 | 475.6667 | 4 | DETERIORATION | 28 | CROSSARM | SHAWNEE | COR OF LEO+CLRPOND WSD | CMI_PLANNED | YES | NO | NO | 860693 | 114373 | 22099 | 6641 | 1137 | 0.00055266 | 2.3237e-05 | 23.7833 | 1 | 310 | Mainline | 958 | Fuse | FuseOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2021
J2001.006667 | PD-01172020-00428 | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3722 | 913722 | 2020-01-17 20:38 | 2020-01-17 22:42 | 123.68 | 106 | 99 | 13108.6667 | 5 | ELECTRICAL TRACKING | 18 | INSULATOR | FORT SMITH | BURNHAM RD. AT DUNCAN | CMI_NORMAL | NO | NO | NO | 860693 | 82183 | 61162 | 4565 | 1438 | 0.01523 | 0.00012316 | 123.6667 | 1 | 310 | Mainline | 5751 | Fuse | FuseOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | Ark - Series 3
J2001.006679 |  | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3731 | 833731 | 2020-01-17 20:47 | 2020-01-17 20:55 | 8.13 | 1 | 1 | 8.1333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | THE VILLAGE | 1611 BRIGHTON AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 168109 | 148298 | 5759 | 1902 | 9.4498e-06 | 1.1619e-06 | 8.1333 | 1 | 310 | Customer | 8425 | Load | TranOHDeltaSplitBank | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2020
J2001.006678 |  | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3722 | 913722 | 2020-01-17 20:48 | 2020-01-17 22:49 | 120.95 | 1 | 1 | 114.1333 | 5 | ELECTRICAL TRACKING | 18 | INSULATOR | FORT SMITH | 1601 BURNHAM RD + DUNCAN | CMI_NORMAL | NO | NO | NO | 860693 | 82183 | 61162 | 4565 | 1438 | 0.00013261 | 1.1619e-06 | 114.1333 | 1 | 310 | Customer | 3121 | Load | Tran1phOH | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | Ark - Series 3
J2001.006681 | PD-01172020-00425 | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2163 | 892163 | 2020-01-17 20:52 | 2020-01-17 23:56 | 183.7 | 1 | 2 | 101.6167 | 4 | DETERIORATION | 50 | CONNECTOR | UNION CITY | 1/2MS SW.29-1/2ME BANNER RD. | CMI_NORMAL | NO | NO | NO | 860693 | 128730 | 12746 | 3185 | 1135 | 0.00011806 | 1.1619e-06 | 101.6167 | 1 | 310 | Load | 63409 | Load | Tran1phOH | GRADY LYLE NELSON | 405-401-8829 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2021
J2001.006686 |  | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1823 | 931823 | 2020-01-17 21:02 | 2020-01-17 21:29 | 26.95 | 1 | 2 | 18.5667 | 1 | CANCELLED | 57 | CANCELLED | ALMA | MAPLE SHADE RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 82183 | 61162 | 2835 | 1228 | 2.1572e-05 | 1.1619e-06 | 18.5667 | 1 | 310 | Customer | 13526 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | Ark - Series 2
J2001.006683 |  | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1823 | 931823 | 2020-01-17 21:02 | 2020-01-17 21:25 | 23.17 | 112 | 62 | 2079.4667 | 5 | ELECTRICAL TRACKING | 18 | INSULATOR | ALMA | MAPLE SHADE RD | CMI_NORMAL | NO | NO | NO | 860693 | 82183 | 61162 | 2835 | 1228 | 0.002416 | 0.00013013 | 18.5667 | 1 | 310 | Mainline | 1562 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | Ark - Series 2
J2001.006685 |  | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1823 | 931823 | 2020-01-17 21:08 | 2020-01-17 21:27 | 19.25 | 1 | 1 | 12.0833 | 5 | ELECTRICAL TRACKING | 18 | INSULATOR | ALMA | ELMHURST ST,KINGSWOOD ADD,ALMA | CMI_NORMAL | NO | NO | NO | 860693 | 82183 | 61162 | 2835 | 1228 | 1.4039e-05 | 1.1619e-06 | 12.0833 | 1 | 310 | Customer | 4533 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | Ark - Series 2
J2001.006687 | PD-01172020-00430 | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_424 | 580424 | 2020-01-17 21:10 | 2020-01-18 07:41 | 630.43 | 303 | 97 | 182946.6446 | 3 | DAMAGED BY PUBLIC | 12 | POLE | STONEWALL | AHLOSO Y/MV .8MSE WS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 77588 | 11508 | 3412 | 436 | 0.21256 | 0.00035204 | 603.7843 | 1 | 310 | Mainline | 306 | Fuse | FuseOH | CAMERON BRADY | 580-307-7052 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2021
J2001.006715 |  | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6523 | 836523 | 2020-01-17 22:08 | 2020-01-17 22:14 | 6 | 1 | 1 | 6 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7305 LYREWOOD LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 128730 | 115984 | 7420 | 2257 | 6.9711e-06 | 1.1619e-06 | 6 | 1 | 310 | Customer | 38608 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | OK - 2022
J2001.006718 | PD-01172020-00433 | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2224 | 882224 | 2020-01-17 22:26 | 2020-01-17 23:39 | 72.82 | 1 | 1 | 72.8167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | GUTHRIE | LOT 69 VALLEY VIEW ESTATES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 168109 | 19811 | 5386 | 1849 | 8.4602e-05 | 1.1619e-06 | 72.8167 | 1 | 320 | Customer | 68909 | Load | Tran1phPad | JOSEPH WAYNE POOL | 405-919-2253 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006723 | PD-01172020-00435 | METRO EAST | EAST | 8690:WILD MARY | WILD_MARY_9023 | 869023 | 2020-01-17 22:40 | 2020-01-18 04:16 | 336 | 1 | 1 | 322.4333 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | MOORE | LOT 18 BLOCK 2 | CMI_NORMAL | NO | NO | NO | 860693 | 114373 | 71211 | 4021 | 2247 | 0.00037462 | 1.1619e-06 | 322.4333 | 1 | 320 | Customer | 388483 | Load | Tran1phPad | BRENTON DOWNES | 580-450-0056 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006725 |  | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3722 | 913722 | 2020-01-17 22:49 | 2020-01-17 23:19 | 29.5 | 1 | 1 | 29.5 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 1318 BURNHAM BET DUNCAN+GORDON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 82183 | 61162 | 4565 | 1438 | 3.4275e-05 | 1.1619e-06 | 29.5 | 1 | 310 | Customer | 4597 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-17 | 2020 |  | Ark - Series 3
J2001.006735 | PD-01172020-00439 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4033 | 834033 | 2020-01-17 23:39 | 2020-01-18 01:17 | 98.05 | 1 | 1 | 93.0833 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | L30,B10-ROCKWELL,HEFNER | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860693 | 128730 | 115984 | 10841 | 1115 | 0.00010815 | 1.1619e-06 | 93.0833 | 1 | 310 | Customer | 80557 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-17 | 2020 |  | #N/A
J2001.006746 | PD-01182020-00001 | SOUTHERN | ADA | 5809:VANOSS | VANOSS_922 | 580922 | 2020-01-18 01:03 | 2020-01-18 02:11 | 68.23 | 1 | 1 | 68.2333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | STRATFORD | 430 E.STATE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 77588 | 11508 | 978 | 978 | 7.9277e-05 | 1.1619e-06 | 68.2333 | 1 | 320 | Customer | 5143 | Load | Tran1phOH | BRUCE E BEAM | 405-626-0490 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2021
J2001.006758 |  | METRO WEST | WEST | 8222:CZECH HALL | CZECH_HALL_2222 | 822222 | 2020-01-18 02:54 | 2020-01-18 03:11 | 17.27 | 1 | 1 | 17.2667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 11501 LOCHWOOD DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860693 | 128730 | 115984 | 8603 | 2027 | 2.0061e-05 | 1.1619e-06 | 17.2667 | 1 | 310 | Customer | 76447 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006766 |  | METRO WEST | WEST | 8222:CZECH HALL | CZECH_HALL_2222 | 822222 | 2020-01-18 03:39 | 2020-01-18 04:17 | 38.52 | 1 | 1 | 38.5167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 11501 LOCHWOOD DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 128730 | 115984 | 8603 | 2027 | 4.4752e-05 | 1.1619e-06 | 38.5167 | 1 | 310 | Customer | 76447 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006778 | PD-01182020-00007 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5024 | 865024 | 2020-01-18 06:26 | 2020-01-18 12:18 | 352.02 | 1 | 1 | 307.5833 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | MIDWEST CITY | 403 W.RICKENBACKER | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860678 | 114373 | 71211 | 8623 | 1072 | 0.00035737 | 1.1619e-06 | 307.5833 | 1 | 320 | Customer | 17086 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2022
J2001.006780 | PD-01182020-00009 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5132 | 815132 | 2020-01-18 06:34 | 2020-01-18 08:17 | 103.48 | 1 | 1 | 103.4833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2708 SW.79 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 159052 | 102121 | 13933 | 2003 | 0.00012023 | 1.1619e-06 | 103.4833 | 1 | 320 | Customer | 20913 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006784 | PD-01182020-00012 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1929 | 851929 | 2020-01-18 06:51 | 2020-01-18 09:39 | 167.95 | 1 | 1 | 29.7643 | 4 | DETERIORATION | 20 | FUSE BARREL | MIDWEST CITY | 3210 BELAIRE DR | CMI_NORMAL | NO | NO | NO | 860678 | 114373 | 71211 | 12441 | 828 | 3.4582e-05 | 1.1619e-06 | 29.7643 | 1 | 310 | Load | 29725 | Load | TranOpenDelta | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2022
J2001.006783 | PD-01182020-00011 | METRO EAST | EAST | 8690:WILD MARY | WILD_MARY_9023 | 869023 | 2020-01-18 06:51 | 2020-01-18 09:17 | 145.72 | 2 | 2 | 265.1833 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 2824 SE 90TH ST | CMI_NORMAL | NO | NO | NO | 860678 | 114373 | 71211 | 4021 | 2247 | 0.00030811 | 2.3237e-06 | 132.5917 | 1 | 310 | Secondary | 71773 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006787 | PD-01182020-00010 | SOUTHERN | HEALDTON | 5306:COUNTY LINE | COUNTY LINE 21 | 530621 | 2020-01-18 06:56 | 2020-01-18 09:05 | 128.93 | 1 | 2 | 96.05 | 5 | ELECTRICAL TRACKING | 21 | FUSE - TRANSFORMER | RATLIFF CITY | CONTINENTAL RD/KNOB HILL RD .1W .2S .1W | CMI_NORMAL | NO | NO | NO | 860678 | 77588 | 6795 | 755 | 342 | 0.0001116 | 1.1619e-06 | 96.05 | 1 | 310 | Load | 371128 | Load | Tran1phOH | JUSTIN B MARSHALL | 580-221-5051 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-18 | 2020 |  | #N/A
J2001.006790 |  | NORTHEAST | SAPULPA | 7605:DRUMRIGHT | DRUMRIGHT_541 | 760541 | 2020-01-18 07:19 | 2020-01-18 07:19 | 0 | 322 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | DRUMRIGHT | 200 N CENTER AVE | CMI_MOMENTARY | YES | NO | NO | 860678 | 73995 | 40746 | 1694 | 322 | 0 | 0.00037412 | 0 | 1 | 0 | Feeder | DRUMRGHT_541 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-18 | 2020 |  | #N/A
J2001.006792 | PD-01182020-00013 | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6223 | 866223 | 2020-01-18 07:31 | 2020-01-18 12:00 | 269.15 | 1 | 1 | 269.15 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 3ME DOU BL + MS 29 | CMI_NORMAL | NO | NO | NO | 860678 | 114373 | 71211 | 7208 | 2235 | 0.00031272 | 1.1619e-06 | 269.15 | 1 | 310 | Load | 45843 | Load | Tran1phOH | DAVID M CLEMMONS | 405-777-8355 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006793 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1862 | 941862 | 2020-01-18 07:35 | 2020-01-18 13:15 | 340.12 | 1 | 0 | 332.45 | 4 | DETERIORATION | 12 | POLE | LAMAR | LAMAR AR | CMI_PLANNED | YES | NO | NO | 860678 | 82183 | 7540 | 730 | 730 | 0.00038627 | 1.1619e-06 | 332.45 | 1 | 0 | Load | 773 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-18 | 2020 |  | Ark - Series 2
J2001.006805 | PD-01182020-00018 | METRO NORTH | NORTH | 8464:BRYANT | BRYANT_6421 | 846421 | 2020-01-18 08:14 | 2020-01-18 13:31 | 316.53 | 1 | 1 | 310.6167 | 4 | DETERIORATION | 17 | JUMPER | EDMOND | 5400 E.MEMORIAL RD | CMI_NORMAL | NO | NO | NO | 860678 | 168109 | 148298 | 1894 | 1265 | 0.0003609 | 1.1619e-06 | 310.6167 | 1 | 310 | Load | 32910 | Load | Tran1phOH | CURTIS W PINKERTON | 405-464-8500 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006806 | PD-01182020-00022 | SOUTHERN | DURANT | 5504:BUTTERFIELD | BUTTERFIELD_422 | 550422 | 2020-01-18 08:17 | 2020-01-18 12:23 | 246.48 | 1 | 1 | 246.4833 | 13 | PREMATURE FAILURE | 2 | TRANSFORMER OH | DURANT | AIRPORT ROAD | CMI_NORMAL | NO | NO | NO | 860678 | 77588 | 15483 | 3484 | 561 | 0.00028638 | 1.1619e-06 | 246.4833 | 1 | 320 | Load | 18073 | Load | Tran3phPadWye | MICHAEL N STROHL | 903-821-1619 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006807 | PD-01182020-00021 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-01-18 08:28 | 2020-01-18 12:39 | 251.42 | 2 | 6 | 182.7667 | 5 | ELECTRICAL TRACKING | 17 | JUMPER | OKLAHOMA CITY | 1915 NW.15 | CMI_NORMAL | NO | NO | NO | 860678 | 168109 | 148298 | 11100 | 2037 | 0.00021235 | 2.3237e-06 | 91.3833 | 1 | 310 | Secondary | 6744 | Load | Tran1phOH | CURTIS W PINKERTON | 405-464-8500 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2021
J2001.006809 | PD-01182020-00023 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4821 | 824821 | 2020-01-18 08:42 | 2020-01-18 09:15 | 33.38 | 1 | 1 | 33.3833 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 2109 W. SHERIDAN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 168109 | 148298 | 4192 | 242 | 3.8787e-05 | 1.1619e-06 | 33.3833 | 1 | 310 | Customer | 1037 | Load | TranOpenDelta | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2022
J2001.006810 | PD-01182020-00024 | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_622 | 770622 | 2020-01-18 08:44 | 2020-01-18 10:15 | 91.17 | 1 | 1 | 91.1667 | 4 | DETERIORATION | 21 | FUSE - TRANSFORMER | BRISTOW | 3/4 N OF 4M CNR ON 48 BRISTOW | CMI_NORMAL | NO | NO | NO | 860678 | 73995 | 40746 | 3781 | 2009 | 0.00010592 | 1.1619e-06 | 91.1667 | 1 | 310 | Customer | 19448 | Load | Tran1phOH | CGI ADMIN | 918-261-6802 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-18 | 2020 |  | #N/A
J2001.006816 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3831 | 913831 | 2020-01-18 09:02 | 2020-01-18 12:08 | 185.35 | 1 | 0 | 172.9833 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 520 RALEIGH | CMI_PLANNED | YES | NO | NO | 860678 | 82183 | 61162 | 2934 | 485 | 0.00020098 | 1.1619e-06 | 172.9833 | 1 | 0 | Tap | 2775 | Fuse | FuseRiser | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-18 | 2020 |  | Ark - Series 2
J2001.006817 |  | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5021 | 865021 | 2020-01-18 09:04 | 2020-01-18 10:51 | 106.85 | 20 | 15 | 1731.8333 | 3 | DAMAGED BY PUBLIC | 12 | POLE | MIDWEST CITY | 1212 SOUTH AIR DEPOT | CMI_PLANNED | YES | NO | NO | 860678 | 114373 | 71211 | 8623 | 1291 | 0.0020122 | 2.3237e-05 | 86.5917 | 1 | 308 | Tap | 18373 | Fuse | FuseOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006818 |  | SOUTHERN | SULPHUR | 5709:PRICES FALLS | PRICES_FALLS_923 | 570923 | 2020-01-18 09:05 | 2020-01-18 09:05 | 0 | 183 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | DAVIS | 5175 KAY STARR TRAIL | CMI_MOMENTARY | YES | NO | NO | 860678 | 77588 | 6811 | 373 | 183 | 0 | 0.00021262 | 0 | 1 | 0 | Feeder | PRIC FAL_923 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006819 | PD-01182020-00026 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5125 | 815125 | 2020-01-18 09:05 | 2020-01-18 09:57 | 52.35 | 99 | 70 | 5050.65 | 22 | WIND | 23 | FUSE - PRIMARY | OKLAHOMA CITY | SSW62 + MCKINLEY | CMI_NORMAL | NO | NO | NO | 860678 | 159052 | 102121 | 13933 | 1432 | 0.0058682 | 0.00011503 | 51.0167 | 1 | 310 | Mainline | 9457 | Fuse | FuseOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006821 | PD-01182020-00027 | METRO SOUTH | SOUTH | 8722:MILLENNIUM | MILLENNIUM_2224 | 872224 | 2020-01-18 09:07 | 2020-01-18 11:46 | 158.57 | 1 | 1 | 133.7833 | 22 | WIND | 21 | FUSE - TRANSFORMER | NORMAN | .2ME 12TH AVE NE ON TECUMSEH | CMI_NORMAL | NO | NO | NO | 860678 | 159052 | 56931 | 4205 | 639 | 0.00015544 | 1.1619e-06 | 133.7833 | 1 | 310 | Customer | 80840 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006834 |  | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_421 | 710421 | 2020-01-18 09:29 | 2020-01-18 09:38 | 8.67 | 1 | 1 | 8.6667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | CHANDLER | 212 W 5TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 114373 | 7462 | 2822 | 1173 | 1.007e-05 | 1.1619e-06 | 8.6667 | 1 | 310 | Customer | 2839 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2021
J2001.006836 | PD-01182020-00028 | SOUTHERN | SULPHUR | 5709:PRICES FALLS | PRICES_FALLS_923 | 570923 | 2020-01-18 09:34 | 2020-01-18 16:01 | 386.6 | 1 | 1 | 170.25 | 22 | WIND | 12 | POLE | DAVIS | FALLS CREEK WELCOME CENTER | CMI_NORMAL | NO | NO | NO | 860678 | 77588 | 6811 | 373 | 183 | 0.00019781 | 1.1619e-06 | 170.25 | 1 | 310 | Load | 372155 | Load | Tran3phPadWye | CHRIS CLOSE | 405-238-0419 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006839 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-01-18 09:37 | 2020-01-18 12:56 | 199.03 | 3 | 4 | 525.6 | 22 | WIND | 17 | JUMPER | OKLAHOMA CITY | 1915 NW.15 | CMI_NORMAL | NO | NO | NO | 860678 | 168109 | 148298 | 11100 | 2037 | 0.00061068 | 3.4856e-06 | 175.2 | 1 | 310 | Secondary | 6744 | Load | Tran1phOH | [7 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2021
J2001.006841 | PD-01182020-00030 | METRO EAST | EAST | 8416:DUNJEE | DUNJEE_1623 | 841623 | 2020-01-18 09:40 | 2020-01-18 13:24 | 223.93 | 1 | 2 | 221.6167 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 5412 LENOX AV | CMI_NORMAL | NO | NO | NO | 860678 | 114373 | 71211 | 3540 | 1988 | 0.00025749 | 1.1619e-06 | 221.6167 | 1 | 310 | Load | 51335 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006842 | PD-01182020-00033 | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1022 | 541022 | 2020-01-18 09:47 | 2020-01-18 12:55 | 187.65 | 68 | 26 | 4837.6333 | 5 | ELECTRICAL TRACKING | 28 | CROSSARM | MADILL | 400 S OF GRLDINE + 2ND | CMI_NORMAL | NO | NO | NO | 860678 | 77588 | 7201 | 2378 | 873 | 0.0056207 | 7.9007e-05 | 71.1417 | 1 | 310 | Mainline | 604 | Switch | SwitchOH | DAVID TAYLOR | 580-574-4517 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006843 | PD-01182020-00031 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5136 | 815136 | 2020-01-18 09:49 | 2020-01-18 10:21 | 32.18 | 1 | 1 | 32.1833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2501 SW.82 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 159052 | 102121 | 13933 | 1299 | 3.7393e-05 | 1.1619e-06 | 32.1833 | 1 | 310 | Customer | 33942 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2021
J2001.006854 | PD-01182020-00037 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6324 | 816324 | 2020-01-18 09:51 | 2020-01-18 14:02 | 251.3 | 6 | 7 | 1489.35 | 22 | WIND | 34 | CONDUCTOR SECONDARY - OH | MOORE | 829 NW.7 | CMI_NORMAL | NO | NO | NO | 860678 | 159052 | 102121 | 11824 | 2048 | 0.0017304 | 6.9712e-06 | 248.225 | 1 | 310 | Secondary | 52244 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2021
J2001.006848 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7429 | 847429 | 2020-01-18 09:57 | 2020-01-18 10:04 | 7.05 | 1 | 1 | 7.05 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2316 NE.21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 168109 | 148298 | 6155 | 680 | 8.1912e-06 | 1.1619e-06 | 7.05 | 1 | 310 | Customer | 40681 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2022
J2001.006850 |  | METRO EAST | EAST | 8685:TINKER FIELD 4 | TINKER_4_8531 | 868531 | 2020-01-18 09:59 | 2020-01-18 21:28 | 689.18 | 2 | 0 | 1378.3723 | 5 | ELECTRICAL TRACKING | 3 | SWITCHING CUBICLE | OKLAHOMA CITY | West side of bldg 255 | CMI_PLANNED | YES | NO | NO | 860678 | 114373 | 71211 | 7 | 2 | 0.0016015 | 2.3237e-06 | 689.1861 | 1 | 0 | Tap | 344884 | Fuse | SwitchCubicleFuse | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006851 | PD-01182020-00045 | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1821 | 931821 | 2020-01-18 10:00 | 2020-01-18 11:07 | 67.02 | 1 | 1 | 67.0167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ALMA | 5 POLE S-LONDON + 345 W-HENRY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 82183 | 61162 | 2835 | 821 | 7.7865e-05 | 1.1619e-06 | 67.0167 | 1 | 310 | Load | 3832 | Load | Tran1phOH | KRIS L HALMES | 479-430-9447 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-18 | 2020 |  | Ark - Series 2
J2001.006855 | PD-01182020-00040 | NORTHEAST | SAPULPA | 3214:LONE STAR | LONE_STAR_1422 | 321422 | 2020-01-18 10:09 | 2020-01-18 11:14 | 64.97 | 2 | 2 | 121.1 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 21 | FUSE - TRANSFORMER | SAPULPA | 1/4W 81-W AV + 151ST 3 SPANS S | CMI_NORMAL | NO | NO | NO | 860678 | 73995 | 40746 | 2656 | 1096 | 0.0001407 | 2.3237e-06 | 60.55 | 1 | 310 | Load | 44190 | Load | Tran1phOH | CGI ADMIN | 918-261-6802 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2020
J2001.006856 | PD-01182020-00038 | METRO EAST | SHAWNEE | 7407:REMINGTON | REMINGTON 22 | 740722 | 2020-01-18 10:10 | 2020-01-18 15:18 | 307.93 | 1 | 1 | 307.9333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SHAWNEE | 1506 N.HARRISON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 114373 | 22099 | 3665 | 1645 | 0.00035778 | 1.1619e-06 | 307.9333 | 1 | 310 | Customer | 3477 | Load | TranOpenDelta | STEVEN CASKEY | 405-777-8855 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-18 | 2020 |  | #N/A
J2001.006857 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-18 10:13 | 2020-01-18 16:56 | 403.42 | 2 | 1 | 560.6 | 4 | DETERIORATION | 12 | POLE | ARKOMA | N OF BOONE ON ST-LINE | CMI_PLANNED | YES | NO | NO | 860678 | 82183 | 61162 | 2934 | 875 | 0.00065135 | 2.3237e-06 | 280.3 | 1 | 308 | Tap | 7348 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-18 | 2020 |  | Ark - Series 2
J2001.006860 | PD-01182020-00039 | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5822 | 845822 | 2020-01-18 10:15 | 2020-01-18 11:48 | 92.72 | 1 | 2 | 85.9 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | SPENCER | 9108 NE.45 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860678 | 114373 | 71211 | 2986 | 934 | 9.9805e-05 | 1.1619e-06 | 85.9 | 1 | 310 | Customer | 24541 | Load | Tran1phOH | STEVEN CASKEY | 405-777-8855 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-18 | 2020 |  | #N/A
J2001.006861 | PD-01182020-00042 | NORTHWEST | ENID | 4219:BUNCH CREEK | BUNCH CREEK 41 | 421941 | 2020-01-18 10:18 | 2020-01-18 11:35 | 77.28 | 1 | 1 | 77.2833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | GARBER | 7MN,ME,1/2MS-- GARBER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 53518 | 37579 | 910 | 910 | 8.9794e-05 | 1.1619e-06 | 77.2833 | 1 | 310 | Load | 382716 | Load | Tran1phOH | WILLIAM R PETHICK | 580-278-8129 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006863 | PD-01182020-00041 | METRO EAST | SHAWNEE | 7433:ROCK CREEK | ROCK_CREEK_3322 | 743322 | 2020-01-18 10:26 | 2020-01-18 17:59 | 453.35 | 3 | 3 | 1331.9 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | SHAWNEE | 1810 N.HARRISON | CMI_NORMAL | NO | NO | NO | 860678 | 114373 | 22099 | 1799 | 1032 | 0.0015475 | 3.4856e-06 | 443.9667 | 1 | 310 | Secondary | 12622 | Load | Tran1phPad | DAVID M CLEMMONS | 405-777-8355 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006865 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-18 10:28 | 2020-01-18 12:24 | 115.85 | 1 | 0 | 115.8438 | 4 | DETERIORATION | 12 | POLE | 0 | 2M E. HARTMAN - 1/2M S HWY 194 | CMI_PLANNED | YES | NO | NO | 860678 | 82183 | 7540 | 1504 | 1200 | 0.0001346 | 1.1619e-06 | 115.8438 | 1 | 0 | Load | 15132 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-18 | 2020 |  | Ark - Series 2
J2001.006868 | PD-01182020-00044 | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-18 10:28 | 2020-01-18 15:25 | 296.75 | 45 | 64 | 11248.5 | 22 | WIND | 17 | JUMPER | MUSTANG | 1/2 MN SW74+1/8MW MUST | CMI_NORMAL | NO | NO | NO | 860678 | 128730 | 115984 | 18234 | 4429 | 0.013069 | 5.2284e-05 | 249.9667 | 1 | 310 | Mainline | 23598 | Fuse | FuseRiser | HOWARD GETCHELL | 530-410-8920 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2022
J2001.006870 |  | METRO WEST | WEST | 8158:SARA | SARA_5864 | 815864 | 2020-01-18 10:28 | 2020-01-18 16:04 | 336.05 | 1 | 2 | 249.9667 | 22 | WIND | 17 | JUMPER | MUSTANG | 452 W MAPLE BRANCH WAY | CMI_NORMAL | NO | NO | NO | 860678 | 128730 | 115984 | 18234 | 4810 | 0.00029043 | 1.1619e-06 | 249.9667 | 1 | 310 | Customer | 65364 | Load | Tran1phPad | [7 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2022
J2001.006874 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_823 | 870823 | 2020-01-18 10:43 | 2020-01-18 10:59 | 16.67 | 1 | 1 | 16.6667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 2825 S.DEWEY AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 159052 | 56931 | 6777 | 2379 | 1.9365e-05 | 1.1619e-06 | 16.6667 | 1 | 310 | Customer | 17090 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006876 | PD-01182020-00047 | SOUTHERN | HEALDTON | 5306:COUNTY LINE | COUNTY LINE 22 | 530622 | 2020-01-18 10:51 | 2020-01-18 12:20 | 88.9 | 1 | 2 | 86.2333 | 4 | DETERIORATION | 50 | CONNECTOR | TATUMS | T.M. .1SW 1BLK N ES | CMI_NORMAL | NO | NO | NO | 860678 | 77588 | 6795 | 755 | 413 | 0.00010019 | 1.1619e-06 | 86.2333 | 1 | 310 | Customer | 667 | Load | Tran1phOH | JUSTIN B MARSHALL | 580-221-5051 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-18 | 2020 |  | #N/A
J2001.006883 | PD-01182020-00049 | METRO EAST | SHAWNEE | 7435:MISSION HILL | MISSION HILL 24 | 743524 | 2020-01-18 10:58 | 2020-01-18 13:33 | 155.47 | 24 | 18 | 3405.2 | 4 | DETERIORATION | 28 | CROSSARM | TECUMSEH | ROSE DR + SHARON RD | CMI_NORMAL | NO | NO | NO | 860678 | 114373 | 22099 | 948 | 948 | 0.0039564 | 2.7885e-05 | 141.8833 | 1 | 310 | Mainline | 100078 | Recloser | Rec1phHydralic | STEVEN CASKEY | 405-777-8855 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-18 | 2020 |  | OK - 2021
J2001.006887 |  | METRO EAST | EAST | 8685:TINKER FIELD 4 | TINKER_4_8531 | 868531 | 2020-01-18 11:09 | 2020-01-18 21:26 | 617.5 | 3 | 0 | 691.506 | 5 | ELECTRICAL TRACKING | 3 | SWITCHING CUBICLE | 0 | 0 | CMI_NORMAL | NO | NO | NO | 860678 | 114373 | 71211 | 7 | 2 | 0.00080344 | 3.4856e-06 | 230.502 | 1 | 0 | Mainline | 868531 | Switch | 0 | [7 empty] | Equipment | N | SUBSTATION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006892 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1022 | 541022 | 2020-01-18 11:24 | 2020-01-18 12:57 | 93.18 | 1 | 1 | 79.5167 | 5 | ELECTRICAL TRACKING | 28 | CROSSARM | MADILL | SO 5TH MADILL | CMI_NORMAL | NO | NO | NO | 860678 | 77588 | 7201 | 2378 | 873 | 9.2388e-05 | 1.1619e-06 | 79.5167 | 1 | 310 | Customer | 10768 | Load | Tran1phOH | DAVID TAYLOR | 580-574-4517 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006899 | PD-01182020-00053 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7022 | 817022 | 2020-01-18 11:48 | 2020-01-18 13:01 | 73.07 | 1 | 2 | 32.3 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | MOORE | 737 CAMELOT DR | CMI_NORMAL | NO | NO | NO | 860678 | 159052 | 102121 | 9938 | 2104 | 3.7529e-05 | 1.1619e-06 | 32.3 | 1 | 310 | Customer | 7286 | Load | Tran1phOH | GERARDO D SOTO | 405-758-6334 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006906 | PD-01182020-00057 | NORTHEAST | MUSKOGEE | 3312:CHECOTAH | CHECOTAH 22 | 331222 | 2020-01-18 11:59 | 2020-01-18 14:27 | 147.63 | 1 | 2 | 139.2667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | TEXANNA | RIO HONDO INC 9 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860678 | 73995 | 33249 | 2886 | 1530 | 0.00016181 | 1.1619e-06 | 139.2667 | 1 | 320 | Customer | 15118 | Load | Tran1phPad | CONTRACTOR 5 DAVID ELLIOT INC | 918-639-5055 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-18 | 2020 |  | OK - 2020
J2001.006910 |  | SOUTHERN | SULPHUR | 5709:PRICES FALLS | PRICES_FALLS_923 | 570923 | 2020-01-18 12:25 | 2020-01-18 12:25 | 0 | 182 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | DAVIS | 5175 KAY STARR TRAIL | CMI_MOMENTARY | YES | NO | NO | 860678 | 77588 | 6811 | 373 | 183 | 0 | 0.00021146 | 0 | 1 | 0 | Feeder | PRIC FAL_923 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006921 |  | METRO EAST | EAST | 8542:RENO | RENO_4224 | 854224 | 2020-01-18 12:56 | 2020-01-18 13:02 | 5.43 | 1 | 1 | 5.4333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 733 GREENWOOD DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 114373 | 71211 | 5214 | 1221 | 6.3129e-06 | 1.1619e-06 | 5.4333 | 1 | 310 | Customer | 25332 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2022
J2001.006923 | PD-01182020-00063 | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1721 | 861721 | 2020-01-18 13:05 | 2020-01-18 17:05 | 240.15 | 1 | 2 | 29.6333 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | DEL CITY | 4113 MONICA DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860678 | 114373 | 71211 | 6940 | 1505 | 3.443e-05 | 1.1619e-06 | 29.6333 | 1 | 310 | Customer | 46666 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-18 | 2020 |  | #N/A
J2001.006924 |  | SOUTHERN | SULPHUR | 5709:PRICES FALLS | PRICES_FALLS_923 | 570923 | 2020-01-18 13:07 | 2020-01-18 15:21 | 134.4 | 1 | 1 | 129.6167 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | DAVIS | FALLS CREEK-PONCA CITY 1ST | CMI_NORMAL | NO | NO | NO | 860678 | 77588 | 6811 | 373 | 183 | 0.0001506 | 1.1619e-06 | 129.6167 | 1 | 310 | Customer | 14356 | Load | TranOpenDelta | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006926 | PD-01182020-00064 | SOUTHERN | SULPHUR | 5706:LAKE ARBUCKLE | LAKE ARBUCKLE 46 | 570646 | 2020-01-18 13:14 | 2020-01-18 14:23 | 69.12 | 1 | 1 | 69.1167 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | DOUGHERTY | HWY 110 & KSTAR 1.5S ES | CMI_NORMAL | NO | NO | NO | 860678 | 77588 | 6811 | 366 | 239 | 8.0305e-05 | 1.1619e-06 | 69.1167 | 1 | 310 | Customer | 243265 | Load | Tran1phPad | [7 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-18 | 2020 |  | #N/A
J2001.006929 | PD-01182020-00065 | METRO SOUTH | SOUTH CENTRAL | 8194:WESTMOORE | WESTMOORE_9429 | 819429 | 2020-01-18 13:27 | 2020-01-18 14:47 | 80.03 | 1 | 1 | 80.0333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 12601 SMITHFIELD LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 159052 | 102121 | 8099 | 1132 | 9.2989e-05 | 1.1619e-06 | 80.0333 | 1 | 310 | Customer | 257847 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006931 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3831 | 913831 | 2020-01-18 13:51 | 2020-01-18 15:56 | 125.13 | 1 | 1 | 73.55 | 5 | ELECTRICAL TRACKING | 2 | TRANSFORMER OH | FORT SMITH | 3005 S.5 | CMI_PLANNED | YES | NO | NO | 860678 | 82183 | 61162 | 2934 | 485 | 8.5456e-05 | 1.1619e-06 | 73.55 | 1 | 308 | Load | 2723 | Load | Tran3phWye | ORDERS CONTRACTOR | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-18 | 2020 |  | Ark - Series 2
J2001.006933 | PD-01182020-00069 | METRO NORTH | GUTHRIE | 8814:PINE STREET | PINE_STREET_1424 | 881424 | 2020-01-18 14:06 | 2020-01-18 16:10 | 124.05 | 1 | 2 | 11.35 | 12 | POOR CONNECTION | 50 | CONNECTOR | GUTHRIE | 1405 N.ELM | CMI_NORMAL | NO | NO | NO | 860678 | 168109 | 19811 | 3099 | 1237 | 1.3187e-05 | 1.1619e-06 | 11.35 | 1 | 310 | Customer | 43545 | Load | Tran1phOH | JOSEPH WAYNE POOL | 405-919-2253 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006938 | PD-01182020-00071 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1521 | 811521 | 2020-01-18 14:11 | 2020-01-18 16:10 | 118.52 | 1 | 1 | 116.3167 | 23 | CUSTOMER EQUIPMENT | 15 | METER - SECONDARY | OKLAHOMA CITY | 1726 PETTEE DR. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 159052 | 102121 | 6061 | 1242 | 0.00013515 | 1.1619e-06 | 116.3167 | 1 | 310 | Customer | 83842 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-18 | 2020 |  | OK - 2022
J2001.006940 |  | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2923 | 812923 | 2020-01-18 14:18 | 2020-01-18 14:28 | 9.85 | 1 | 1 | 9.85 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 2948 SW.52 PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 159052 | 102121 | 6377 | 1633 | 1.1444e-05 | 1.1619e-06 | 9.85 | 1 | 310 | Customer | 31052 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-18 | 2020 |  | #N/A
J2001.006948 | PD-01182020-00081 | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-18 15:00 | 2020-01-18 20:01 | 300.7 | 1 | 4 | 167.8333 | 12 | POOR CONNECTION | 50 | CONNECTOR | MUSTANG | 408 N.RICHARD TR | CMI_NORMAL | NO | NO | NO | 860678 | 128730 | 115984 | 18234 | 4429 | 0.000195 | 1.1619e-06 | 167.8333 | 1 | 310 | Customer | 50768 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2022
J2001.006949 | PD-01182020-00084 | ARKANSAS | POTEAU | 3608:MULDROW | MULDROW 21 | 360821 | 2020-01-18 15:19 | 2020-01-18 15:54 | 35.05 | 1 | 1 | 35.05 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MULDROW | 310 E.BROADWAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 82183 | 13481 | 2270 | 1224 | 4.0724e-05 | 1.1619e-06 | 35.05 | 1 | 310 | Customer | 11085 | Load | Tran1phPad | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-18 | 2020 |  | #N/A
J2001.006951 | PD-01182020-00085 | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-18 15:24 | 2020-01-18 20:16 | 292.07 | 6 | 12 | 2649.2 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | MUSTANG | 309 W. APPLE BRANCH WAY | CMI_NORMAL | NO | NO | NO | 860678 | 128730 | 115984 | 18234 | 4429 | 0.003078 | 6.9712e-06 | 441.5333 | 1 | 310 | Secondary | 63880 | Load | Tran1phPad | HOWARD GETCHELL | 530-410-8920 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2022
J2001.006952 | PD-01182020-00086 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9921 | 829921 | 2020-01-18 15:35 | 2020-01-18 16:59 | 83.53 | 1 | 1 | 47.3333 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 6720 NW.11 | CMI_NORMAL | NO | NO | NO | 860678 | 128730 | 115984 | 9223 | 1635 | 5.4995e-05 | 1.1619e-06 | 47.3333 | 1 | 310 | Customer | 30129 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006954 | PD-01182020-00088 | METRO EAST | EAST | 8542:RENO | RENO_4224 | 854224 | 2020-01-18 15:44 | 2020-01-18 17:53 | 128.5 | 1 | 1 | 128.5 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MIDWEST CITY | 733 GREENWOOD DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 114373 | 71211 | 5214 | 1221 | 0.0001493 | 1.1619e-06 | 128.5 | 1 | 310 | Customer | 25332 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2022
J2001.006955 |  | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_524 | 890524 | 2020-01-18 15:53 | 2020-01-18 15:54 | 0.82 | 10 | 0 | 7.3818 | 1 | CANCELLED | 57 | CANCELLED | 0 | 0 | CMI_MOMENTARY | YES | NO | NO | 860678 | 128730 | 12746 | 6937 | 1651 | 8.5768e-06 | 1.1619e-05 | 0.73818 | 1 | 0 | Mainline |  | 0 | 0 | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006957 | PD-01182020-00091 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4035 | 834035 | 2020-01-18 16:05 | 2020-01-18 17:53 | 108.38 | 1 | 2 | 108.3833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | *140 E MACARTHUR-400 N HEFNER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 128730 | 115984 | 10841 | 1423 | 0.00012593 | 1.1619e-06 | 108.3833 | 1 | 320 | Customer | 73173 | Load | Tran1phPad | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006959 | PD-01182020-00093 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6523 | 836523 | 2020-01-18 16:11 | 2020-01-18 17:15 | 63.6 | 1 | 1 | 63.6 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7305 LYREWOOD LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 128730 | 115984 | 7420 | 2257 | 7.3895e-05 | 1.1619e-06 | 63.6 | 1 | 310 | Customer | 38608 | Load | Tran1phPad | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2022
J2001.006968 | PD-01182020-00094 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6324 | 816324 | 2020-01-18 16:47 | 2020-01-18 17:20 | 33.22 | 5 | 3 | 154.875 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MOORE | 121 EBERLE DR | CMI_NORMAL | NO | NO | NO | 860678 | 159052 | 102121 | 11824 | 2048 | 0.00017995 | 5.8094e-06 | 30.975 | 1 | 310 | Load | 33402 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2021
J2001.006967 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6324 | 816324 | 2020-01-18 16:47 | 2020-01-18 16:47 | 0 | 270 | 0 | 0 | 1 | CANCELLED | 57 | CANCELLED | MOORE | NW 12TH ST BTWN JANEWAY AND GALE ST | CMI_MOMENTARY | YES | NO | NO | 860678 | 159052 | 102121 | 11824 | 2048 | 0 | 0.00031371 | 0 | 1 | 0 | Mainline | 347960 | Recloser | Rec3phElectronic | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2021
J2001.006973 | PD-01182020-00095 | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 22 | 570822 | 2020-01-18 16:56 | 2020-01-18 17:35 | 38.82 | 1 | 2 | 37.95 | 4 | DETERIORATION | 50 | CONNECTOR | DAVIS | 403 E ALLEN | CMI_NORMAL | NO | NO | NO | 860678 | 77588 | 6811 | 1858 | 955 | 4.4093e-05 | 1.1619e-06 | 37.95 | 1 | 320 | Customer | 13773 | Load | Tran1phOH | BRUCE E BEAM | 405-626-0490 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-18 | 2020 |  | OK - 2021
J2001.006974 | PD-01182020-00096 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1522 | 811522 | 2020-01-18 17:04 | 2020-01-18 18:52 | 108.37 | 1 | 1 | 89.65 | 27 | TREE:NON PREVENTABLE | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 2311 SW.26 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860678 | 159052 | 102121 | 6061 | 1941 | 0.00010416 | 1.1619e-06 | 89.65 | 1 | 310 | Customer | 48254 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-18 | 2020 |  | OK - 2022
J2001.006976 | PD-01182020-00097 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3621 | 853621 | 2020-01-18 17:05 | 2020-01-18 18:40 | 94.63 | 1 | 2 | 89.8167 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1164 N.MISSOURI | CMI_NORMAL | NO | NO | NO | 860678 | 168109 | 148298 | 5920 | 2165 | 0.00010436 | 1.1619e-06 | 89.8167 | 1 | 310 | Customer | 7039 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2022
J2001.006975 | PD-01182020-00098 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6523 | 836523 | 2020-01-18 17:06 | 2020-01-18 21:32 | 265.58 | 1 | 1 | 265.5833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | WARR ACRES | 5712 NW 66th St | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 128730 | 115984 | 7420 | 2257 | 0.00030857 | 1.1619e-06 | 265.5833 | 1 | 310 | Customer | 21478 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2022
J2001.006977 | PD-01182020-00099 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5029 | 865029 | 2020-01-18 17:16 | 2020-01-18 19:23 | 126.8 | 1 | 1 | 126.8 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 1108 JET DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 114373 | 71211 | 8623 | 1736 | 0.00014733 | 1.1619e-06 | 126.8 | 1 | 320 | Customer | 10561 | Load | Tran1phOH | STEVEN CASKEY | 405-777-8855 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006981 | PD-01182020-00101 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3621 | 853621 | 2020-01-18 17:28 | 2020-01-18 18:37 | 69.18 | 3 | 3 | 202.45 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1728 NE.PARK | CMI_NORMAL | NO | NO | NO | 860678 | 168109 | 148298 | 5920 | 2165 | 0.00023522 | 3.4856e-06 | 67.4833 | 1 | 310 | Secondary | 957 | Load | TranOpenDelta | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2022
J2001.006988 |  | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_621 | 880621 | 2020-01-18 17:47 | 2020-01-18 18:05 | 18.83 | 1 | 1 | 16.2167 | 1 | CANCELLED | 57 | CANCELLED | GUTHRIE | 11/4MS ON HWY 77 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 168109 | 19811 | 5163 | 1877 | 1.8842e-05 | 1.1619e-06 | 16.2167 | 1 | 308 | Customer | 40900 | Load | TranOH3phDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006986 | PD-01182020-00102 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-01-18 17:47 | 2020-01-18 19:42 | 115.38 | 1 | 1 | 115.3833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DEL CITY | 3313 CHEEK DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 159052 | 102121 | 7415 | 2238 | 0.00013406 | 1.1619e-06 | 115.3833 | 1 | 310 | Customer | 7373 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2022
J2001.006989 |  | METRO SOUTH | SOUTH CENTRAL | 8133:WR AIRPORT | WR_AIRPORT_3323 | 813323 | 2020-01-18 18:10 | 2020-01-18 18:10 | 0.3 | 83 | 0 | 24.9 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 5401 S INDEPENDENCE AVE | CMI_MOMENTARY | YES | NO | NO | 860678 | 159086 | 102122 | 1487 | 83 | 2.8931e-05 | 9.6436e-05 | 0.3 | 1 | 0 | Feeder | WR WLD AIR_3323 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.006993 | PD-01182020-00105 | METRO SOUTH | SOUTH CENTRAL | 8133:WR AIRPORT | WR_AIRPORT_3323 | 813323 | 2020-01-18 18:23 | 2020-01-18 19:23 | 59.88 | 83 | 15 | 4952.3333 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 23 | FUSE - PRIMARY | OKLAHOMA CITY | 5401 S INDEPENDENCE AVE | CMI_NORMAL | NO | NO | NO | 860678 | 159086 | 102122 | 1487 | 83 | 0.005754 | 9.6436e-05 | 59.6667 | 1 | 310 | Feeder | WR WLD AIR_3323 | Recloser | SubRecloser | Substation Operations Crew | [6 empty] | Animals | N | SUBSTATION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.007004 |  | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-18 18:24 | 2020-01-18 18:48 | 23.25 | 3 | 2 | 53.05 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | MUSTANG | 408 N.RICHARD TR | CMI_NORMAL | NO | NO | NO | 860678 | 128731 | 115984 | 18234 | 4429 | 6.1637e-05 | 3.4856e-06 | 17.6833 | 1 | 310 | Load | 50768 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2022
J2001.006998 | PD-01182020-00104 | METRO EAST | EAST | 8542:RENO | RENO_4222 | 854222 | 2020-01-18 18:26 | 2020-01-18 19:11 | 44.5 | 1 | 1 | 15.7523 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DEL CITY | 5500 E. RENO AVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 114338 | 71176 | 5214 | 1688 | 1.8302e-05 | 1.1619e-06 | 15.7523 | 1 | 310 | Customer | 77364 | Load | Tran3phWye | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.007007 | PD-01182020-00106 | METRO WEST | WEST | 8158:SARA | SARA_5871 | 815871 | 2020-01-18 18:54 | 2020-01-18 20:31 | 96.5 | 1 | 1 | 10.5 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 1400 S SARA RD | CMI_NORMAL | NO | NO | NO | 860678 | 128731 | 115984 | 18234 | 5388 | 1.22e-05 | 1.1619e-06 | 10.5 | 1 | 310 | Load | 242455 | Load | Tran1phOH | GARY A DUNCAN | 405-474-9336 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2022
J2001.007009 | PD-01182020-00107 | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-01-18 19:25 | 2020-01-18 21:42 | 137.45 | 1 | 1 | 122.3667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 12113 EDNA RD | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860678 | 159086 | 56964 | 4239 | 3070 | 0.00014217 | 1.1619e-06 | 122.3667 | 1 | 320 | Customer | 48837 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.007029 | PD-01182020-00123 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6121 | 836121 | 2020-01-18 22:17 | 2020-01-18 23:11 | 53.98 | 1 | 2 | 53.9833 | 3 | DAMAGED BY PUBLIC | 15 | METER - SECONDARY | OKLAHOMA CITY | 1524 NW.38 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860678 | 168110 | 148298 | 11100 | 1638 | 6.2722e-05 | 1.1619e-06 | 53.9833 | 1 | 310 | Customer | 1246 | Load | TranOpenDelta | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | OK - 2021
J2001.007030 | PD-01182020-00124 | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-01-18 22:25 | 2020-01-19 00:04 | 98.75 | 1 | 1 | 98.75 | 4 | DETERIORATION | 15 | METER - SECONDARY | RAVIA | 10601 DUSTY LN | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860678 | 77589 | 7201 | 2192 | 1673 | 0.00011474 | 1.1619e-06 | 98.75 | 1 | 320 | Load | 241383 | Load | Tran1phOH | DAVID TAYLOR | 580-574-4517 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.007034 | PD-01182020-00126 | METRO EAST | EAST | 8542:RENO | RENO_4222 | 854222 | 2020-01-18 22:41 | 2020-01-19 00:13 | 92.18 | 1 | 1 | 92.1833 | 12 | POOR CONNECTION | 50 | CONNECTOR | DEL CITY | 5500 E. RENO AVE | CMI_NORMAL | NO | NO | NO | 860678 | 114338 | 71176 | 5214 | 1688 | 0.00010711 | 1.1619e-06 | 92.1833 | 1 | 320 | Customer | 77364 | Load | Tran3phWye | THOMAS E COLE | 405-623-9338 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-18 | 2020 |  | #N/A
J2001.007070 |  | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1723 | 861723 | 2020-01-19 06:17 | 2020-01-19 06:33 | 15.8 | 1 | 1 | 15.8 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DEL CITY | 4889 SE.44 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 114338 | 71176 | 6948 | 1599 | 1.8355e-05 | 1.1617e-06 | 15.8 | 1 | 310 | Customer | 44985 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-19 | 2020 |  | #N/A
J2001.007078 | PD-01192020-00034 | METRO WEST | WEST | 8158:SARA | SARA_5862 | 815862 | 2020-01-19 07:33 | 2020-01-19 08:11 | 37.7 | 1 | 1 | 30.1573 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 12301 SW.CHISHOLM | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 128731 | 115984 | 18234 | 3607 | 3.5035e-05 | 1.1617e-06 | 30.1573 | 1 | 310 | Customer | 63658 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | OK - 2022
J2001.007084 |  | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1021 | 311021 | 2020-01-19 07:57 | 2020-01-19 07:57 | 0 | 299 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MUSKOGEE | 1541 COUNTRY CLUB PLACE | CMI_MOMENTARY | YES | NO | NO | 860782 | 73995 | 33249 | 2902 | 299 | 0 | 0.00034736 | 0 | 1 | 0 | Feeder | RIVERSIDE_1021 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-19 | 2020 |  | #N/A
J2001.007086 | PD-01192020-00036 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4124 | 814124 | 2020-01-19 08:17 | 2020-01-19 09:30 | 73.02 | 12 | 14 | 849.6 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 617 SW.45 | CMI_NORMAL | NO | NO | NO | 860782 | 159086 | 102122 | 5807 | 2012 | 0.00098701 | 1.3941e-05 | 70.8 | 1 | 310 | Load | 9066 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-19 | 2020 |  | #N/A
J2001.007091 | PD-01192020-00038 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9921 | 829921 | 2020-01-19 08:41 | 2020-01-19 10:30 | 109.47 | 8 | 7 | 744.6667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | BETHANY | 6304 NW.22 | CMI_NORMAL | NO | NO | NO | 860782 | 128731 | 115984 | 9223 | 1635 | 0.0008651 | 9.2939e-06 | 93.0833 | 1 | 310 | Load | 27586 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007090 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9921 | 829921 | 2020-01-19 08:41 | 2020-01-19 08:41 | 0.05 | 1636 | 0 | 81.8 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 1101 N CHISHOLM RD | CMI_MOMENTARY | YES | NO | NO | 860782 | 128731 | 115984 | 9223 | 1635 | 9.503e-05 | 0.0019006 | 0.05 | 1 | 0 | Feeder | WESTOAKS_9921 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007093 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_871 | 830871 | 2020-01-19 08:50 | 2020-01-19 09:01 | 10.6 | 1 | 1 | 10.6 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 18904 RESTO LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 168110 | 148298 | 19362 | 4239 | 1.2314e-05 | 1.1617e-06 | 10.6 | 1 | 310 | Customer | 359642 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | OK - 2021
J2001.007103 | PD-01192020-00041 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_526 | 510526 | 2020-01-19 09:26 | 2020-01-19 11:38 | 132.2 | 5 | 5 | 634.3333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ARDMORE | 332 D NW. | CMI_NORMAL | NO | NO | NO | 860782 | 77589 | 23584 | 4774 | 1620 | 0.00073693 | 5.8087e-06 | 126.8667 | 1 | 310 | Load | 13947 | Load | Tran1phOH | JUSTIN B MARSHALL | 580-221-5051 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-19 | 2020 |  | OK - 2020
J2001.007107 | PD-01192020-00042 | SOUTHERN | PAULS VALLEY | 5611:MAYSVILLE | MAYSVILLE 21 | 561121 | 2020-01-19 09:42 | 2020-01-19 11:08 | 85.68 | 3 | 3 | 253.4 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MAYSVILLE | MAYSVILLE | CMI_NORMAL | NO | NO | NO | 860782 | 77589 | 6206 | 945 | 493 | 0.00029438 | 3.4852e-06 | 84.4667 | 1 | 310 | Load | 848 | Load | Tran1phOH | BRUCE E BEAM | 405-626-0490 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | OK - 2021
J2001.007104 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1022 | 541022 | 2020-01-19 09:45 | 2020-01-19 09:45 | 0 | 873 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MADILL | 12537 HIGHWAY 199 | CMI_MOMENTARY | YES | NO | NO | 860782 | 77589 | 7201 | 2378 | 873 | 0 | 0.0010142 | 0 | 1 | 0 | Feeder | GLASSES_1022 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007109 | PD-01192020-00043 | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1022 | 541022 | 2020-01-19 09:49 | 2020-01-19 11:27 | 98.3 | 1 | 2 | 91.9833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MADILL | US HWY 70 AND US HWY 377 | CMI_NORMAL | NO | NO | NO | 860782 | 77589 | 7201 | 2378 | 873 | 0.00010686 | 1.1617e-06 | 91.9833 | 1 | 310 | Load | 2977 | Load | TranOpenDelta | DAVID TAYLOR | 580-574-4517 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007106 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3831 | 913831 | 2020-01-19 09:50 | 2020-01-19 12:18 | 148.42 | 4 | 0 | 585.6333 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 3631 TOWSON | CMI_PLANNED | YES | NO | NO | 860782 | 82183 | 61162 | 2934 | 485 | 0.00068035 | 4.6469e-06 | 146.4083 | 1 | 0 | Mainline | 327603 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-19 | 2020 |  | Ark - Series 2
J2001.007108 | PD-01192020-00044 | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1022 | 541022 | 2020-01-19 09:53 | 2020-01-19 10:57 | 64.43 | 1 | 1 | 64.4333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MADILL | 1006 SAMBO DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 77589 | 7201 | 2378 | 873 | 7.4854e-05 | 1.1617e-06 | 64.4333 | 1 | 310 | Customer | 8065 | Load | Tran1phPad | DAVID TAYLOR | 580-574-4517 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007110 |  | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6523 | 836523 | 2020-01-19 09:56 | 2020-01-19 10:04 | 8.07 | 1 | 1 | 8.0667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | WARR ACRES | 6135 NW 63rd St | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 128731 | 115984 | 7420 | 2257 | 9.3713e-06 | 1.1617e-06 | 8.0667 | 1 | 310 | Customer | 42608 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | OK - 2022
J2001.007119 | PD-01192020-00048 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3925 | 833925 | 2020-01-19 09:57 | 2020-01-19 12:05 | 127.72 | 3 | 5 | 376.45 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | BETHANY | 7004 NW.59 TR | CMI_NORMAL | NO | NO | NO | 860782 | 168110 | 148298 | 7850 | 2183 | 0.00043733 | 3.4852e-06 | 125.4833 | 1 | 310 | Secondary | 14393 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | OK - 2022
J2001.007116 | PD-01192020-00046 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6324 | 816324 | 2020-01-19 09:59 | 2020-01-19 10:31 | 32.07 | 6 | 9 | 184.1 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MOORE | 829 NW.7 | CMI_NORMAL | NO | NO | NO | 860782 | 159086 | 102122 | 11824 | 2048 | 0.00021388 | 6.9704e-06 | 30.6833 | 1 | 310 | Secondary | 52244 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | OK - 2021
J2001.007113 | PD-01192020-00047 | METRO WEST | WEST | 8158:SARA | SARA_5864 | 815864 | 2020-01-19 09:59 | 2020-01-19 11:15 | 75.62 | 1 | 1 | 72.8833 | 4 | DETERIORATION | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 500 N RICHLAND RD | CMI_NORMAL | NO | NO | NO | 860782 | 128731 | 115984 | 18234 | 4810 | 8.4671e-05 | 1.1617e-06 | 72.8833 | 1 | 310 | Customer | 34612 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | OK - 2022
J2001.007118 | PD-01192020-00050 | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1621 | 581621 | 2020-01-19 10:03 | 2020-01-19 11:10 | 66.73 | 1 | 1 | 62.6333 | 4 | DETERIORATION | 20 | FUSE BARREL | ADA | ALLEY N 6TH E OF OAK | CMI_NORMAL | NO | NO | NO | 860782 | 77589 | 11509 | 3456 | 1805 | 7.2763e-05 | 1.1617e-06 | 62.6333 | 1 | 320 | Load | 24969 | Load | Tran3phWye | CAMERON BRADY | 580-307-7052 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007122 | PD-01192020-00051 | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_629 | 730629 | 2020-01-19 10:08 | 2020-01-19 12:37 | 148.68 | 4 | 9 | 582.7667 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | SEMINOLE | 2220 GROUNDS | CMI_NORMAL | NO | NO | NO | 860782 | 114338 | 13601 | 4061 | 567 | 0.00067702 | 4.6469e-06 | 145.6917 | 1 | 310 | Load | 5941 | Load | Tran1phOH | DELBERT HISAW | 405-683-1721 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | OK - 2021
J2001.007121 |  | NORTHEAST | SAPULPA | 7620:ANTIOCH | ANTIOCH 49 | 762049 | 2020-01-19 10:16 | 2020-01-19 10:25 | 9.63 | 1 | 1 | 9.6333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | CUSHING | .5MW .5MN YALE ES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 73995 | 40746 | 183 | 183 | 1.1191e-05 | 1.1617e-06 | 9.6333 | 1 | 310 | Load | 16787 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-19 | 2020 |  | #N/A
J2001.007126 | PD-01192020-00054 | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-19 10:26 | 2020-01-19 12:18 | 112.32 | 6 | 9 | 631.2 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MUSTANG | 738 S.GLEN LN | CMI_NORMAL | NO | NO | NO | 860782 | 128731 | 115984 | 18234 | 4429 | 0.00073329 | 6.9704e-06 | 105.2 | 1 | 310 | Load | 42887 | Load | Tran1phPad | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | OK - 2022
J2001.007132 |  | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-19 10:26 | 2020-01-19 12:22 | 116.3 | 4 | 5 | 420.8 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MUSTANG | 714 S.GLEN LN | CMI_NORMAL | NO | NO | NO | 860782 | 128731 | 115984 | 18234 | 4429 | 0.00048886 | 4.6469e-06 | 105.2 | 1 | 310 | Load | 42886 | Load | Tran1phPad | [7 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | OK - 2022
J2001.007131 | PD-01192020-00052 | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_624 | 730624 | 2020-01-19 10:45 | 2020-01-19 11:48 | 63.48 | 1221 | 350 | 77452.1 | 15 | SQUIRREL | 18 | INSULATOR | SEMINOLE | 125 HWY 9 WEST | CMI_NORMAL | NO | NO | NO | 860782 | 114338 | 13601 | 4061 | 1221 | 0.089979 | 0.0014185 | 63.4333 | 1 | 310 | Feeder | FIXICO_624 | Recloser | SubRecloser | DELBERT HISAW | 405-683-1721 | [5 empty] | Animals | N | SUBSTATION | 138kV | 2020-01-19 | 2020 |  | OK - 2020
J2001.007134 | PD-01192020-00053 | NORTHEAST | MUSKOGEE | 3111:FIVE TRIBES | FIVE_TRIBES_1129 | 311129 | 2020-01-19 10:48 | 2020-01-19 12:51 | 122.58 | 45 | 25 | 5073.75 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | MUSKOGEE | AIR BASE MUSKOGEE | CMI_NORMAL | NO | NO | NO | 860782 | 73995 | 33249 | 1682 | 865 | 0.0058943 | 5.2278e-05 | 112.75 | 1 | 310 | Mainline | 14447 | Fuse | FuseOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-19 | 2020 |  | #N/A
J2001.007137 |  | METRO EAST | EAST | 8417:ROUND BARN | ROUND_BARN_1723 | 841723 | 2020-01-19 10:53 | 2020-01-19 11:02 | 9.03 | 1 | 1 | 9.0333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 14420 ANDERSON ROAD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 114338 | 71176 | 1008 | 1008 | 1.0494e-05 | 1.1617e-06 | 9.0333 | 1 | 310 | Load | 73208 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007136 | PD-01192020-00056 | SOUTHERN | PAULS VALLEY | 5619:RUSH CREEK | RUSH_CREEK_1922 | 561922 | 2020-01-19 10:54 | 2020-01-19 11:41 | 47.05 | 1 | 1 | 43.6833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | PAULS VALLEY | S OF LESLIE E OF EAST AVE | CMI_NORMAL | NO | NO | NO | 860782 | 77589 | 6206 | 2072 | 1192 | 5.0748e-05 | 1.1617e-06 | 43.6833 | 1 | 310 | Customer | 5754 | Load | Tran1phOH | BRUCE E BEAM | 405-626-0490 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-19 | 2020 |  | OK - 2021
J2001.007138 | PD-01192020-00055 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2623 | 862623 | 2020-01-19 10:54 | 2020-01-19 11:32 | 37.75 | 1 | 1 | 36.05 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2400 SE.37 | CMI_NORMAL | NO | NO | NO | 860782 | 159086 | 102122 | 7415 | 297 | 4.1881e-05 | 1.1617e-06 | 36.05 | 1 | 311 | Customer | 11393 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007139 | PD-01192020-00057 | NORTHEAST | SAPULPA | 7614:KNIPE | KNIPE_1423 | 761423 | 2020-01-19 10:55 | 2020-01-19 13:09 | 134.18 | 1 | 1 | 53.2667 | 16 | SUBSTATION OPERATION | 55 | SCADA - CIRCUIT TRIP | SEMINOLE | .4E WESTERN 300 S OF HWY33 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 73995 | 40746 | 1824 | 790 | 6.1882e-05 | 1.1617e-06 | 53.2667 | 1 | 310 | Customer | 22769 | Load | Tran1phOH | DELBERT HISAW | 405-683-1721 | [5 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007140 |  | SOUTHERN | DURANT | 5504:BUTTERFIELD | BUTTERFIELD_429 | 550429 | 2020-01-19 10:59 | 2020-01-19 10:59 | 0.03 | 1272 | 0 | 42.4 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | DURANT | 2401 CALE SWITCH RD | CMI_MOMENTARY | YES | NO | NO | 860782 | 77589 | 15483 | 3484 | 1272 | 4.9258e-05 | 0.0014777 | 0.033333 | 1 | 0 | Feeder | BUTTEFLD_429 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007143 | PD-01192020-00058 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1523 | 811523 | 2020-01-19 11:00 | 2020-01-19 12:05 | 64.93 | 1 | 1 | 3.6667 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 2015 SW.9 | CMI_NORMAL | NO | NO | NO | 860782 | 159086 | 102122 | 6061 | 805 | 4.2597e-06 | 1.1617e-06 | 3.6667 | 1 | 310 | Customer | 22503 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-19 | 2020 |  | OK - 2022
J2001.007142 | PD-01192020-00059 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_866 | 830866 | 2020-01-19 11:01 | 2020-01-19 13:13 | 131.58 | 1 | 1 | 130.7344 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | Btwn Bldgs 600 and 700-Cottages at Quail Springs apartment complex | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 168110 | 148298 | 19362 | 4303 | 0.00015188 | 1.1617e-06 | 130.7344 | 1 | 320 | Customer | 403238 | Load | Tran1phPad | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007145 | PD-01192020-00060 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2225 | 832225 | 2020-01-19 11:08 | 2020-01-19 12:37 | 89.35 | 1 | 1 | 89.35 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 2436 NW.33 | CMI_NORMAL | NO | NO | NO | 860782 | 168110 | 148298 | 9172 | 2038 | 0.0001038 | 1.1617e-06 | 89.35 | 1 | 311 | Customer | 10449 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-19 | 2020 |  | OK - 2021
J2001.007147 | PD-01192020-00062 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3021 | 743021 | 2020-01-19 11:11 | 2020-01-19 11:53 | 42.48 | 1 | 1 | 42.4833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SHAWNEE | 707 N.UNION | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 114338 | 22099 | 6641 | 1701 | 4.9354e-05 | 1.1617e-06 | 42.4833 | 1 | 320 | Customer | 4012 | Load | Tran1phOH | ADAM CLARK | 580-310-8924 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | OK - 2021
J2001.007146 | PD-01192020-00061 | SOUTHERN | DURANT | 5504:BUTTERFIELD | BUTTERFIELD_429 | 550429 | 2020-01-19 11:12 | 2020-01-19 12:11 | 59.03 | 1 | 1 | 59.0333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DURANT | 1215 S 9th | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 77589 | 15483 | 3484 | 1272 | 6.8581e-05 | 1.1617e-06 | 59.0333 | 1 | 310 | Load | 422460 | Load | Tran3phWye | MICHAEL N STROHL | 903-821-1619 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007150 | PD-01192020-00065 | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_621 | 550621 | 2020-01-19 11:56 | 2020-01-19 13:11 | 74.15 | 1 | 1 | 74.15 | 11 | OVERLOAD | 49 | CUSTOMER EQUIPMENT | DURANT | HWY 70/ WESTERN MEADOWS, 150E, 250N | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860782 | 77589 | 15483 | 6737 | 902 | 8.6143e-05 | 1.1617e-06 | 74.15 | 1 | 310 | Load | 360442 | Load | Tran3phWye | MICHAEL N STROHL | 903-821-1619 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007151 |  | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_647 | 890647 | 2020-01-19 12:00 | 2020-01-19 12:00 | 0 | 1070 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | SOUTHARD | HWY 51 AND HWY 51A, GO.5 MILE SOUTH, .5 MILE EAST | CMI_MOMENTARY | YES | NO | NO | 860782 | 128731 | 12747 | 1365 | 1070 | 0 | 0.0012431 | 0 | 1 | 0 | Feeder | SOUTHARD_647 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007155 | PD-01192020-00072 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3672 | 853672 | 2020-01-19 12:20 | 2020-01-19 14:14 | 114.03 | 1 | 1 | 19.5787 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | RENO & OKLAHOMA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 168110 | 148298 | 5920 | 239 | 2.2745e-05 | 1.1617e-06 | 19.5787 | 1 | 310 | Customer | 255229 | Load | Tran3phPadWye | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007163 | PD-01192020-00084 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2029 | 862029 | 2020-01-19 12:43 | 2020-01-19 14:16 | 93.12 | 1 | 1 | 93.1167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 714 SE.21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 159086 | 102122 | 4744 | 982 | 0.00010818 | 1.1617e-06 | 93.1167 | 1 | 310 | Customer | 7110 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007166 | PD-01192020-00089 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1226 | 831226 | 2020-01-19 13:06 | 2020-01-19 13:43 | 37.15 | 1 | 1 | 37.15 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1500 NW.45 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 168110 | 148298 | 7744 | 1747 | 4.3158e-05 | 1.1617e-06 | 37.15 | 1 | 310 | Customer | 13980 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | OK - 2021
J2001.007169 | PD-01192020-00091 | METRO EAST | SHAWNEE | 7409:MCLOUD | MCLOUD_922 | 740922 | 2020-01-19 13:16 | 2020-01-19 13:53 | 37.43 | 1 | 2 | 34.5833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | SHAWNEE | 4MW OBU | CMI_NORMAL | NO | NO | NO | 860782 | 114338 | 22099 | 2031 | 1210 | 4.0177e-05 | 1.1617e-06 | 34.5833 | 1 | 310 | Load | 5987 | Load | Tran1phOH | ADAM CLARK | 580-310-8924 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-19 | 2020 |  | OK - 2021
J2001.007170 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3831 | 913831 | 2020-01-19 13:17 | 2020-01-19 17:16 | 239.2 | 4 | 4 | 946.7333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 2920 TOWSON AV + S.BOSTON ST. | CMI_PLANNED | YES | NO | NO | 860782 | 82183 | 61162 | 2934 | 485 | 0.0010999 | 4.6469e-06 | 236.6833 | 1 | 310 | Load | 5177 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-19 | 2020 |  | Ark - Series 2
J2001.007173 | PD-01192020-00097 | NORTHWEST | ENID | 4109:WAUKOMIS | WAUKOMIS 22 | 410922 | 2020-01-19 13:53 | 2020-01-19 15:27 | 93.98 | 1 | 2 | 3.7 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | WAUKOMIS | 551 W.EUCLID | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860782 | 53518 | 37579 | 1558 | 255 | 4.2984e-06 | 1.1617e-06 | 3.7 | 1 | 320 | Customer | 7242 | Load | Tran1phOH | WILLIAM R PETHICK | 580-278-8129 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007181 | PD-01192020-00109 | NORTHEAST | SAPULPA | 3216:BEELINE | BEELINE_1633 | 321633 | 2020-01-19 14:43 | 2020-01-19 18:04 | 201.33 | 11 | 17 | 1971.2 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | GLENPOOL | 688 E 135TH PL | CMI_NORMAL | NO | NO | NO | 860782 | 73995 | 40746 | 5564 | 1948 | 0.00229 | 1.2779e-05 | 179.2 | 1 | 310 | Load | 40297 | Load | Tran1phOH | CONTRACTOR 5 DAVID ELLIOT INC | 918-639-5055 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007182 |  | METRO SOUTH | SOUTH | 8728:CHERRY CREEK | CHERRY_CREEK_2831 | 872831 | 2020-01-19 15:00 | 2020-01-19 15:00 | 0 | 483 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | NORMAN | 48TH AV NW & KATHY LYNN DR | CMI_MOMENTARY | YES | NO | NO | 860782 | 159086 | 56964 | 7104 | 1643 | 0 | 0.00056112 | 0 | 1 | 0 | Mainline | 332600 | Recloser | Rec3phElectronic | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007186 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9922 | 829922 | 2020-01-19 15:42 | 2020-01-19 15:45 | 3.08 | 1 | 1 | 3.0833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 534 N.ROCKWELL | CMI_MOMENTARY | YES | NO | NO | 860782 | 128731 | 115984 | 9223 | 842 | 3.582e-06 | 1.1617e-06 | 3.0833 | 1 | 310 | Customer | 42621 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007192 | PD-01192020-00118 | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-19 16:19 | 2020-01-19 21:03 | 284.15 | 1 | 1 | 68.0833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MUSTANG | 524 S.FOREST DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 128731 | 115984 | 18234 | 4429 | 7.9095e-05 | 1.1617e-06 | 68.0833 | 1 | 310 | Customer | 41956 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | OK - 2022
J2001.007194 | PD-01192020-00117 | METRO WEST | WEST | 8158:SARA | SARA_5862 | 815862 | 2020-01-19 16:27 | 2020-01-19 18:37 | 130.37 | 1 | 1 | 130.3667 | 11 | OVERLOAD | 2 | TRANSFORMER OH | MUSTANG | 1321 N.MORGAN RD | CMI_NORMAL | NO | NO | NO | 860782 | 128731 | 115984 | 18234 | 3607 | 0.00015145 | 1.1617e-06 | 130.3667 | 1 | 310 | Customer | 4098 | Load | Tran1phOH | HOWARD GETCHELL | 530-410-8920 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | OK - 2022
J2001.007199 | PD-01192020-00122 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1226 | 831226 | 2020-01-19 16:41 | 2020-01-19 18:27 | 105.5 | 1 | 1 | 105.5 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1500 NW.45 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 168110 | 148298 | 7744 | 1747 | 0.00012256 | 1.1617e-06 | 105.5 | 1 | 320 | Customer | 13980 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | OK - 2021
J2001.007200 | PD-01192020-00121 | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1723 | 911723 | 2020-01-19 16:43 | 2020-01-19 17:37 | 53.93 | 1 | 1 | 52.9 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | CENTRAL CITY | 1.5 M N. HWY 255 ON HAZEL SUE | CMI_NORMAL | NO | NO | NO | 860782 | 82183 | 61162 | 4240 | 1624 | 6.1456e-05 | 1.1617e-06 | 52.9 | 1 | 310 | Customer | 16465 | Load | Tran1phOH | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-01-19 | 2020 |  | #N/A
J2001.007201 |  | SOUTHERN | HEALDTON | 5309:POOLEVILLE | POOLEVILLE_927 | 530927 | 2020-01-19 16:45 | 2020-01-19 17:22 | 36.55 | 1 | 0 | 35.9333 | 4 | DETERIORATION | 27 | CUTOUT | 0 | 2643 RANCH RD | CMI_PLANNED | YES | NO | NO | 860782 | 77589 | 6795 | 400 | 141 | 4.1745e-05 | 1.1617e-06 | 35.9333 | 1 | 0 | Load | 336119 | Load | Tran3phWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007203 |  | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6523 | 836523 | 2020-01-19 16:53 | 2020-01-19 17:02 | 9.53 | 1 | 1 | 9.5333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | WARR ACRES | 6135 NW 63rd St | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 128731 | 115984 | 7420 | 2257 | 1.1075e-05 | 1.1617e-06 | 9.5333 | 1 | 310 | Customer | 42608 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | OK - 2022
J2001.007205 | PD-01192020-00123 | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 22 | 320922 | 2020-01-19 17:06 | 2020-01-19 19:11 | 124.67 | 3 | 3 | 374 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | BIXBY | 211 N GRANT ST | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860782 | 73995 | 40746 | 2749 | 1310 | 0.00043449 | 3.4852e-06 | 124.6667 | 1 | 310 | Secondary | 42232 | Load | Tran1phOH | CGI ADMIN | 918-261-6802 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-19 | 2020 |  | OK - 2021
J2001.007208 |  | SOUTHERN | HEALDTON | 5309:POOLEVILLE | POOLEVILLE_927 | 530927 | 2020-01-19 17:30 | 2020-01-19 18:01 | 30.88 | 1 | 0 | 25.7667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | 0 | NE NW NW SEC5 T2S R2W | CMI_PLANNED | YES | NO | NO | 860782 | 77589 | 6795 | 400 | 141 | 2.9934e-05 | 1.1617e-06 | 25.7667 | 1 | 0 | Load | 25425 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007215 |  | NORTHWEST | ENID | 4414:HENNESSEY | HENNESSEY_1423 | 441423 | 2020-01-19 18:12 | 2020-01-19 18:12 | 0 | 286 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | HENNESSEY | HWY51 AND HWY 81 WEST 0.5 MILE, SOUTH 0.75 MILE | CMI_MOMENTARY | YES | NO | NO | 860782 | 53517 | 37578 | 1953 | 286 | 0 | 0.00033226 | 0 | 1 | 0 | Feeder | HENNESSEY_1423 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007220 |  | METRO WEST | WEST | 8158:SARA | SARA_5862 | 815862 | 2020-01-19 18:30 | 2020-01-19 21:13 | 162.98 | 1 | 1 | 120.8167 | 4 | DETERIORATION | 2 | TRANSFORMER OH | MUSTANG | 1321 N.MORGAN RD | CMI_NORMAL | NO | NO | NO | 860782 | 128729 | 115983 | 18234 | 3607 | 0.00014036 | 1.1617e-06 | 120.8167 | 1 | 310 | Customer | 4098 | Load | Tran1phOH | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | OK - 2022
J2001.007229 | PD-01192020-00130 | METRO EAST | EAST | 8416:DUNJEE | DUNJEE_1623 | 841623 | 2020-01-19 19:04 | 2020-01-19 20:05 | 60.83 | 1 | 1 | 60.8333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 7400 N.E. 36TH STREET | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 114335 | 71175 | 3540 | 1988 | 7.0672e-05 | 1.1617e-06 | 60.8333 | 1 | 320 | Load | 343195 | Load | 0 | STEVEN CASKEY | 405-777-8855 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007232 | PD-01192020-00133 | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_621 | 770621 | 2020-01-19 19:36 | 2020-01-20 01:18 | 341.72 | 3 | 5 | 1009.8 | 4 | DETERIORATION | 2 | TRANSFORMER OH | BRISTOW | 600 S ASH | CMI_NORMAL | NO | NO | NO | 860782 | 73994 | 40745 | 3780 | 1575 | 0.0011731 | 3.4852e-06 | 336.6 | 1 | 310 | Load | 42875 | Load | Tran1phOH | DWAYNE FOX | 405-695-8501 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-19 | 2020 |  | OK - 2021
J2001.007236 |  | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_429 | 580429 | 2020-01-19 19:57 | 2020-01-19 20:03 | 5.95 | 1 | 1 | 5.95 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ADA | 2N CADDO BR NW CRNR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 77585 | 11509 | 3413 | 1343 | 6.9123e-06 | 1.1617e-06 | 5.95 | 1 | 310 | Customer | 21598 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | OK - 2021
J2001.007240 | PD-01192020-00138 | METRO NORTH | NORTH | 8209:CLASSEN | CLASSEN_961 | 820961 | 2020-01-19 20:19 | 2020-01-19 21:17 | 57.78 | 1 | 1 | 57.7833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | KERR + SHARTEL - OK CO JAIL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 168109 | 148297 | 3881 | 866 | 6.7129e-05 | 1.1617e-06 | 57.7833 | 1 | 320 | Customer | 2660 | Load | Tran3phPadWye | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007241 | PD-01192020-00140 | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_623 | 550623 | 2020-01-19 20:33 | 2020-01-20 00:30 | 236.57 | 1 | 1 | 210.4833 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | DURANT | 119 KIMBER LANE | CMI_NORMAL | NO | NO | NO | 860782 | 77585 | 15482 | 6736 | 1717 | 0.00024453 | 1.1617e-06 | 210.4833 | 1 | 320 | Customer | 6339 | Load | Tran1phPad | JOE LOFTIS | 918-884-5349 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007246 | PD-01192020-00146 | METRO NORTH | NORTH | 8209:CLASSEN | CLASSEN_961 | 820961 | 2020-01-19 20:50 | 2020-01-19 21:46 | 56.12 | 1 | 1 | 56.1167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 900 West Main | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 168109 | 148297 | 3881 | 866 | 6.5193e-05 | 1.1617e-06 | 56.1167 | 1 | 310 | Customer | 363502 | Load | Tran3phWye | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-19 | 2020 |  | #N/A
J2001.007251 | PD-01192020-00147 | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3422 | 843422 | 2020-01-19 21:31 | 2020-01-19 22:05 | 33.58 | 1 | 1 | 16.025 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 8820 PLACID DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 168109 | 148297 | 1224 | 726 | 1.8617e-05 | 1.1617e-06 | 16.025 | 1 | 320 | Customer | 5255 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-19 | 2020 |  | #N/A
J2001.007261 |  | NORTHEAST | SAPULPA | 3210:HICKORY HILL | HICKORY_HILL_1024 | 321024 | 2020-01-20 00:37 | 2020-01-20 00:48 | 10.32 | 1 | 1 | 10.3167 | 1 | CANCELLED | 57 | CANCELLED | SAPULPA | 1025 E.TAFT 125A | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 73994 | 40745 | 2683 | 1246 | 1.1985e-05 | 1.1617e-06 | 10.3167 | 1 | 320 | Customer | 44756 | Load | TranOH3phDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2022
J2001.007278 | PD-01202020-00002 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-01-20 03:05 | 2020-01-20 04:25 | 80.1 | 4 | 5 | 313.6667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 400 NW.19 | CMI_NORMAL | NO | NO | NO | 860782 | 168109 | 148297 | 11100 | 2336 | 0.0003644 | 4.6469e-06 | 78.4167 | 1 | 310 | Load | 23308 | Load | TranOpenDelta | ADAM COX | 405-328-8938 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2020
J2001.007277 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-01-20 03:05 | 2020-01-20 03:05 | 0.02 | 2336 | 0 | 38.9333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 1121 NW 30TH ST | CMI_MOMENTARY | YES | NO | NO | 860782 | 168109 | 148297 | 11100 | 2336 | 4.523e-05 | 0.0027138 | 0.016667 | 1 | 0 | Feeder | WESTR AV_6125 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-20 | 2020 |  | OK - 2020
J2001.007284 | PD-01202020-00008 | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2173 | 862173 | 2020-01-20 04:34 | 2020-01-20 06:34 | 119.57 | 1 | 1 | 108.7667 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | NOBLE | 305 ROBIN CI | CMI_NORMAL | NO | NO | NO | 860782 | 159086 | 56964 | 4239 | 164 | 0.00012636 | 1.1617e-06 | 108.7667 | 1 | 310 | Customer | 64892 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007288 |  | SOUTHERN | HEALDTON | 5321:WILDHORSE | WILDHORSE_2122 | 532122 | 2020-01-20 05:28 | 2020-01-20 05:29 | 0.7 | 35 | 0 | 24.5 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | RATLIFF CITY | 4770 WEST COUNTY LINE RD | CMI_MOMENTARY | YES | NO | NO | 860782 | 77585 | 6794 | 155 | 35 | 2.8462e-05 | 4.0661e-05 | 0.7 | 1 | 0 | Feeder | WILDHORSE_2122 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-20 | 2020 |  | #N/A
J2001.007294 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_861 | 830861 | 2020-01-20 05:33 | 2020-01-20 08:34 | 181.6 | 52 | 38 | 7054.6667 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | 4613 NW 164TH TER | CMI_NORMAL | NO | NO | NO | 860782 | 168109 | 148297 | 19362 | 3932 | 0.0081956 | 6.041e-05 | 135.6667 | 1 | 310 | Mainline | 226656 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007291 | PD-01202020-00009 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_861 | 830861 | 2020-01-20 05:33 | 2020-01-20 12:22 | 409.38 | 3 | 4 | 394 | 13 | PREMATURE FAILURE | 1 | TRANSFORMER UG | OKLAHOMA CITY | LOT 10 BLK 1 LONE OAK PARK | CMI_NORMAL | NO | NO | NO | 860782 | 168109 | 148297 | 19362 | 3932 | 0.00045772 | 3.4852e-06 | 131.3333 | 1 | 310 | Secondary | 227837 | Load | Tran1phPad | HOWARD GETCHELL | 530-410-8920 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007290 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_861 | 830861 | 2020-01-20 05:33 | 2020-01-20 05:33 | 0 | 3932 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 4001 NW 164TH | CMI_MOMENTARY | YES | NO | NO | 860782 | 168109 | 148297 | 19362 | 3932 | 0 | 0.0045679 | 0 | 1 | 0 | Feeder | LONE OAK_861 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007306 |  | SOUTHERN | HEALDTON | 5321:WILDHORSE | WILDHORSE_2122 | 532122 | 2020-01-20 07:07 | 2020-01-20 07:10 | 2.93 | 35 | 0 | 102.6667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | RATLIFF CITY | 4770 WEST COUNTY LINE RD | CMI_MOMENTARY | YES | NO | NO | 860782 | 77585 | 6794 | 155 | 35 | 0.00011927 | 4.0661e-05 | 2.9333 | 1 | 0 | Feeder | WILDHORSE_2122 | Recloser | 0 | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-20 | 2020 |  | #N/A
J2001.007308 |  | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6022 | 836022 | 2020-01-20 07:19 | 2020-01-20 07:19 | 0 | 1232 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 4315 N COUNCIL RD | CMI_MOMENTARY | YES | NO | NO | 860782 | 128729 | 115983 | 5504 | 1231 | 0 | 0.0014313 | 0 | 1 | 0 | Feeder | WOODLAWN_6022 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-20 | 2020 |  | OK - 2022
J2001.007310 | PD-01202020-00015 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6022 | 836022 | 2020-01-20 07:24 | 2020-01-20 08:17 | 52.8 | 5 | 3 | 245.3333 | 4 | DETERIORATION | 21 | FUSE - TRANSFORMER | BETHANY | 3110 ALEXANDER LN | CMI_NORMAL | NO | NO | NO | 860782 | 128729 | 115983 | 5504 | 1231 | 0.00028501 | 5.8087e-06 | 49.0667 | 1 | 310 | Load | 18803 | Load | Tran1phOH | STEVEN GILES | 405-227-2802 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | OK - 2022
J2001.007312 | PD-01202020-00024 | SOUTHERN | ARDMORE | 5109:ARDMORE WEST | ARDMORE_WEST_929 | 510929 | 2020-01-20 07:34 | 2020-01-20 08:42 | 67.87 | 1 | 1 | 67.8667 | 4 | DETERIORATION | 20 | FUSE BARREL | ARDMORE | 77 + 12 2.5W | CMI_NORMAL | NO | NO | NO | 860782 | 77585 | 23583 | 1315 | 614 | 7.8843e-05 | 1.1617e-06 | 67.8667 | 1 | 310 | Load | 1132 | Load | Tran1phOH | RANDAL G CALLAWAY | 580-220-8449 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007313 | PD-01202020-00028 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1424 | 311424 | 2020-01-20 07:50 | 2020-01-20 08:34 | 43.73 | 1 | 1 | 40.9333 | 4 | DETERIORATION | 20 | FUSE BARREL | MUSKOGEE | ANTIQUES | CMI_NORMAL | NO | NO | NO | 860782 | 73994 | 33249 | 4566 | 798 | 4.7554e-05 | 1.1617e-06 | 40.9333 | 1 | 310 | Customer | 7704 | Load | TranOpenDelta | REID R WILLIAMS | 512-618-8800 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | OK - 2020
J2001.007314 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1862 | 941862 | 2020-01-20 07:52 | 2020-01-20 13:17 | 324.43 | 1 | 1 | 185.15 | 4 | DETERIORATION | 12 | POLE | LAMAR | LAMAR AR | CMI_PLANNED | YES | NO | NO | 860782 | 82180 | 7540 | 730 | 730 | 0.0002151 | 1.1617e-06 | 185.15 | 1 | 308 | Load | 1716 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | Ark - Series 2
J2001.007317 | PD-01202020-00038 | SOUTHERN | SULPHUR | 5705:SULPHUR | SULPHUR_529 | 570529 | 2020-01-20 07:59 | 2020-01-20 09:33 | 93.8 | 1 | 1 | 93.8 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SULPHUR | 1123 W 10TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 77585 | 6811 | 3631 | 1186 | 0.00010897 | 1.1617e-06 | 93.8 | 1 | 320 | Customer | 3964 | Load | Tran1phOH | CHAD A DOTSON | 405-488-5658 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2021
J2001.007327 | PD-01202020-00052 | NORTHEAST | MUSKOGEE | 3314:PORUM | PORUM_1421 | 331421 | 2020-01-20 08:04 | 2020-01-20 10:51 | 167.27 | 3 | 4 | 473.9 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | PORUM | SEMINOLE/MUSKOGEE+3RD, PORUM | CMI_NORMAL | NO | NO | NO | 860782 | 73994 | 33249 | 596 | 596 | 0.00055055 | 3.4852e-06 | 157.9667 | 1 | 310 | Load | 11785 | Load | Tran1phOH | JAMES MCDONALD | 405-361-7186 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | OK - 2022
J2001.007319 | PD-01202020-00047 | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-20 08:05 | 2020-01-20 09:27 | 82.2 | 1 | 2 | 36.6588 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSTANG | * FIELD STONE APTS - MUSTANG | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 128729 | 115983 | 18234 | 4429 | 4.2588e-05 | 1.1617e-06 | 36.6588 | 1 | 310 | Customer | 73238 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2022
J2001.007321 | PD-01202020-00049 | NORTHWEST | ENID | 4105:ENID | ENID_521 | 410521 | 2020-01-20 08:08 | 2020-01-20 10:30 | 142.32 | 31 | 9 | 2106.45 | 3 | DAMAGED BY PUBLIC | 23 | FUSE - PRIMARY | ENID | .5BS-MAPLE + MADISON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 53517 | 37578 | 1326 | 613 | 0.0024471 | 3.6014e-05 | 67.95 | 1 | 310 | Mainline | 2406 | Fuse | FuseOH | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | #N/A
J2001.007324 | PD-01202020-00051 | METRO EAST | EAST | 8411:ACORN | ACORN_1170 | 841170 | 2020-01-20 08:13 | 2020-01-20 09:31 | 77.9 | 1 | 1 | 77.9 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 8900 E HEFNER RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 114335 | 71175 | 1791 | 1091 | 9.0499e-05 | 1.1617e-06 | 77.9 | 1 | 320 | Load | 248200 | Load | 0 | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007323 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-01-20 08:14 | 2020-01-20 18:50 | 635.4 | 3 | 2 | 1789 | 4 | DETERIORATION | 12 | POLE | BIXBY | 141ST + MEMORIAL-WS | CMI_PLANNED | YES | NO | NO | 860782 | 73994 | 40745 | 2749 | 1439 | 0.0020783 | 3.4852e-06 | 596.3333 | 1 | 310 | Mainline | 62946 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | OK - 2021
J2001.007325 | PD-01202020-00053 | NORTHEAST | SAPULPA | 3220:KELLYVILLE | KELLYVILLE_2024 | 322024 | 2020-01-20 08:18 | 2020-01-20 11:48 | 210.05 | 1 | 1 | 210.05 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | SAPULPA | 1/4S OF TAFT ON MESA RD | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860782 | 73994 | 40745 | 2551 | 1580 | 0.00024402 | 1.1617e-06 | 210.05 | 1 | 310 | Customer | 45236 | Load | Tran1phOH | CONTRACTOR 5 DAVID ELLIOT INC | 918-639-5055 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2020
J2001.007331 | PD-01202020-00061 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5134 | 815134 | 2020-01-20 08:25 | 2020-01-20 09:21 | 56.15 | 1 | 1 | 51.7667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 8905 S.GRACE | CMI_NORMAL | NO | NO | NO | 860782 | 159086 | 102122 | 13933 | 2466 | 6.0139e-05 | 1.1617e-06 | 51.7667 | 1 | 310 | Load | 17800 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007337 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_861 | 830861 | 2020-01-20 08:37 | 2020-01-20 12:14 | 217.5 | 2 | 3 | 435 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | LOT 17 BLK 1 LONE OAK PARK | CMI_NORMAL | NO | NO | NO | 860782 | 168109 | 148297 | 19362 | 3932 | 0.00050535 | 2.3235e-06 | 217.5 | 1 | 310 | Secondary | 227836 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007342 |  | METRO WEST | WEST | 8158:SARA | SARA_5871 | 815871 | 2020-01-20 08:53 | 2020-01-20 09:33 | 40.38 | 11 | 4 | 319.275 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 1417 edinburg dr | CMI_PLANNED | YES | NO | NO | 860782 | 128729 | 115983 | 18234 | 5388 | 0.00037091 | 1.2779e-05 | 29.025 | 1 | 308 | Load | 63697 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2022
J2001.007344 | PD-01202020-00098 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2225 | 832225 | 2020-01-20 08:55 | 2020-01-20 09:52 | 57.23 | 1 | 3 | 57.2333 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | OKLAHOMA CITY | 2217 NW 23RD | CMI_NORMAL | NO | NO | NO | 860782 | 168109 | 148297 | 9172 | 2038 | 6.649e-05 | 1.1617e-06 | 57.2333 | 1 | 310 | Load | 365756 | Load | Tran3phPadWye | REX R WILSON | 405-535-4507 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | OK - 2021
J2001.007345 |  | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6523 | 836523 | 2020-01-20 08:58 | 2020-01-20 09:08 | 9.98 | 1 | 1 | 9.9833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7305 LYREWOOD LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 128729 | 115983 | 7420 | 2257 | 1.1598e-05 | 1.1617e-06 | 9.9833 | 1 | 310 | Customer | 38608 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2022
J2001.007348 | PD-01202020-00109 | METRO EAST | SHAWNEE | 7435:MISSION HILL | MISSION HILL 24 | 743524 | 2020-01-20 09:07 | 2020-01-20 10:49 | 102.28 | 1 | 1 | 102.2833 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | SHAWNEE | 2025 S GORDON COOPER DR | CMI_NORMAL | NO | NO | NO | 860782 | 114335 | 22099 | 948 | 948 | 0.00011883 | 1.1617e-06 | 102.2833 | 1 | 310 | Customer | 367478 | Load | Tran3phWye | BRYAN K TATUM | 405-659-0746 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | OK - 2021
J2001.007347 |  | NORTHEAST | MUSKOGEE | 3111:FIVE TRIBES | FIVE_TRIBES_1131 | 311131 | 2020-01-20 09:07 | 2020-01-20 09:14 | 6.6 | 1 | 1 | 6.6 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 610 MARRIETTA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 73994 | 33249 | 1682 | 817 | 7.6674e-06 | 1.1617e-06 | 6.6 | 1 | 310 | Customer | 6722 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-20 | 2020 |  | #N/A
J2001.007349 | PD-01202020-00101 | SOUTHERN | DURANT | 5504:BUTTERFIELD | BUTTERFIELD_429 | 550429 | 2020-01-20 09:13 | 2020-01-20 12:25 | 191.65 | 1 | 2 | 187 | 3 | DAMAGED BY PUBLIC | 31 | CONDUCTOR SERVICE - OH | DURANT | 2161 ENTERPRISE DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 77585 | 15482 | 3484 | 1272 | 0.00021724 | 1.1617e-06 | 187 | 1 | 310 | Load | 327190 | Load | TranOpenDelta | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007355 | PD-01202020-00116 | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2523 | 512523 | 2020-01-20 09:24 | 2020-01-20 11:40 | 135.53 | 1 | 1 | 135.5333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ARDMORE | STOBTOWN CH 1.5N .3W .1N | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 77585 | 23583 | 3305 | 960 | 0.00015745 | 1.1617e-06 | 135.5333 | 1 | 320 | Load | 30143 | Load | Tran1phOH | RANDAL G CALLAWAY | 580-220-8449 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2021
J2001.007357 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-20 09:28 | 2020-01-20 15:58 | 389.82 | 2 | 2 | 621.7 | 4 | DETERIORATION | 12 | POLE | LAVACA | 2805 S. HWY 96 | CMI_PLANNED | YES | NO | NO | 860782 | 82180 | 61160 | 2734 | 2122 | 0.00072225 | 2.3235e-06 | 310.85 | 1 | 308 | Tap | 197884 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | Ark - Series 2
J2001.007359 |  | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1122 | 511122 | 2020-01-20 09:30 | 2020-01-20 09:30 | 0.03 | 1205 | 0 | 40.1667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 3623 RED CEDAR RD | CMI_MOMENTARY | YES | NO | NO | 860782 | 77585 | 23583 | 2207 | 1206 | 4.6663e-05 | 0.0013999 | 0.033333 | 1 | 0 | Feeder | DRIPPING_SPRI_1122 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007365 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-20 09:40 | 2020-01-20 14:13 | 272.9 | 1 | 1 | 258.5167 | 4 | DETERIORATION | 12 | POLE | CLARKSVILLE | HARTMAN | CMI_PLANNED | YES | NO | NO | 860782 | 82180 | 7540 | 1504 | 1200 | 0.00030033 | 1.1617e-06 | 258.5167 | 1 | 308 | Load | 7303 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-20 | 2020 |  | Ark - Series 2
J2001.007366 | PD-01202020-00142 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2222 | 832222 | 2020-01-20 09:41 | 2020-01-20 10:26 | 44.72 | 1 | 1 | 44.7167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 4217 N.YOUNGS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 168109 | 148297 | 9172 | 1556 | 5.1949e-05 | 1.1617e-06 | 44.7167 | 1 | 310 | Customer | 49089 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | OK - 2022
J2001.007371 | PD-01202020-00160 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3621 | 853621 | 2020-01-20 09:49 | 2020-01-20 10:52 | 62.97 | 1 | 1 | 62.9667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1317 NE.16 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 168109 | 148297 | 5920 | 2165 | 7.3151e-05 | 1.1617e-06 | 62.9667 | 1 | 310 | Customer | 86 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2022
J2001.007377 |  | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2524 | 512524 | 2020-01-20 10:01 | 2020-01-20 11:51 | 109.23 | 5 | 4 | 171.9167 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | LONE GROVE | 14 SHORTY LN | CMI_PLANNED | YES | NO | NO | 860782 | 77585 | 23583 | 3305 | 999 | 0.00019972 | 5.8087e-06 | 34.3833 | 1 | 308 | Load | 360935 | Load | Tran1phPad | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007381 |  | SOUTHERN | HEALDTON | 5309:POOLEVILLE | POOLEVILLE_927 | 530927 | 2020-01-20 10:05 | 2020-01-20 11:45 | 99.73 | 2 | 0 | 168.0833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | 0 | 7-76 2S 4E SS | CMI_PLANNED | YES | NO | NO | 860782 | 77585 | 6794 | 400 | 141 | 0.00019527 | 2.3235e-06 | 84.0417 | 1 | 0 | Load | 24982 | Load | Tran3phWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007383 | PD-01202020-00165 | METRO SOUTH | SOUTH | 8722:MILLENNIUM | MILLENNIUM_2224 | 872224 | 2020-01-20 10:08 | 2020-01-20 10:59 | 50.97 | 1 | 1 | 48.4167 | 4 | DETERIORATION | 50 | CONNECTOR | NORMAN | LOT 7 BLK 3 SHADOWLAKE SEC 2 | CMI_NORMAL | NO | NO | NO | 860782 | 159086 | 56964 | 4205 | 639 | 5.6247e-05 | 1.1617e-06 | 48.4167 | 1 | 320 | Customer | 101517 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007387 | PD-01202020-00176 | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-01-20 10:11 | 2020-01-20 17:52 | 460.6 | 4 | 4 | 1779 | 3 | DAMAGED BY PUBLIC | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | Foxmor Estates | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 159086 | 56964 | 4239 | 3070 | 0.0020667 | 4.6469e-06 | 444.75 | 1 | 310 | Secondary | 258468 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007389 | PD-01202020-00170 | SOUTHERN | DURANT | 5512:COLBERT | COLBERT_1221 | 551221 | 2020-01-20 10:12 | 2020-01-20 14:00 | 227.78 | 1 | 2 | 217.1333 | 12 | POOR CONNECTION | 50 | CONNECTOR | CALERA | CURTIS AVE + S 1ST ST | CMI_NORMAL | NO | NO | NO | 860782 | 77585 | 15482 | 2166 | 895 | 0.00025225 | 1.1617e-06 | 217.1333 | 1 | 310 | Customer | 11601 | Load | TranOHDeltaSplitBank | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007390 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-20 10:15 | 2020-01-20 14:57 | 282.42 | 3 | 1 | 796.35 | 4 | DETERIORATION | 12 | POLE | ARKOMA | 421 SUMNER | CMI_PLANNED | YES | NO | NO | 860782 | 82180 | 61160 | 2934 | 875 | 0.00092515 | 3.4852e-06 | 265.45 | 1 | 308 | Load | 782 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-20 | 2020 |  | Ark - Series 2
J2001.007395 | PD-01202020-00180 | METRO SOUTH | SOUTH CENTRAL | 8194:WESTMOORE | WESTMOORE_9424 | 819424 | 2020-01-20 10:26 | 2020-01-20 12:16 | 110.25 | 1 | 1 | 105.9 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | VILLAS @ CASCATA LAKES SEC 1 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860782 | 159086 | 102122 | 8100 | 1644 | 0.00012303 | 1.1617e-06 | 105.9 | 1 | 310 | Customer | 231800 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007396 | PD-01202020-00179 | NORTHWEST | ENID | 4105:ENID | ENID_521 | 410521 | 2020-01-20 10:26 | 2020-01-20 10:57 | 30.87 | 1 | 1 | 30.8667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ENID | 1002 W Maine | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 53517 | 37578 | 1326 | 613 | 3.5859e-05 | 1.1617e-06 | 30.8667 | 1 | 320 | Load | 254373 | Load | Tran3phPadWye | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | #N/A
J2001.007402 | PD-01202020-00189 | SOUTHERN | PAULS VALLEY | 5620:PRAIRIE POINT | PRAIRIE_POINT_2022 | 562022 | 2020-01-20 10:42 | 2020-01-20 12:41 | 118.67 | 1 | 1 | 118.6667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | ELMORE CITY | 7 + 76,6N,2E,1N,.1E,NS | CMI_NORMAL | NO | NO | NO | 860782 | 77585 | 6206 | 607 | 38 | 0.00013786 | 1.1617e-06 | 118.6667 | 1 | 310 | Load | 27425 | Load | TranOpenDelta | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007401 | PD-01202020-00188 | METRO WEST | EL RENO | 8908:ROMAN NOSE | ROMAN_NOSE_847 | 890847 | 2020-01-20 10:43 | 2020-01-20 12:56 | 132.6 | 1 | 1 | 125.5667 | 22 | WIND | 17 | JUMPER | WATONGA | 83420 N2620 RD | CMI_NORMAL | NO | NO | NO | 860782 | 128729 | 12746 | 525 | 214 | 0.00014588 | 1.1617e-06 | 125.5667 | 1 | 310 | Load | 392361 | Load | Tran1phOH | [7 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2020
J2001.007403 | PD-01202020-00191 | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_621 | 550621 | 2020-01-20 10:45 | 2020-01-20 14:34 | 228.65 | 1 | 1 | 228.65 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DURANT | HWY 70/ WESTERN MEADOWS, 150E, 250N | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 77585 | 15482 | 6736 | 901 | 0.00026563 | 1.1617e-06 | 228.65 | 1 | 310 | Load | 360442 | Load | Tran3phWye | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007407 | PD-01202020-00204 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4823 | 824823 | 2020-01-20 10:55 | 2020-01-20 13:27 | 152.22 | 1 | 1 | 152.2167 | 3 | DAMAGED BY PUBLIC | 15 | METER - SECONDARY | OKLAHOMA CITY | 3024 SW.26 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 168109 | 148297 | 4191 | 1795 | 0.00017684 | 1.1617e-06 | 152.2167 | 1 | 310 | Customer | 20033 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2021
J2001.007408 | PD-01202020-00208 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5132 | 815132 | 2020-01-20 10:58 | 2020-01-20 11:41 | 43.43 | 2 | 2 | 75.55 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2836 SW.80 | CMI_NORMAL | NO | NO | NO | 860782 | 159086 | 102122 | 13933 | 2003 | 8.7769e-05 | 2.3235e-06 | 37.775 | 1 | 310 | Secondary | 25021 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007413 | PD-01202020-00211 | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-20 11:07 | 2020-01-20 11:47 | 40.23 | 1 | 1 | 30.95 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | HARTMAN | ON MAIN ST. - S. OF RR | CMI_NORMAL | NO | NO | NO | 860782 | 82180 | 7540 | 1504 | 1200 | 3.5956e-05 | 1.1617e-06 | 30.95 | 1 | 310 | Customer | 16548 | Load | TranOpenDelta | KRIS L HALMES | 479-430-9447 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-01-20 | 2020 |  | Ark - Series 2
J2001.007416 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-01-20 11:10 | 2020-01-20 11:54 | 43.72 | 9 | 11 | 370.05 | 5 | ELECTRICAL TRACKING | 2 | TRANSFORMER OH | OKLAHOMA CITY | 1608 NW.20 | CMI_PLANNED | YES | NO | NO | 860782 | 168109 | 148297 | 11100 | 2037 | 0.0004299 | 1.0456e-05 | 41.1167 | 1 | 310 | Load | 10379 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2021
J2001.007415 | PD-01202020-00218 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9923 | 829923 | 2020-01-20 11:14 | 2020-01-20 12:26 | 72.18 | 1 | 1 | 67.8833 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 7413 NW.6 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860782 | 128729 | 115983 | 9223 | 863 | 7.8862e-05 | 1.1617e-06 | 67.8833 | 1 | 310 | Customer | 34408 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007421 |  | ARKANSAS | OZARK | 9406:HELBERG | HELBERG_622 | 940622 | 2020-01-20 11:34 | 2020-01-20 12:14 | 40.17 | 1 | 1 | 40.1667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OZARK | 107 SO 10TH ST + COMMERCIAL ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 82180 | 7540 | 1720 | 886 | 4.6663e-05 | 1.1617e-06 | 40.1667 | 1 | 310 | Customer | 5143 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | Ark - Series 3
J2001.007435 | PD-01202020-00250 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9931 | 829931 | 2020-01-20 12:00 | 2020-01-20 12:42 | 41.58 | 1 | 1 | 24.2905 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 5001 NW 10TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 128729 | 115983 | 9223 | 2194 | 2.8219e-05 | 1.1617e-06 | 24.2905 | 1 | 320 | Customer | 42748 | Load | Tran1phPad | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007442 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-20 12:20 | 2020-01-20 15:49 | 208.68 | 1 | 1 | 200.4667 | 4 | DETERIORATION | 12 | POLE | CLARKSVILLE | 3M E-HARTMAN, 600 N-HWY 64 | CMI_PLANNED | YES | NO | NO | 860782 | 82180 | 7540 | 1504 | 1200 | 0.00023289 | 1.1617e-06 | 200.4667 | 1 | 308 | Load | 3066 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-20 | 2020 |  | Ark - Series 2
J2001.007443 | PD-01202020-00267 | SOUTHERN | DURANT | 5512:COLBERT | COLBERT_1222 | 551222 | 2020-01-20 12:22 | 2020-01-20 13:18 | 56.47 | 4 | 4 | 128.3333 | 4 | DETERIORATION | 20 | FUSE BARREL | COLBERT | RED RIVER MANOR .75S COLBERT | CMI_NORMAL | NO | NO | NO | 860782 | 77585 | 15482 | 2166 | 1271 | 0.00014909 | 4.6469e-06 | 32.0833 | 1 | 310 | Secondary | 28597 | Load | Tran1phPad | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007450 | PD-01202020-00286 | SOUTHERN | HEALDTON | 5319:FOX | FOX 21 | 531921 | 2020-01-20 12:34 | 2020-01-20 13:32 | 57.88 | 1 | 1 | 55.8167 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | HEALDTON | 76/53E,3W,.5N,ES | CMI_NORMAL | NO | NO | NO | 860782 | 77585 | 6794 | 706 | 341 | 6.4844e-05 | 1.1617e-06 | 55.8167 | 1 | 320 | Load | 28311 | Load | TranOpenDelta | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007452 |  | METRO NORTH | GUTHRIE | 8819:LIBERTY LAKE | LIBERTY_LAKE_1921 | 881921 | 2020-01-20 12:35 | 2020-01-20 13:42 | 67.42 | 1 | 1 | 57.0833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | GUTHRIE | 9620 S Coltrane RD | CMI_PLANNED | YES | NO | NO | 860782 | 168109 | 19812 | 3351 | 1525 | 6.6316e-05 | 1.1617e-06 | 57.0833 | 1 | 308 | Load | 404215 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007454 | PD-01202020-00278 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4035 | 834035 | 2020-01-20 12:39 | 2020-01-20 13:46 | 66.87 | 1 | 1 | 66.8667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | *140 E MACARTHUR-400 N HEFNER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 128729 | 115983 | 10841 | 1423 | 7.7681e-05 | 1.1617e-06 | 66.8667 | 1 | 310 | Customer | 73173 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007457 | PD-01202020-00283 | METRO WEST | WEST | 8158:SARA | SARA_5871 | 815871 | 2020-01-20 12:46 | 2020-01-20 15:57 | 190.68 | 3 | 3 | 477.4 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 10613 NW 17TH ST | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860782 | 128729 | 115983 | 18234 | 5388 | 0.00055461 | 3.4852e-06 | 159.1333 | 1 | 310 | Secondary | 302784 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2022
J2001.007462 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-20 12:54 | 2020-01-20 19:15 | 380.75 | 2 | 0 | 761.335 | 4 | DETERIORATION | 12 | POLE | ARKOMA | 104 BOON | CMI_PLANNED | YES | NO | NO | 860782 | 82180 | 61160 | 2934 | 875 | 0.00088447 | 2.3235e-06 | 380.6675 | 1 | 0 | Load | 7052 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-20 | 2020 |  | Ark - Series 2
J2001.007468 | PD-01202020-00302 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6121 | 836121 | 2020-01-20 13:09 | 2020-01-20 13:40 | 31.28 | 1 | 1 | 31.2833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3314 N.KENTUCKY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 168109 | 148297 | 11100 | 1638 | 3.6343e-05 | 1.1617e-06 | 31.2833 | 1 | 310 | Customer | 30971 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2021
J2001.007472 | PD-01202020-00298 | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2224 | 882224 | 2020-01-20 13:09 | 2020-01-20 19:13 | 364.47 | 20 | 18 | 3798.7667 | 3 | DAMAGED BY PUBLIC | 36 | CONDUCTOR PRIMARY - UG | EDMOND | S CEDAR CREEK + SOONER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 168109 | 19812 | 5386 | 1849 | 0.0044132 | 2.3235e-05 | 189.9383 | 1 | 311 | Mainline | 28808 | Fuse | FuseRiser | JASON CLARK | 405-420-5186 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007470 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-20 13:11 | 2020-01-20 16:22 | 191.18 | 1 | 0 | 191.1788 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | SW OF SUBSTATION | CMI_PLANNED | YES | NO | NO | 860782 | 82180 | 61160 | 2734 | 2122 | 0.0002221 | 1.1617e-06 | 191.1788 | 1 | 0 | Mainline | 100352 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | Ark - Series 2
J2001.007471 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-20 13:12 | 2020-01-20 13:18 | 6.27 | 2169 | 99 | 13616.2833 | 6 | HOT LINE HOLD ORDER | 56 | SCADA - LOCKOUT | FT SMITH | 4699 S ZERO ST | CMI_NORMAL | NO | NO | NO | 860782 | 82180 | 61160 | 2734 | 2122 | 0.015819 | 0.0025198 | 6.2777 | 1 | 310 | Feeder | CARNALL_2564 | Recloser | SubRecloser | [7 empty] | Other | N | SUBSTATION | 69kV | 2020-01-20 | 2020 |  | Ark - Series 2
J2001.007473 | PD-01202020-00299 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3624 | 853624 | 2020-01-20 13:16 | 2020-01-20 14:55 | 99.42 | 1 | 1 | 99.4167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1319.5 NE.6 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 168109 | 148297 | 5920 | 928 | 0.0001155 | 1.1617e-06 | 99.4167 | 1 | 320 | Customer | 48440 | Load | Tran1phOH | REX R WILSON | 405-535-4507 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007482 |  | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3422 | 843422 | 2020-01-20 13:26 | 2020-01-20 15:55 | 149.17 | 1 | 0 | 133.0833 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | NE.69 + 500 E-EASTERN | CMI_PLANNED | YES | NO | NO | 860782 | 168109 | 148297 | 1224 | 726 | 0.00015461 | 1.1617e-06 | 133.0833 | 1 | 0 | Mainline | 2577 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | #N/A
J2001.007488 | PD-01202020-00313 | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-20 13:29 | 2020-01-20 14:33 | 64.48 | 1 | 1 | 60.4667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | LAVACA | 3514 BUGSCUFFLE RD | CMI_NORMAL | NO | NO | NO | 860782 | 82180 | 61160 | 2734 | 2122 | 7.0246e-05 | 1.1617e-06 | 60.4667 | 1 | 310 | Load | 249237 | Load | Tran1phOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | Ark - Series 2
J2001.007494 | PD-01202020-00312 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5031 | 865031 | 2020-01-20 13:33 | 2020-01-20 14:55 | 81.9 | 1 | 1 | 81.9 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | MIDWEST CITY | 1110 BELL DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860782 | 114335 | 71175 | 8627 | 1597 | 9.5146e-05 | 1.1617e-06 | 81.9 | 1 | 320 | Customer | 8301 | Load | Tran1phOH | STEPHEN R MEADOWS | 405-641-5657 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2022
J2001.007492 | PD-01202020-00323 | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_523 | 320523 | 2020-01-20 13:33 | 2020-01-20 14:59 | 85.9 | 1 | 2 | 85.9 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | SAPULPA | PINE APT W ON MIKE ST. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 73994 | 40745 | 3840 | 1718 | 9.9793e-05 | 1.1617e-06 | 85.9 | 1 | 310 | Customer | 44057 | Load | Tran1phPad | CGI ADMIN | 918-261-6802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | OK - 2022
J2001.007499 | PD-01202020-00321 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2224 | 852224 | 2020-01-20 13:40 | 2020-01-20 16:34 | 173.6 | 1 | 1 | 125.5667 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | CHOCTAW | NE 10TH + KENT | CMI_NORMAL | NO | NO | NO | 860782 | 114335 | 71175 | 11628 | 1523 | 0.00014588 | 1.1617e-06 | 125.5667 | 1 | 310 | Load | 72184 | Load | Tran3phWye | STEPHEN R MEADOWS | 405-641-5657 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007500 | PD-01202020-00319 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6123 | 836123 | 2020-01-20 13:43 | 2020-01-20 14:52 | 69.35 | 1 | 1 | 69.35 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 839 W.EUBANKS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 168109 | 148297 | 11100 | 942 | 8.0566e-05 | 1.1617e-06 | 69.35 | 1 | 311 | Customer | 27162 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2020
J2001.007514 | PD-01202020-00344 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6524 | 836524 | 2020-01-20 13:53 | 2020-01-20 14:53 | 59.88 | 4 | 5 | 226.1 | 4 | DETERIORATION | 21 | FUSE - TRANSFORMER | WARR ACRES | 5429 NW.66 | CMI_NORMAL | NO | NO | NO | 860782 | 128729 | 115983 | 7420 | 1651 | 0.00026267 | 4.6469e-06 | 56.525 | 1 | 310 | Secondary | 23140 | Load | Tran1phOH | STEVEN GILES | 405-227-2802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007515 | PD-01202020-00338 | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2922 | 812922 | 2020-01-20 13:58 | 2020-01-20 15:39 | 101.43 | 3 | 3 | 240.15 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | SW.37 + GOFF | CMI_NORMAL | NO | NO | NO | 860782 | 159086 | 102122 | 6377 | 1137 | 0.00027899 | 3.4852e-06 | 80.05 | 1 | 310 | Secondary | 7445 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | #N/A
J2001.007524 |  | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_647 | 890647 | 2020-01-20 14:22 | 2020-01-20 14:27 | 4.83 | 1 | 1 | 2.0137 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | CANTON | 605 OWENS DRIVE | CMI_MOMENTARY | YES | NO | NO | 860782 | 128729 | 12746 | 1365 | 1070 | 2.3393e-06 | 1.1617e-06 | 2.0137 | 1 | 310 | Customer | 222231 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007526 | PD-01202020-00351 | NORTHWEST | WOODWARD | 4608:WOODWARD DISTR | WOODWARD_DIST_846 | 460846 | 2020-01-20 14:23 | 2020-01-20 18:04 | 220.77 | 1 | 1 | 211.6667 | 12 | POOR CONNECTION | 50 | CONNECTOR | VICI | VICI W-BUXTON,.5BS-BROADWAY | CMI_NORMAL | NO | NO | NO | 860782 | 53517 | 10419 | 1214 | 652 | 0.0002459 | 1.1617e-06 | 211.6667 | 1 | 320 | Customer | 10190 | Load | TranOpenDelta | ROY L THRASH | 580-334-5371 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2020
J2001.007527 | PD-01202020-00352 | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-01-20 14:26 | 2020-01-20 15:12 | 46.23 | 1 | 1 | 46.2333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BRANCH | NW 3D + A, BRANCH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 82180 | 61160 | 958 | 490 | 5.3711e-05 | 1.1617e-06 | 46.2333 | 1 | 310 | Customer | 6711 | Load | Tran1phOH | KRIS L HALMES | 479-430-9447 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 34.5/19.9kV | 2020-01-20 | 2020 |  | Ark - Series 2
J2001.007533 | PD-01202020-00353 | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_433 | 510433 | 2020-01-20 14:29 | 2020-01-20 16:01 | 91.75 | 1 | 2 | 77.65 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | ARDMORE | 910 6 NE. | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860782 | 77585 | 23583 | 2317 | 1258 | 9.0209e-05 | 1.1617e-06 | 77.65 | 1 | 311 | Customer | 2170 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007531 |  | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3729 | 833729 | 2020-01-20 14:30 | 2020-01-20 15:03 | 32.78 | 1 | 1 | 32.7833 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1013 NW.90 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 168109 | 148297 | 5759 | 1401 | 3.8086e-05 | 1.1617e-06 | 32.7833 | 1 | 310 | Customer | 672 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2021
J2001.007530 | PD-01202020-00354 | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-20 14:31 | 2020-01-20 17:14 | 162.67 | 1 | 1 | 10.25 | 4 | DETERIORATION | 50 | CONNECTOR | MUSTANG | 713 S.BROOKVIEW LN | CMI_NORMAL | NO | NO | NO | 860782 | 128729 | 115983 | 18234 | 4429 | 1.1908e-05 | 1.1617e-06 | 10.25 | 1 | 310 | Customer | 47123 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2022
J2001.007543 | PD-01202020-00363 | NORTHWEST | WOODWARD | 4616:NEWMAN AVE | NEWMAN_AVE_1641 | 461641 | 2020-01-20 14:55 | 2020-01-20 16:04 | 68.6 | 1 | 2 | 68.6 | 13 | PREMATURE FAILURE | 15 | METER - SECONDARY | SHATTUCK | 711 MAIN SHATTUCK | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860782 | 53517 | 10419 | 2012 | 2012 | 7.9695e-05 | 1.1617e-06 | 68.6 | 1 | 310 | Customer | 10969 | Load | Tran1phOH | ROY L THRASH | 580-334-5371 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | OK - 2020
J2001.007544 |  | SOUTHERN | HEALDTON | 5309:POOLEVILLE | POOLEVILLE_927 | 530927 | 2020-01-20 14:56 | 2020-01-20 15:29 | 33.12 | 1 | 0 | 31.1167 | 4 | DETERIORATION | 27 | CUTOUT | 0 | HWY 76 & RANCH RD 4.7E SS | CMI_PLANNED | YES | NO | NO | 860782 | 77585 | 6794 | 400 | 141 | 3.6149e-05 | 1.1617e-06 | 31.1167 | 1 | 0 | Load | 331566 | Load | Tran3phWye | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007558 | PD-01202020-00376 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_723 | 870723 | 2020-01-20 15:01 | 2020-01-20 18:24 | 202.72 | 83 | 31 | 13208.0667 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | NORMAN | 1505 PARKVIEW TERR | CMI_NORMAL | NO | NO | NO | 860782 | 159086 | 56964 | 11833 | 2044 | 0.015344 | 9.6424e-05 | 159.1333 | 1 | 310 | Mainline | 22049 | Fuse | FuseOH | CARL F KEMP | 405-618-8371 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007547 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_723 | 870723 | 2020-01-20 15:01 | 2020-01-20 15:01 | 0 | 1506 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | NORMAN | 1800 E IMHOFF RD | CMI_MOMENTARY | YES | NO | NO | 860782 | 159086 | 56964 | 11833 | 2044 | 0 | 0.0017496 | 0 | 1 | 0 | Mainline | 332700 | Recloser | Rec3phElectronic | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007554 |  | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8129 | 838129 | 2020-01-20 15:06 | 2020-01-20 15:06 | 0 | 1637 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 8323 W WILSHIRE | CMI_MOMENTARY | YES | NO | NO | 860782 | 128729 | 115983 | 8954 | 1043 | 0 | 0.0019018 | 0 | 1 | 0 | Mainline | DIVISION_8124T | Switch | SWITCH | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007553 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_723 | 870723 | 2020-01-20 15:08 | 2020-01-20 18:32 | 204.45 | 1 | 1 | 204.45 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | NORMAN | STINSON RESERVE APTS | CMI_NORMAL | NO | NO | NO | 860782 | 159086 | 56964 | 11833 | 2044 | 0.00023752 | 1.1617e-06 | 204.45 | 1 | 310 | Customer | 231058 | Load | Tran1phPad | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007565 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4024 | 834024 | 2020-01-20 15:26 | 2020-01-20 16:19 | 53.1 | 17 | 4 | 639.2 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | 5301 NW 123RD ST | CMI_PLANNED | YES | NO | NO | 860782 | 128729 | 115983 | 10841 | 1677 | 0.00074258 | 1.9749e-05 | 37.6 | 1 | 310 | Load | 222543 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007573 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9929 | 829929 | 2020-01-20 15:40 | 2020-01-20 15:53 | 13.83 | 1 | 1 | 13.8333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BETHANY | 7928 NW.21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 128729 | 115983 | 9223 | 2206 | 1.6071e-05 | 1.1617e-06 | 13.8333 | 1 | 310 | Customer | 38695 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007578 | PD-01202020-00385 | ARKANSAS | FORT SMITH | 9111:MASSARD | MASSARD_1129 | 911129 | 2020-01-20 15:43 | 2020-01-20 19:13 | 209.5 | 18 | 20 | 3351 | 4 | DETERIORATION | 1 | TRANSFORMER UG | FORT SMITH | SO.66 + FRESNO | CMI_NORMAL | NO | NO | NO | 860782 | 82180 | 61160 | 4984 | 356 | 0.003893 | 2.0911e-05 | 186.1667 | 1 | 310 | Mainline | 6575 | Fuse | FuseRiser | DWAIN C CAUGHERN | 479-459-0231 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-20 | 2020 |  | Ark - Series 3
J2001.007576 |  | ARKANSAS | FORT SMITH | 9111:MASSARD | MASSARD_1129 | 911129 | 2020-01-20 15:43 | 2020-01-20 15:43 | 0 | 356 | 0 | 0 | 4 | DETERIORATION | 55 | SCADA - CIRCUIT TRIP | FT SMITH | 8712 HORAN DR | CMI_MOMENTARY | YES | NO | NO | 860782 | 82180 | 61160 | 4984 | 356 | 0 | 0.00041358 | 0 | 1 | 0 | Feeder | MASSARD_1129 | Recloser | SubRecloser | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-20 | 2020 |  | Ark - Series 3
J2001.007594 | PD-01202020-00398 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-20 16:10 | 2020-01-20 20:58 | 287.65 | 1 | 2 | 47.5833 | 11 | OVERLOAD | 2 | TRANSFORMER OH | MOUNTAINBURG | 5M N MTN ON HWY 71 + 3/4M W. | CMI_NORMAL | NO | NO | NO | 860782 | 82180 | 61160 | 3788 | 2584 | 5.5279e-05 | 1.1617e-06 | 47.5833 | 1 | 310 | Load | 16670 | Load | Tran1phOH | DWAIN C CAUGHERN | 479-459-0231 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-20 | 2020 |  | Ark - Series 2
J2001.007595 | PD-01202020-00397 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3021 | 743021 | 2020-01-20 16:11 | 2020-01-20 16:37 | 25.7 | 1 | 1 | 25.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SHAWNEE | 707 N.UNION | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 114335 | 22099 | 6641 | 1701 | 2.9857e-05 | 1.1617e-06 | 25.7 | 1 | 320 | Customer | 4012 | Load | Tran1phOH | BRYAN K TATUM | 405-659-0746 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2021
J2001.007598 | PD-01202020-00405 | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1024 | 311024 | 2020-01-20 16:12 | 2020-01-20 17:15 | 63.48 | 7 | 9 | 410.7833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MUSKOGEE | 2217 HAYES | CMI_NORMAL | NO | NO | NO | 860782 | 73994 | 33249 | 2902 | 1393 | 0.00047722 | 8.1321e-06 | 58.6833 | 1 | 310 | Load | 5706 | Load | Tran1phOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | OK - 2020
J2001.007592 |  | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1024 | 311024 | 2020-01-20 16:12 | 2020-01-20 16:12 | 0 | 1393 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MUSKOGEE | 1541 COUNTRY CLUB PLACE | CMI_MOMENTARY | YES | NO | NO | 860782 | 73994 | 33249 | 2902 | 1393 | 0 | 0.0016183 | 0 | 1 | 0 | Feeder | RIVERSIDE_1024 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-20 | 2020 |  | OK - 2020
J2001.007599 |  | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2029 | 862029 | 2020-01-20 16:19 | 2020-01-20 16:24 | 5.33 | 1 | 1 | 5.3333 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 3229 S HIGH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 159086 | 102122 | 4744 | 982 | 6.1959e-06 | 1.1617e-06 | 5.3333 | 1 | 310 | Customer | 25171 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007602 |  | SOUTHERN | HEALDTON | 5309:POOLEVILLE | POOLEVILLE_927 | 530927 | 2020-01-20 16:28 | 2020-01-20 17:06 | 37.78 | 1 | 0 | 30.8667 | 4 | DETERIORATION | 12 | POLE | 0 | 76 + POOLEVILLE RD,4.9E,SS | CMI_PLANNED | YES | NO | NO | 860782 | 77585 | 6794 | 400 | 141 | 3.5859e-05 | 1.1617e-06 | 30.8667 | 1 | 0 | Load | 26731 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007607 |  | ARKANSAS | FORT SMITH | 9508:WHITESIDE | WHITESIDE_822 | 950822 | 2020-01-20 16:51 | 2020-01-20 18:22 | 90.53 | 1 | 1 | 36.6833 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | VAN BUREN | 4TH ST. ON RIVER | CMI_PLANNED | YES | NO | NO | 860782 | 82180 | 61160 | 1919 | 209 | 4.2616e-05 | 1.1617e-06 | 36.6833 | 1 | 308 | Load | 13309 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-20 | 2020 |  | Ark - Series 2
J2001.007608 | PD-01202020-00420 | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-01-20 16:52 | 2020-01-20 18:08 | 76.28 | 1 | 2 | 70.4667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | EL RENO | 604 LYNN DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860782 | 128729 | 12746 | 6937 | 1823 | 8.1864e-05 | 1.1617e-06 | 70.4667 | 1 | 320 | Customer | 63954 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007612 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7424 | 847424 | 2020-01-20 17:01 | 2020-01-20 17:08 | 7.3 | 1 | 1 | 7.3 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4915 N.KELLEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 168109 | 148297 | 6155 | 2197 | 8.4807e-06 | 1.1617e-06 | 7.3 | 1 | 310 | Customer | 4542 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2020
J2001.007613 | PD-01202020-00422 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6121 | 836121 | 2020-01-20 17:08 | 2020-01-20 19:43 | 154.93 | 1 | 1 | 154.4833 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | OKLAHOMA CITY | 1115 NW.34 | CMI_NORMAL | NO | NO | NO | 860782 | 168109 | 148297 | 11100 | 1638 | 0.00017947 | 1.1617e-06 | 154.4833 | 1 | 320 | Customer | 1925 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2021
J2001.007615 |  | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3729 | 833729 | 2020-01-20 17:10 | 2020-01-20 17:13 | 3.2 | 1 | 1 | 3.2 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1013 NW.90 | CMI_MOMENTARY | YES | NO | NO | 860782 | 168109 | 148297 | 5759 | 1401 | 3.7176e-06 | 1.1617e-06 | 3.2 | 1 | 310 | Customer | 672 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2021
J2001.007621 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1325 | 911325 | 2020-01-20 17:16 | 2020-01-20 22:13 | 296.4 | 2 | 2 | 565.6167 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 5820 TOWSON, N-S.ZERO ST. | CMI_PLANNED | YES | NO | NO | 860782 | 82180 | 61160 | 1455 | 216 | 0.0006571 | 2.3235e-06 | 282.8083 | 1 | 308 | Load | 5192 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | Ark - Series 2
J2001.007617 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7424 | 847424 | 2020-01-20 17:20 | 2020-01-20 17:26 | 5.8 | 1 | 1 | 5.8 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4915 N.KELLEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 168109 | 148297 | 6155 | 2197 | 6.7381e-06 | 1.1617e-06 | 5.8 | 1 | 310 | Customer | 4542 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | OK - 2020
J2001.007620 |  | ARKANSAS | FORT SMITH | 9111:MASSARD | MASSARD_1129 | 911129 | 2020-01-20 17:27 | 2020-01-20 19:19 | 112.3 | 1 | 1 | 21.5333 | 4 | DETERIORATION | 1 | TRANSFORMER UG | FORT SMITH | SO.68 CI == SUNCHASE ADDN | CMI_NORMAL | NO | NO | NO | 860782 | 82180 | 61160 | 4984 | 356 | 2.5016e-05 | 1.1617e-06 | 21.5333 | 1 | 310 | Customer | 16853 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-20 | 2020 |  | Ark - Series 3
J2001.007623 | PD-01202020-00424 | NORTHEAST | SAPULPA | 7610:PRINCEVILLE | PRINCEVILLE_1021 | 761021 | 2020-01-20 17:29 | 2020-01-20 19:00 | 91.03 | 1 | 1 | 91.0333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | BRISTOW | 2S 1E HWY33 + 48 | CMI_NORMAL | NO | NO | NO | 860782 | 73994 | 40745 | 304 | 304 | 0.00010576 | 1.1617e-06 | 91.0333 | 1 | 310 | Load | 22007 | Load | Tran1phOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | #N/A
J2001.007632 | PD-01202020-00430 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_524 | 510524 | 2020-01-20 18:08 | 2020-01-20 19:24 | 75.8 | 1 | 1 | 75.8 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ARDMORE | 909 C ST SE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 77595 | 23587 | 4778 | 1435 | 8.8059e-05 | 1.1617e-06 | 75.8 | 1 | 310 | Customer | 9555 | Load | Tran1phOH | DAVID TAYLOR | 580-574-4517 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | OK - 2021
J2001.007633 |  | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5624 | 865624 | 2020-01-20 18:14 | 2020-01-24 13:35 | 5480.77 | 2 | 0 | 10961.5492 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1/3MN I-240 E/SUNNYLN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 159101 | 102133 | 2751 | 112 | 0.012734 | 2.3235e-06 | 5480.7746 | 1 | 0 | Mainline | 5501 | Fuse | FuseRiser | Crew | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007635 | PD-01202020-00432 | METRO EAST | SHAWNEE | 7412:PEARSON | PEARSON 21 | 741221 | 2020-01-20 18:16 | 2020-01-20 19:33 | 77.22 | 1 | 1 | 77.2167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ST. LOUIS | 1/4MN ST.LOUIS STORE WS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 114346 | 22101 | 677 | 677 | 8.9705e-05 | 1.1617e-06 | 77.2167 | 1 | 310 | Customer | 21790 | Load | Tran1phOH | ADAM CLARK | 580-310-8924 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | OK - 2021
J2001.007643 | PD-01202020-00438 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1421 | 311421 | 2020-01-20 18:46 | 2020-01-20 20:38 | 112.28 | 6 | 10 | 584.9 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | MUSKOGEE | 2202 N.36 | CMI_NORMAL | NO | NO | NO | 860782 | 74014 | 33256 | 4567 | 1104 | 0.0006795 | 6.9704e-06 | 97.4833 | 1 | 310 | Load | 11849 | Load | Tran1phPad | CONTRACTOR 5 DAVID ELLIOT INC | 918-639-5055 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | #N/A
J2001.007644 | PD-01202020-00434 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3624 | 853624 | 2020-01-20 18:53 | 2020-01-20 19:41 | 48.28 | 1 | 1 | 48.2833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1319.5 NE.6 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 168127 | 148311 | 5922 | 928 | 5.6092e-05 | 1.1617e-06 | 48.2833 | 1 | 310 | Customer | 48440 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-20 | 2020 |  | #N/A
J2001.007667 |  | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1424 | 311424 | 2020-01-20 20:40 | 2020-01-20 20:48 | 8.03 | 798 | 89 | 6410.6 | 3 | DAMAGED BY PUBLIC | 12 | POLE | MUSKOGEE | 2612 TENNYSON | CMI_PLANNED | YES | NO | NO | 860782 | 74014 | 33256 | 4567 | 798 | 0.0074474 | 0.00092706 | 8.0333 | 1 | 310 | Feeder | TENNYSON_1424 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-20 | 2020 |  | OK - 2020
J2001.007670 | PD-01202020-00458 | NORTHEAST | MUSKOGEE | 3111:FIVE TRIBES | FIVE_TRIBES_1131 | 311131 | 2020-01-20 20:48 | 2020-01-20 21:32 | 44.15 | 1 | 1 | 44.15 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MUSKOGEE | 1230 S.6 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 74014 | 33256 | 1682 | 817 | 5.1291e-05 | 1.1617e-06 | 44.15 | 1 | 310 | Customer | 5680 | Load | Tran1phOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-20 | 2020 |  | #N/A
J2001.007673 |  | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1421 | 311421 | 2020-01-20 21:02 | 2020-01-20 21:03 | 0.9 | 6 | 0 | 4.9987 | 1 | CANCELLED | 57 | CANCELLED | MUSKOGEE | 2202 N.36 | CMI_MOMENTARY | YES | NO | NO | 860782 | 74014 | 33256 | 4567 | 1104 | 5.8072e-06 | 6.9704e-06 | 0.83312 | 1 | 0 | Load | 11849 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | #N/A
J2001.007682 | PD-01202020-00462 | SOUTHERN | HEALDTON | 5306:COUNTY LINE | COUNTY LINE 22 | 530622 | 2020-01-20 21:19 | 2020-01-20 23:45 | 146.08 | 1 | 1 | 146.0833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | HENNEPIN | HENNEPIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860782 | 77595 | 6795 | 755 | 413 | 0.00016971 | 1.1617e-06 | 146.0833 | 1 | 320 | Load | 17350 | Load | Tran1phOH | GARRID H BROWN | 405-207-3948 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-20 | 2020 |  | #N/A
J2001.007710 | PD-01212020-00011 | METRO SOUTH | SOUTH | 8722:MILLENNIUM | MILLENNIUM_2222 | 872222 | 2020-01-21 03:47 | 2020-01-21 05:32 | 104.98 | 1 | 1 | 4.1452 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | NORMAN | 1049 12th Av NE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 159101 | 56968 | 4205 | 738 | 4.815e-06 | 1.1616e-06 | 4.1452 | 1 | 320 | Customer | 331702 | Load | Tran3phPadWye | DARREN L STOCKTON | 918-777-1697 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007721 | PD-01212020-00016 | METRO EAST | SEMINOLE | 7508:EMAHAKA | EMAHAKA 21 | 750821 | 2020-01-21 05:22 | 2020-01-21 08:18 | 175.67 | 1 | 1 | 172.2 | 4 | DETERIORATION | 2 | TRANSFORMER OH | WEWOKA | 1MS HWY 59 & HWY 270 | CMI_NORMAL | NO | NO | NO | 860892 | 114346 | 13602 | 253 | 253 | 0.00020003 | 1.1616e-06 | 172.2 | 1 | 310 | Load | 170570 | Load | Tran1phOH | AUSTIN WELLIVER | 405-221-0200 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | #N/A
J2001.007737 | PD-01212020-00017 | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-21 06:13 | 2020-01-21 10:50 | 277.02 | 5 | 4 | 1347.3333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | MUSTANG | L18,B3-LAKE VIEW LANE | CMI_NORMAL | NO | NO | NO | 860892 | 128756 | 116002 | 18239 | 4429 | 0.001565 | 5.8079e-06 | 269.4667 | 1 | 310 | Load | 87421 | Load | Tran1phOH | JAMES CALDWELL | 405-973-6233 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | OK - 2022
J2001.007742 |  | METRO NORTH | GUTHRIE | 8814:PINE STREET | PINE_STREET_1429 | 881429 | 2020-01-21 06:42 | 2020-01-21 06:49 | 6.87 | 1 | 1 | 6.8667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | GUTHRIE | 4129 SEACREST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 168127 | 19816 | 3101 | 1713 | 7.9762e-06 | 1.1616e-06 | 6.8667 | 1 | 310 | Load | 209924 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007745 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_863 | 830863 | 2020-01-21 06:47 | 2020-01-21 07:12 | 24.35 | 1 | 1 | 24.35 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | .5MW OF PENN + NW.142 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 168127 | 148311 | 19363 | 1672 | 2.8285e-05 | 1.1616e-06 | 24.35 | 1 | 310 | Customer | 69766 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007749 | PD-01212020-00022 | METRO SOUTH | SOUTH CENTRAL | 8194:WESTMOORE | WESTMOORE_9421 | 819421 | 2020-01-21 07:14 | 2020-01-21 08:44 | 90.02 | 1 | 1 | 90.0167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2220 WHITBOURNE PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 159101 | 102133 | 8101 | 1426 | 0.00010456 | 1.1616e-06 | 90.0167 | 1 | 310 | Customer | 52914 | Load | Tran1phPad | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007750 | PD-01212020-00019 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-01-21 07:20 | 2020-01-21 11:02 | 222.42 | 1 | 2 | 222.4167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | CHOCTAW | 3795 WILD CANARY DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 114346 | 71181 | 11628 | 3534 | 0.00025836 | 1.1616e-06 | 222.4167 | 1 | 320 | Customer | 61872 | Load | Tran1phPad | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007759 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-01-21 07:50 | 2020-01-21 17:07 | 556.95 | 3 | 1 | 687 | 4 | DETERIORATION | 12 | POLE | BIXBY | 141ST + MEMORIAL-WS | CMI_PLANNED | YES | NO | NO | 860892 | 74014 | 40758 | 2749 | 1439 | 0.00079801 | 3.4848e-06 | 229 | 1 | 308 | Mainline | 62946 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | OK - 2021
J2001.007762 | PD-01212020-00028 | METRO EAST | EAST | 8417:ROUND BARN | ROUND_BARN_1723 | 841723 | 2020-01-21 07:56 | 2020-01-21 10:27 | 150.85 | 2 | 2 | 295.0167 | 5 | ELECTRICAL TRACKING | 27 | CUTOUT | ARCADIA | 301 N.LEE | CMI_NORMAL | NO | NO | NO | 860892 | 114346 | 71181 | 1009 | 1009 | 0.00034269 | 2.3232e-06 | 147.5083 | 1 | 310 | Load | 29783 | Load | Tran1phOH | JASON CLARK | 405-420-5186 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007765 | PD-01212020-00033 | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-01-21 08:11 | 2020-01-21 10:45 | 154.48 | 2 | 3 | 153.0667 | 13 | PREMATURE FAILURE | 36 | CONDUCTOR PRIMARY - UG | EL RENO | 5MN FOREMAN,2MW HWY-81 | CMI_NORMAL | NO | NO | NO | 860892 | 128756 | 12754 | 6942 | 1823 | 0.0001778 | 2.3232e-06 | 76.5333 | 1 | 310 | Tap | 2143 | Fuse | FuseRiser | BRENTON DOWNES | 580-450-0056 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007769 | PD-01212020-00043 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7429 | 847429 | 2020-01-21 08:15 | 2020-01-21 08:47 | 31.57 | 1 | 1 | 25.3589 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 2309 E.MADISON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 168127 | 148311 | 6158 | 680 | 2.9456e-05 | 1.1616e-06 | 25.3589 | 1 | 310 | Customer | 6347 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | OK - 2022
J2001.007768 | PD-01212020-00039 | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-01-21 08:16 | 2020-01-21 11:36 | 200.1 | 1 | 1 | 74.2833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | EL RENO | 604 LYNN DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 128756 | 12754 | 6942 | 1823 | 8.6286e-05 | 1.1616e-06 | 74.2833 | 1 | 320 | Customer | 63954 | Load | Tran1phPad | JOSH BLACK | 405-403-9382 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007775 | PD-01212020-00059 | METRO NORTH | GUTHRIE | 8814:PINE STREET | PINE_STREET_1429 | 881429 | 2020-01-21 08:34 | 2020-01-21 09:25 | 51.32 | 1 | 1 | 51.3167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | GUTHRIE | 4129 SEACREST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 168127 | 19816 | 3101 | 1713 | 5.9609e-05 | 1.1616e-06 | 51.3167 | 1 | 310 | Load | 209924 | Load | Tran1phOH | KELLEY D WATSON | 405-763-8148 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007776 | PD-01212020-00071 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1926 | 851926 | 2020-01-21 08:37 | 2020-01-21 09:43 | 66.43 | 1 | 1 | 51.2833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MIDWEST CITY | 9800 NE.21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 114346 | 71181 | 12441 | 2125 | 5.957e-05 | 1.1616e-06 | 51.2833 | 1 | 310 | Customer | 40763 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | OK - 2021
J2001.007780 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3633 | 833633 | 2020-01-21 08:47 | 2020-01-21 08:55 | 8.08 | 1 | 1 | 8.0833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | THE VILLAGE | 10401 N PENNSYLVANIA AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 168127 | 148311 | 8789 | 4 | 9.3895e-06 | 1.1616e-06 | 8.0833 | 1 | 310 | Customer | 59273 | Load | Tran3phPadWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007781 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-01-21 08:49 | 2020-01-21 13:57 | 308 | 3 | 2 | 882.3 | 4 | DETERIORATION | 12 | POLE | HARTMAN | 262 CR 2260 | CMI_PLANNED | YES | NO | NO | 860892 | 82188 | 7542 | 1505 | 1201 | 0.0010249 | 3.4848e-06 | 294.1 | 1 | 308 | Load | 8672 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-21 | 2020 |  | Ark - Series 2
J2001.007782 | PD-01212020-00088 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3722 | 833722 | 2020-01-21 08:49 | 2020-01-21 10:28 | 98.6 | 15 | 4 | 1318.5 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 1206 NW.83 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860892 | 168127 | 148311 | 5760 | 1109 | 0.0015316 | 1.7424e-05 | 87.9 | 1 | 310 | Load | 8996 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | OK - 2022
J2001.007783 |  | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 21 | 570821 | 2020-01-21 08:50 | 2020-01-21 08:59 | 8.62 | 1 | 1 | 8.6167 | 1 | CANCELLED | 6 | LIGHTING - STREET | DAVIS | 602 E.MAIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 77595 | 6811 | 1858 | 903 | 1.0009e-05 | 1.1616e-06 | 8.6167 | 1 | 310 | Customer | 78 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | OK - 2021
J2001.007784 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-21 08:54 | 2020-01-21 10:29 | 94.68 | 2 | 0 | 187.3833 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 501 S.U | CMI_PLANNED | YES | NO | NO | 860892 | 82188 | 61166 | 2934 | 875 | 0.00021766 | 2.3232e-06 | 93.6917 | 1 | 0 | Load | 7235 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-21 | 2020 |  | Ark - Series 2
J2001.007785 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1862 | 941862 | 2020-01-21 08:54 | 2020-01-21 16:21 | 446.95 | 1 | 1 | 444.3333 | 4 | DETERIORATION | 12 | POLE | LAMAR | LAMAR AR 72846 | CMI_PLANNED | YES | NO | NO | 860892 | 82188 | 7542 | 730 | 730 | 0.00051613 | 1.1616e-06 | 444.3333 | 1 | 308 | Load | 105 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | Ark - Series 2
J2001.007786 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-21 08:54 | 2020-01-21 10:28 | 93.53 | 3 | 2 | 274.3 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 328 S.U,3 POLE E-STATE LINE RD | CMI_PLANNED | YES | NO | NO | 860892 | 82188 | 61166 | 2934 | 875 | 0.00031862 | 3.4848e-06 | 91.4333 | 1 | 308 | Load | 5100 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-21 | 2020 |  | Ark - Series 2
J2001.007787 |  | NORTHWEST | ENID | 4135:SO 4TH ST | SO_4TH_ST_3522 | 413522 | 2020-01-21 09:06 | 2020-01-21 09:14 | 8.1 | 1 | 1 | 8.1 | 1 | CANCELLED | 6 | LIGHTING - STREET | ENID | 621 E SOUTHGATE RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 53521 | 37580 | 3094 | 1483 | 9.4088e-06 | 1.1616e-06 | 8.1 | 1 | 310 | Load | 377935 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007788 |  | METRO NORTH | GUTHRIE | 8813:FITZGERALD CR | FITZGERALD_CR_1342 | 881342 | 2020-01-21 09:08 | 2020-01-21 12:33 | 205.02 | 1 | 2 | 111.75 | 4 | DETERIORATION | 12 | POLE | GUTHRIE | 4MNCOLLEGE 4MEPINE | CMI_PLANNED | YES | NO | NO | 860892 | 168127 | 19816 | 1045 | 808 | 0.00012981 | 1.1616e-06 | 111.75 | 1 | 310 | Mainline | 3123 | Switch | SwitchOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007790 | PD-01212020-00103 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7029 | 817029 | 2020-01-21 09:10 | 2020-01-21 09:43 | 33.45 | 1 | 2 | 10.2676 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 9600 S.SHIELDS BLVD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 159101 | 102133 | 9939 | 1756 | 1.1927e-05 | 1.1616e-06 | 10.2676 | 1 | 310 | Customer | 78306 | Load | Tran1phPad | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | OK - 2022
J2001.007792 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-21 09:14 | 2020-01-21 13:47 | 273.07 | 1 | 1 | 223.2 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 25 ST CHAFFEE | CMI_PLANNED | YES | NO | NO | 860892 | 82188 | 61166 | 2735 | 2123 | 0.00025927 | 1.1616e-06 | 223.2 | 1 | 308 | Load | 200852 | Load | Tran3phWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | Ark - Series 2
J2001.007795 |  | METRO NORTH | NORTH | 8535:OU MED CENTER | OU_MEDICAL_CEN_3572 | 853572 | 2020-01-21 09:21 | 2020-01-21 14:37 | 315.97 | 1 | 0 | 315.45 | 1 | CANCELLED | 1 | TRANSFORMER UG | OKLAHOMA CITY | In the alley between NW 5th and 6th | CMI_PLANNED | YES | NO | NO | 860892 | 168127 | 148311 | 524 | 498 | 0.00036642 | 1.1616e-06 | 315.45 | 1 | 0 | Mainline | 415111 | Fuse | FuseRiser | Crew | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007799 | PD-01212020-00131 | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_724 | 510724 | 2020-01-21 09:22 | 2020-01-21 11:39 | 136.82 | 4 | 5 | 499.8 | 4 | DETERIORATION | 50 | CONNECTOR | ARDMORE | 1418 W.BROADWAY | CMI_NORMAL | NO | NO | NO | 860892 | 77595 | 23587 | 4509 | 1625 | 0.00058056 | 4.6463e-06 | 124.95 | 1 | 310 | Load | 12327 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | #N/A
J2001.007801 | PD-01212020-00119 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4122 | 814122 | 2020-01-21 09:23 | 2020-01-21 10:12 | 49.13 | 7 | 5 | 338.5667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 332 SE.50 | CMI_NORMAL | NO | NO | NO | 860892 | 159101 | 102133 | 5808 | 1271 | 0.00039327 | 8.1311e-06 | 48.3667 | 1 | 310 | Load | 1952 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | #N/A
J2001.007796 |  | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4122 | 814122 | 2020-01-21 09:23 | 2020-01-21 09:23 | 0 | 1271 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 5203 S SAGE AVE | CMI_MOMENTARY | YES | NO | NO | 860892 | 159101 | 102133 | 5808 | 1271 | 0 | 0.0014764 | 0 | 1 | 0 | Feeder | SAGE_4122 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-21 | 2020 |  | #N/A
J2001.007798 | PD-01212020-00115 | METRO EAST | SEMINOLE | 7208:CYPRESS | CYPRESS_822 | 720822 | 2020-01-21 09:23 | 2020-01-21 10:39 | 75.73 | 1 | 1 | 75.7333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | HOLDENVILLE | ON 3RD EAST OF TRE-VYN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 114346 | 13602 | 2520 | 1432 | 8.7971e-05 | 1.1616e-06 | 75.7333 | 1 | 310 | Customer | 18106 | Load | Tran1phOH | DELBERT HISAW | 405-683-1721 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | OK - 2020
J2001.007804 | PD-01212020-00132 | SOUTHERN | SULPHUR | 5712:JOLLYVILLE | JOLLYVILLE_1264 | 571264 | 2020-01-21 09:30 | 2020-01-21 11:29 | 119.43 | 1 | 1 | 119.4333 | 13 | PREMATURE FAILURE | 47 | ARRESTOR OH | DAVIS | DAVIS PUMP UNIT | CMI_NORMAL | NO | NO | NO | 860892 | 77595 | 6811 | 372 | 262 | 0.00013873 | 1.1616e-06 | 119.4333 | 1 | 310 | Customer | 12295 | Load | Tran1phOH | GARRID H BROWN | 405-207-3948 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007815 | PD-01212020-00140 | METRO WEST | WEST | 8222:CZECH HALL | CZECH_HALL_2224 | 822224 | 2020-01-21 09:42 | 2020-01-21 11:58 | 135.8 | 1 | 2 | 130.7333 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | YUKON | 601 VANDAMENT | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860892 | 128756 | 116002 | 8603 | 1332 | 0.00015186 | 1.1616e-06 | 130.7333 | 1 | 321 | Customer | 34416 | Load | TranOpenDelta | STEVEN GILES | 405-227-2802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007814 | PD-01212020-00143 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1922 | 851922 | 2020-01-21 09:43 | 2020-01-21 12:34 | 170.55 | 1 | 1 | 170.55 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MIDWEST CITY | CRESCENT CIRCLE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 114346 | 71181 | 12441 | 1795 | 0.00019811 | 1.1616e-06 | 170.55 | 1 | 310 | Customer | 59434 | Load | Tran1phPad | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007820 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_722 | 870722 | 2020-01-21 09:50 | 2020-01-21 11:55 | 125 | 3 | 2 | 102.6 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | NORMAN | 650 HWY 9 | CMI_PLANNED | YES | NO | NO | 860892 | 159101 | 56968 | 11834 | 1582 | 0.00011918 | 3.4848e-06 | 34.2 | 1 | 308 | Mainline | 205124 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007823 |  | NORTHEAST | MUSKOGEE | 3111:FIVE TRIBES | FIVE_TRIBES_1129 | 311129 | 2020-01-21 09:56 | 2020-01-21 13:26 | 210.22 | 3 | 3 | 524.3 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | MUSKOGEE | HILLDALE HIGH SCHOOL | CMI_PLANNED | YES | NO | NO | 860892 | 74014 | 33256 | 1682 | 865 | 0.00060902 | 3.4848e-06 | 174.7667 | 1 | 308 | Load | 250306 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-21 | 2020 |  | #N/A
J2001.007824 |  | NORTHEAST | MUSKOGEE | 3111:FIVE TRIBES | FIVE_TRIBES_1129 | 311129 | 2020-01-21 09:56 | 2020-01-21 13:27 | 210.27 | 1 | 1 | 174.5667 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | MUSKOGEE | HILLDALE HIGH SCHOOL SB FIELD | CMI_PLANNED | YES | NO | NO | 860892 | 74014 | 33256 | 1682 | 865 | 0.00020277 | 1.1616e-06 | 174.5667 | 1 | 308 | Load | 19362 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-21 | 2020 |  | #N/A
J2001.007836 |  | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3624 | 853624 | 2020-01-21 10:16 | 2020-01-21 10:16 | 0 | 927 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 1200 NE 4TH ST | CMI_MOMENTARY | YES | NO | NO | 860892 | 168127 | 148311 | 5922 | 928 | 0 | 0.0010768 | 0 | 1 | 0 | Feeder | WASH PRK_3624 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007844 | PD-01212020-00189 | SOUTHERN | PAULS VALLEY | 5620:PRAIRIE POINT | PRAIRIE_POINT_2021 | 562021 | 2020-01-21 10:29 | 2020-01-21 12:09 | 100.33 | 1 | 1 | 100.3333 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | ELMORE CITY | 24257 E CR 1670 RD | CMI_NORMAL | NO | NO | NO | 860892 | 77595 | 6207 | 607 | 569 | 0.00011655 | 1.1616e-06 | 100.3333 | 1 | 310 | Load | 336110 | Load | TranOpenDelta | GARRID H BROWN | 405-207-3948 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | OK - 2021
J2001.007849 | PD-01212020-00188 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-01-21 10:31 | 2020-01-21 11:08 | 37.38 | 1 | 1 | 7.8287 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4324 S.BARNES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 159101 | 102133 | 7605 | 2461 | 9.0937e-06 | 1.1616e-06 | 7.8287 | 1 | 310 | Customer | 44754 | Load | Tran1phPad | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | #N/A
J2001.007845 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1024 | 941024 | 2020-01-21 10:31 | 2020-01-21 12:08 | 97.33 | 25 | 3 | 1584.5833 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | CLARKSVILLE | CO RD 15 + 69 KV R/W | CMI_PLANNED | YES | NO | NO | 860892 | 82188 | 7542 | 1505 | 304 | 0.0018406 | 2.904e-05 | 63.3833 | 1 | 308 | Mainline | 3980 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-21 | 2020 |  | Ark - Series 2
J2001.007852 | PD-01212020-00192 | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1024 | 311024 | 2020-01-21 10:32 | 2020-01-21 12:00 | 87.52 | 1 | 1 | 87.5167 | 13 | PREMATURE FAILURE | 15 | METER - SECONDARY | MUSKOGEE | 1312 CHESTNUT | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860892 | 74014 | 33256 | 2904 | 1393 | 0.00010166 | 1.1616e-06 | 87.5167 | 1 | 310 | Customer | 3808 | Load | Tran1phOH | REID R WILLIAMS | 512-618-8800 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | OK - 2020
J2001.007855 | PD-01212020-00259 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3624 | 853624 | 2020-01-21 10:38 | 2020-01-21 12:12 | 93.4 | 26 | 1 | 2046.5833 | 13 | PREMATURE FAILURE | 23 | FUSE - PRIMARY | OKLAHOMA CITY | N EVEREST AV & NE 8TH | CMI_NORMAL | NO | NO | NO | 860892 | 168127 | 148311 | 5922 | 928 | 0.0023773 | 3.0201e-05 | 78.7147 | 1 | 310 | Mainline | 206665 | Switch | 0 | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007856 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-01-21 10:38 | 2020-01-21 11:07 | 28.85 | 1 | 1 | 25.3667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 6700 S.POST RD | CMI_PLANNED | YES | NO | NO | 860892 | 159101 | 56968 | 4239 | 1005 | 2.9466e-05 | 1.1616e-06 | 25.3667 | 1 | 308 | Load | 14942 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007858 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-01-21 10:42 | 2020-01-21 10:53 | 11.87 | 1 | 1 | 11.8667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7145 W.MELROSE LN 206 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 128756 | 116002 | 3407 | 2037 | 1.3784e-05 | 1.1616e-06 | 11.8667 | 1 | 310 | Customer | 25282 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007859 | PD-01212020-00203 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3925 | 833925 | 2020-01-21 10:43 | 2020-01-21 12:41 | 118.33 | 1 | 1 | 115.5997 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | BETHANY | 6809 NW.53 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 168127 | 148311 | 7850 | 2183 | 0.00013428 | 1.1616e-06 | 115.5997 | 1 | 320 | Customer | 28184 | Load | TranOHDeltaSplitBank | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | OK - 2022
J2001.007864 | PD-01212020-00209 | METRO NORTH | GUTHRIE | 8819:LIBERTY LAKE | LIBERTY_LAKE_1923 | 881923 | 2020-01-21 10:57 | 2020-01-21 12:25 | 88.42 | 11 | 3 | 865.3333 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | GUTHRIE | .6 MN of Charter Oak Rd on ES of Kelly Ave | CMI_NORMAL | NO | NO | NO | 860892 | 168127 | 19816 | 3352 | 1826 | 0.0010052 | 1.2777e-05 | 78.6667 | 1 | 310 | Mainline | 337732 | Fuse | FuseRiser | JOSEPH WAYNE POOL | 405-919-2253 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007870 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_722 | 870722 | 2020-01-21 11:09 | 2020-01-21 11:55 | 46.08 | 1 | 1 | 44.0833 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | NORMAN | .2ME E.84TH AV + HWY 9 | CMI_PLANNED | YES | NO | NO | 860892 | 159101 | 56968 | 11834 | 1582 | 5.1207e-05 | 1.1616e-06 | 44.0833 | 1 | 308 | Tap | 22020 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007875 | PD-01212020-00266 | NORTHEAST | MUSKOGEE | 3312:CHECOTAH | CHECOTAH 22 | 331222 | 2020-01-21 11:14 | 2020-01-21 12:18 | 64.43 | 1 | 1 | 64.4333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | CHECOTAH | 610 N E 4TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 74014 | 33256 | 2887 | 1530 | 7.4845e-05 | 1.1616e-06 | 64.4333 | 1 | 320 | Customer | 7272 | Load | Tran1phOH | NICHOLAS SELVIDGE | 918-652-1986 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | OK - 2020
J2001.007882 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1022 | 541022 | 2020-01-21 11:19 | 2020-01-21 12:04 | 45.2 | 4 | 1 | 180.8508 | 4 | DETERIORATION | 15 | METER - SECONDARY | MADILL | TALIAFERRO ACRES | CMI_PLANNED | YES | NO | NO | 860892 | 77595 | 7201 | 2378 | 873 | 0.00021007 | 4.6463e-06 | 45.2127 | 1 | 308 | Load | 9323 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007878 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7021 | 817021 | 2020-01-21 11:20 | 2020-01-21 12:05 | 45.02 | 1 | 1 | 45.0167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7000 S.WALKER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 159101 | 102133 | 9939 | 1790 | 5.2291e-05 | 1.1616e-06 | 45.0167 | 1 | 310 | Customer | 52788 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007885 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-21 11:39 | 2020-01-21 13:44 | 125.7 | 2 | 2 | 119.5 | 4 | DETERIORATION | 23 | FUSE - PRIMARY | LAVACA | HWY 96.51/4M.NOF HWY 22 | CMI_PLANNED | YES | NO | NO | 860892 | 82188 | 61166 | 2735 | 2123 | 0.00013881 | 2.3232e-06 | 59.75 | 1 | 308 | Tap | 6994 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | Ark - Series 2
J2001.007887 |  | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1722 | 911722 | 2020-01-21 11:43 | 2020-01-21 17:10 | 327.28 | 5 | 4 | 775.25 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 9020 ROYALRIDGE DR | CMI_PLANNED | YES | NO | NO | 860892 | 82188 | 61166 | 4241 | 1474 | 0.00090052 | 5.8079e-06 | 155.05 | 1 | 308 | Load | 584 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-21 | 2020 |  | #N/A
J2001.007888 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4031 | 834031 | 2020-01-21 11:44 | 2020-01-21 13:38 | 114.27 | 1 | 1 | 74.65 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | 5701 W BRITTON RD | CMI_PLANNED | YES | NO | NO | 860892 | 128756 | 116002 | 10841 | 1641 | 8.6712e-05 | 1.1616e-06 | 74.65 | 1 | 308 | Mainline | 100248 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007893 |  | NORTHEAST | SAPULPA | 3208:TIBBENS ROAD | TIBBENS_RD_824 | 320824 | 2020-01-21 11:47 | 2020-01-21 18:37 | 410.38 | 12 | 5 | 1738.6 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | JENKS | W 110TH ST S | CMI_PLANNED | YES | NO | NO | 860892 | 74014 | 40758 | 3142 | 1401 | 0.0020195 | 1.3939e-05 | 144.8833 | 1 | 310 | Load | 249890 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | OK - 2020
J2001.007894 |  | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_421 | 710421 | 2020-01-21 11:48 | 2020-01-21 12:44 | 55.4 | 4 | 1 | 200.2333 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | CHANDLER | 128 SUNNY PL | CMI_PLANNED | YES | NO | NO | 860892 | 114346 | 7462 | 2822 | 1173 | 0.00023259 | 4.6463e-06 | 50.0583 | 1 | 308 | Load | 9358 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | OK - 2021
J2001.007899 | PD-01212020-00288 | METRO NORTH | NORTH | 8209:CLASSEN | CLASSEN_923 | 820923 | 2020-01-21 12:07 | 2020-01-21 13:13 | 66.05 | 1 | 1 | 66.05 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1504 NW.10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 168127 | 148311 | 3883 | 1147 | 7.6723e-05 | 1.1616e-06 | 66.05 | 1 | 310 | Customer | 8643 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007902 |  | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1823 | 931823 | 2020-01-21 12:21 | 2020-01-21 13:23 | 62.18 | 8 | 5 | 369.6 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | ALMA | MAPLE SHADE - NORTHWOODS ADD. | CMI_PLANNED | YES | NO | NO | 860892 | 82188 | 61166 | 2835 | 1228 | 0.00042932 | 9.2927e-06 | 46.2 | 1 | 308 | Load | 80 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | Ark - Series 2
J2001.007904 | PD-01212020-00309 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1424 | 311424 | 2020-01-21 12:25 | 2020-01-21 16:18 | 233.43 | 15 | 18 | 3501.5 | 5 | ELECTRICAL TRACKING | 28 | CROSSARM | MUSKOGEE | 2705 ELIZABETH | CMI_NORMAL | NO | NO | NO | 860892 | 74014 | 33256 | 4567 | 798 | 0.0040673 | 1.7424e-05 | 233.4333 | 1 | 310 | Load | 6706 | Load | Tran1phOH | GARY MICHAEL KNUPP | 918-577-8564 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | OK - 2020
J2001.007907 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9929 | 829929 | 2020-01-21 12:38 | 2020-01-21 12:47 | 8.65 | 1 | 1 | 8.65 | 1 | CANCELLED | 57 | CANCELLED | BETHANY | 2506 ALEXANDER LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 128756 | 116002 | 9226 | 2207 | 1.0048e-05 | 1.1616e-06 | 8.65 | 1 | 310 | Customer | 42106 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007911 | PD-01212020-00320 | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3422 | 843422 | 2020-01-21 12:48 | 2020-01-21 13:41 | 52.78 | 1 | 1 | 52.7833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 6700 N MARTIN LUTHER KING AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 168127 | 148311 | 1224 | 726 | 6.1312e-05 | 1.1616e-06 | 52.7833 | 1 | 310 | Load | 85348 | Load | Tran3phPadWye | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | #N/A
J2001.007912 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6121 | 836121 | 2020-01-21 13:06 | 2020-01-21 13:34 | 28.58 | 1 | 1 | 28.5833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | NW 33RD + KENTUCKY AVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 168127 | 148311 | 11100 | 1638 | 3.3202e-05 | 1.1616e-06 | 28.5833 | 1 | 310 | Customer | 736 | Load | TranOHDeltaSplitBank | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | OK - 2021
J2001.007921 | PD-01212020-00346 | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_521 | 530521 | 2020-01-21 13:19 | 2020-01-21 13:48 | 28.78 | 1 | 1 | 28.7833 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | HEALDTON | 1E1.5N1/4W OF OIL CY | CMI_NORMAL | NO | NO | NO | 860892 | 77595 | 6795 | 2126 | 1259 | 3.3434e-05 | 1.1616e-06 | 28.7833 | 1 | 310 | Load | 607 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | OK - 2020
J2001.007924 | PD-01212020-00359 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1424 | 311424 | 2020-01-21 13:21 | 2020-01-21 14:17 | 56.18 | 1 | 1 | 56.1833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MUSKOGEE | 415 N 26TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 74014 | 33256 | 4567 | 798 | 6.5262e-05 | 1.1616e-06 | 56.1833 | 1 | 310 | Customer | 3003 | Load | Tran1phOH | REID R WILLIAMS | 512-618-8800 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | OK - 2020
J2001.007923 | PD-01212020-00348 | NORTHWEST | ALVA | 4705:ALVA | ALVA_523 | 470523 | 2020-01-21 13:21 | 2020-01-21 16:06 | 165.18 | 1 | 1 | 165.1833 | 29 | TREES : GROW IN | 37 | CONDUCTOR PRIMARY - OH | ALVA | .25MS OF CR520 AND McCLAIN RD. | CMI_NORMAL | NO | NO | NO | 860892 | 53521 | 5520 | 2439 | 581 | 0.00019187 | 1.1616e-06 | 165.1833 | 1 | 320 | Load | 370486 | Load | Tran1phPad | [7 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | #N/A
J2001.007925 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9929 | 829929 | 2020-01-21 13:24 | 2020-01-21 13:36 | 12.65 | 1 | 1 | 12.65 | 1 | CANCELLED | 57 | CANCELLED | BETHANY | 2506 ALEXANDER LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 128756 | 116002 | 9226 | 2207 | 1.4694e-05 | 1.1616e-06 | 12.65 | 1 | 310 | Customer | 42106 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007928 | PD-01212020-00349 | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2163 | 892163 | 2020-01-21 13:25 | 2020-01-21 14:47 | 81.92 | 1 | 1 | 81.9167 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | MUSTANG | 1825 W JJ COURT WAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 128756 | 12754 | 3188 | 1137 | 9.5153e-05 | 1.1616e-06 | 81.9167 | 1 | 310 | Customer | 406050 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | OK - 2021
J2001.007927 | PD-01212020-00357 | SOUTHERN | DURANT | 5505:DURANT | DURANT 22 | 550522 | 2020-01-21 13:26 | 2020-01-21 14:20 | 54.33 | 1 | 1 | 54.3333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DURANT | OLD HWY 70/LONE OAK RD .1N WS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 77595 | 15484 | 1317 | 797 | 6.3113e-05 | 1.1616e-06 | 54.3333 | 1 | 310 | Customer | 244312 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007932 | PD-01212020-00363 | SOUTHERN | HEALDTON | 5311:RATLIFF | RATLIFF_1121 | 531121 | 2020-01-21 13:36 | 2020-01-21 15:06 | 90.15 | 1 | 1 | 90.15 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | RATLIFF CITY | 7/76 2N .5E | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 77595 | 6795 | 449 | 123 | 0.00010472 | 1.1616e-06 | 90.15 | 1 | 310 | Load | 30424 | Load | TranOpenDelta | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007936 | PD-01212020-00380 | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_623 | 550623 | 2020-01-21 13:52 | 2020-01-21 15:06 | 74.22 | 1 | 1 | 74.2167 | 27 | TREE:NON PREVENTABLE | 21 | FUSE - TRANSFORMER | DURANT | CNTRY EST IV SEWER LIFT | CMI_NORMAL | NO | NO | NO | 860892 | 77595 | 15484 | 6736 | 1717 | 8.6209e-05 | 1.1616e-06 | 74.2167 | 1 | 310 | Load | 23757 | Load | TranOpenDelta | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007937 | PD-01212020-00384 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3729 | 833729 | 2020-01-21 13:54 | 2020-01-21 15:38 | 103.8 | 1 | 2 | 103.8 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1013 NW.90 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 168127 | 148311 | 5760 | 1402 | 0.00012057 | 1.1616e-06 | 103.8 | 1 | 310 | Customer | 672 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | OK - 2021
J2001.007947 |  | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3624 | 853624 | 2020-01-21 14:07 | 2020-01-21 15:23 | 75.87 | 23 | 19 | 772.0333 | 3 | DAMAGED BY PUBLIC | 35 | CONDUCTOR PRIMARY - UG FEEDER | OKLAHOMA CITY | 900 BLK NE.8 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 168127 | 148311 | 5922 | 928 | 0.00089678 | 2.6716e-05 | 33.5667 | 1 | 310 | Load | 206677 | Load | Tran3phPadWye | Crew | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007944 | PD-01212020-00410 | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8122 | 838122 | 2020-01-21 14:15 | 2020-01-21 14:53 | 37.6 | 1 | 1 | 24.8667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | NW 84 & COUNCIL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 128756 | 116002 | 8955 | 971 | 2.8885e-05 | 1.1616e-06 | 24.8667 | 1 | 310 | Load | 213516 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007945 | PD-01212020-00406 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_631 | 870631 | 2020-01-21 14:18 | 2020-01-21 15:01 | 43.22 | 1 | 1 | 43.2167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 2061 W.LINDSEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 159101 | 56968 | 7367 | 1262 | 5.02e-05 | 1.1616e-06 | 43.2167 | 1 | 310 | Customer | 44328 | Load | Tran1phPad | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007948 | PD-01212020-00407 | METRO EAST | EAST | 8690:WILD MARY | WILD_MARY_9023 | 869023 | 2020-01-21 14:23 | 2020-01-21 15:35 | 72.27 | 1 | 1 | 72.2667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 4100 SE.89 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 114346 | 71181 | 4021 | 2247 | 8.3944e-05 | 1.1616e-06 | 72.2667 | 1 | 310 | Customer | 36818 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007957 |  | NORTHEAST | SAPULPA | 3210:HICKORY HILL | HICKORY_HILL_1021 | 321021 | 2020-01-21 14:23 | 2020-01-21 15:13 | 49.45 | 7 | 7 | 126.35 | 4 | DETERIORATION | 17 | JUMPER | SAPULPA | 109 N MISSION | CMI_PLANNED | YES | NO | NO | 860892 | 74014 | 40758 | 2683 | 1437 | 0.00014677 | 8.1311e-06 | 18.05 | 1 | 308 | Load | 44432 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | OK - 2022
J2001.007950 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4028 | 834028 | 2020-01-21 14:25 | 2020-01-21 14:43 | 18.63 | 1 | 1 | 18.6333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 8583 CANDLEWOOD DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 128756 | 116002 | 10841 | 1261 | 2.1644e-05 | 1.1616e-06 | 18.6333 | 1 | 310 | Customer | 50019 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007952 | PD-01212020-00408 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6961 | 846961 | 2020-01-21 14:30 | 2020-01-21 16:38 | 128.17 | 66 | 45 | 8060.8 | 4 | DETERIORATION | 27 | CUTOUT | OKLAHOMA CITY | 1BE-LEE + NW.136 | CMI_NORMAL | NO | NO | NO | 860892 | 168127 | 148311 | 7719 | 1387 | 0.0093633 | 7.6665e-05 | 122.1333 | 1 | 310 | Mainline | 26053 | Fuse | FuseOH | CURTIS W PINKERTON | 405-464-8500 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007961 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4024 | 834024 | 2020-01-21 15:00 | 2020-01-21 18:05 | 184.35 | 1 | 1 | 164.65 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 5301 NW 123RD ST | CMI_NORMAL | NO | NO | NO | 860892 | 128756 | 116002 | 10841 | 1677 | 0.00019126 | 1.1616e-06 | 164.65 | 1 | 310 | Customer | 222543 | Load | Tran1phPad | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007971 | PD-01212020-00463 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6021 | 836021 | 2020-01-21 15:33 | 2020-01-21 21:05 | 331.82 | 2 | 3 | 620.9833 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | BETHANY | 4104 PATTY LN | CMI_NORMAL | NO | NO | NO | 860892 | 128756 | 116002 | 5506 | 1451 | 0.00072133 | 2.3232e-06 | 310.4917 | 1 | 320 | Secondary | 58456 | Load | Tran1phPad | HOWARD GETCHELL | 530-410-8920 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | #N/A
J2001.007973 | PD-01212020-00462 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_631 | 870631 | 2020-01-21 15:36 | 2020-01-21 16:19 | 43.37 | 1 | 1 | 43.3667 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | NORMAN | 2061 W.LINDSEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 159101 | 56968 | 7367 | 1262 | 5.0374e-05 | 1.1616e-06 | 43.3667 | 1 | 315 | Customer | 44328 | Load | Tran1phPad | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007975 |  | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1424 | 311424 | 2020-01-21 15:38 | 2020-01-21 16:08 | 30.05 | 29 | 24 | 872.4167 | 4 | DETERIORATION | 28 | CROSSARM | MUSKOGEE | E/O 26 S/O ELIZABETH | CMI_NORMAL | NO | NO | NO | 860892 | 74014 | 33256 | 4567 | 798 | 0.0010134 | 3.3686e-05 | 30.0833 | 1 | 310 | Mainline | 15057 | Fuse | FuseOH | GARY MICHAEL KNUPP | 918-577-8564 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | OK - 2020
J2001.007979 |  | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3021 | 743021 | 2020-01-21 16:04 | 2020-01-21 16:22 | 17.42 | 1 | 1 | 17.4167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SHAWNEE | 620.5 N.MARKET | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 114346 | 22101 | 6642 | 1701 | 2.0231e-05 | 1.1616e-06 | 17.4167 | 1 | 310 | Customer | 4108 | Load | TranOHDeltaSplitBank | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | OK - 2021
J2001.007980 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6921 | 846921 | 2020-01-21 16:14 | 2020-01-21 16:20 | 5.25 | 1 | 1 | 5.25 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 13508 VIXEN LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 168127 | 148311 | 7719 | 1353 | 6.0983e-06 | 1.1616e-06 | 5.25 | 1 | 310 | Customer | 59343 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007981 | PD-01212020-00511 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5125 | 815125 | 2020-01-21 16:19 | 2020-01-21 16:37 | 18.33 | 1 | 1 | 18.3333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2346 SW 74TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 159101 | 102133 | 13933 | 1432 | 2.1296e-05 | 1.1616e-06 | 18.3333 | 1 | 310 | Customer | 36184 | Load | Tran1phPad | THOMAS E COLE | 405-623-9338 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007984 | PD-01212020-00517 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-01-21 16:27 | 2020-01-21 17:47 | 79.55 | 1 | 1 | 74.8667 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | ARDMORE | SPRINGDALE SCHOOL | CMI_NORMAL | NO | NO | NO | 860892 | 77595 | 23587 | 2207 | 1001 | 8.6964e-05 | 1.1616e-06 | 74.8667 | 1 | 320 | Load | 155352 | Load | Tran3phPadWye | DAVID TAYLOR | 580-574-4517 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007985 |  | METRO WEST | WEST | 8335:BETHANY | BETHANY_3527 | 833527 | 2020-01-21 16:29 | 2020-01-21 16:36 | 6.7 | 1 | 1 | 6.7 | 1 | CANCELLED | 57 | CANCELLED | WARR ACRES | 5304 NW.44 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 128756 | 116002 | 7867 | 1662 | 7.7826e-06 | 1.1616e-06 | 6.7 | 1 | 310 | Customer | 21752 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | OK - 2022
J2001.007987 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6921 | 846921 | 2020-01-21 16:32 | 2020-01-21 16:39 | 6.43 | 1 | 1 | 6.4333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 13508 VIXEN LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 168127 | 148311 | 7719 | 1353 | 7.4729e-06 | 1.1616e-06 | 6.4333 | 1 | 315 | Customer | 59343 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007990 | PD-01212020-00528 | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5429 | 865429 | 2020-01-21 16:40 | 2020-01-22 01:36 | 536.23 | 55 | 56 | 15506.95 | 3 | DAMAGED BY PUBLIC | 36 | CONDUCTOR PRIMARY - UG | MOORE | E EASTERN N NE.5 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 159101 | 102133 | 9806 | 1661 | 0.018013 | 6.3887e-05 | 281.9445 | 1 | 310 | Mainline | 3992 | Fuse | FuseRiser | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007988 | PD-01212020-00539 | SOUTHERN | PAULS VALLEY | 5619:RUSH CREEK | RUSH_CREEK_1921 | 561921 | 2020-01-21 16:42 | 2020-01-21 18:09 | 86.93 | 1 | 1 | 86.9333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | PAULS VALLEY | WILDWOOD APARTMENTS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 77595 | 6207 | 2072 | 824 | 0.00010098 | 1.1616e-06 | 86.9333 | 1 | 310 | Customer | 24434 | Load | Tran1phPad | GARRID H BROWN | 405-207-3948 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | #N/A
J2001.007992 |  | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1423 | 311423 | 2020-01-21 16:50 | 2020-01-21 16:53 | 2.82 | 1 | 1 | 2.8167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 228 S.13 | CMI_MOMENTARY | YES | NO | NO | 860892 | 74014 | 33256 | 4567 | 1494 | 3.2718e-06 | 1.1616e-06 | 2.8167 | 1 | 310 | Customer | 760 | Load | TranOHDeltaSplitBank | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | OK - 2020
J2001.007993 | PD-01212020-00536 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6328 | 816328 | 2020-01-21 16:50 | 2020-01-21 20:19 | 208.68 | 1 | 1 | 208.6833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MOORE | 111 NE.7 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 159101 | 102133 | 11826 | 1188 | 0.0002424 | 1.1616e-06 | 208.6833 | 1 | 310 | Customer | 39550 | Load | Tran1phOH | THOMAS E COLE | 405-623-9338 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.007997 |  | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6023 | 836023 | 2020-01-21 16:56 | 2020-01-21 17:00 | 4.17 | 1 | 1 | 4.1667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BETHANY | 7108 NW.46 | CMI_MOMENTARY | YES | NO | NO | 860892 | 128756 | 116002 | 5506 | 1480 | 4.8399e-06 | 1.1616e-06 | 4.1667 | 1 | 310 | Customer | 50568 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | OK - 2022
J2001.008003 | PD-01212020-00553 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1423 | 311423 | 2020-01-21 17:22 | 2020-01-21 18:06 | 43.58 | 5 | 3 | 207.1667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MUSKOGEE | 551 N.7 | CMI_NORMAL | NO | NO | NO | 860892 | 74014 | 33256 | 4567 | 1494 | 0.00024064 | 5.8079e-06 | 41.4333 | 1 | 310 | Load | 3577 | Load | Tran1phOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | OK - 2020
J2001.008008 | PD-01212020-00557 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3731 | 833731 | 2020-01-21 17:35 | 2020-01-21 20:43 | 187.97 | 1 | 1 | 182.5 | 4 | DETERIORATION | 50 | CONNECTOR | THE VILLAGE | 1406 CARLISLE | CMI_NORMAL | NO | NO | NO | 860892 | 168127 | 148311 | 5760 | 1902 | 0.00021199 | 1.1616e-06 | 182.5 | 1 | 320 | Customer | 8428 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | OK - 2020
J2001.008009 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9929 | 829929 | 2020-01-21 17:40 | 2020-01-21 17:52 | 12.87 | 1 | 1 | 12.8667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BETHANY | 2432 ALEXANDER LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 128756 | 116002 | 9226 | 2207 | 1.4946e-05 | 1.1616e-06 | 12.8667 | 1 | 310 | Customer | 42110 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.008014 |  | METRO SOUTH | SOUTH | 8722:MILLENNIUM | MILLENNIUM_2231 | 872231 | 2020-01-21 17:58 | 2020-01-21 18:17 | 19.35 | 1 | 1 | 19.35 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | LT 15 BLK 3 SUMMIT LAKES 3 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 159101 | 56968 | 4205 | 2053 | 2.2477e-05 | 1.1616e-06 | 19.35 | 1 | 310 | Customer | 100173 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.008015 |  | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_524 | 560524 | 2020-01-21 18:07 | 2020-01-21 18:14 | 7.12 | 1 | 1 | 7.1167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | PAULS VALLEY | 421 E GRANT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 77597 | 6207 | 2458 | 602 | 8.2666e-06 | 1.1616e-06 | 7.1167 | 1 | 310 | Customer | 9294 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-21 | 2020 |  | OK - 2022
J2001.008021 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1223 | 831223 | 2020-01-21 18:37 | 2020-01-21 18:56 | 18.98 | 1 | 1 | 18.9833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | The Lincoln at Central Park | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 168142 | 148325 | 7745 | 634 | 2.2051e-05 | 1.1616e-06 | 18.9833 | 1 | 310 | Customer | 315061 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.008025 | PD-01212020-00571 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1922 | 851922 | 2020-01-21 19:13 | 2020-01-21 21:23 | 129.85 | 1 | 2 | 100.1667 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | MIDWEST CITY | 1024 HAZELWOOD DR | CMI_NORMAL | NO | NO | NO | 860892 | 114349 | 71182 | 12442 | 1795 | 0.00011635 | 1.1616e-06 | 100.1667 | 1 | 320 | Customer | 26115 | Load | Tran1phOH | KYLE L GOODIN | 405-426-9802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.008030 |  | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4022 | 914022 | 2020-01-21 19:31 | 2020-01-21 22:01 | 149.53 | 1 | 1 | 91.9333 | 4 | DETERIORATION | 48 | CABLE TERMINATION | FORT SMITH | 3100 BRIARCLIFF | CMI_PLANNED | YES | NO | NO | 860892 | 82198 | 61170 | 4757 | 1905 | 0.00010679 | 1.1616e-06 | 91.9333 | 1 | 308 | Load | 14632 | Load | Tran3phPadWye | Contractor | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-21 | 2020 |  | Ark - Series 1
J2001.008032 |  | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5429 | 865429 | 2020-01-21 19:59 | 2020-01-21 20:44 | 44.33 | 1 | 1 | 44.3333 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | MOORE | 609 RANDALL DR | CMI_NORMAL | NO | NO | NO | 860892 | 159107 | 102139 | 9807 | 1662 | 5.1497e-05 | 1.1616e-06 | 44.3333 | 1 | 310 | Customer | 48815 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.008042 | PD-01212020-00589 | METRO WEST | WEST | 8222:CZECH HALL | CZECH_HALL_2222 | 822222 | 2020-01-21 21:56 | 2020-01-21 22:42 | 46.33 | 1 | 1 | 46.3333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 11501 LOCHWOOD DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860892 | 128782 | 116027 | 8604 | 2027 | 5.382e-05 | 1.1616e-06 | 46.3333 | 1 | 320 | Customer | 76442 | Load | Tran1phPad | DARREN L STOCKTON | 918-777-1697 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-21 | 2020 |  | #N/A
J2001.008089 | PD-01222020-00007 | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_433 | 510433 | 2020-01-22 04:59 | 2020-01-22 07:02 | 122.62 | 1 | 1 | 122.6167 | 22 | WIND | 17 | JUMPER | ARDMORE | 600 P NE. | CMI_NORMAL | NO | NO | NO | 860969 | 77597 | 23587 | 2317 | 1258 | 0.00014242 | 1.1615e-06 | 122.6167 | 1 | 320 | Load | 26240 | Load | Tran3phPadWye | JUSTIN B MARSHALL | 580-221-5051 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008091 | PD-01222020-00008 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4823 | 824823 | 2020-01-22 05:02 | 2020-01-22 08:22 | 199.95 | 1 | 2 | 199.95 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3230 SW.19 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 168142 | 148325 | 4191 | 1796 | 0.00023224 | 1.1615e-06 | 199.95 | 1 | 311 | Customer | 5789 | Load | Tran1phOH | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | OK - 2021
J2001.008096 | PD-01222020-00010 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2622 | 862622 | 2020-01-22 05:27 | 2020-01-22 10:29 | 302.03 | 88 | 62 | 24415.6 | 22 | WIND | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | SE.22,KATE | CMI_NORMAL | NO | NO | NO | 860969 | 159107 | 102139 | 7416 | 349 | 0.028358 | 0.00010221 | 277.45 | 1 | 311 | Tap | 12185 | Fuse | FuseOH | HOWARD GETCHELL | 530-410-8920 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008100 |  | METRO EAST | EAST | 8692:AIR DEPOT | AIR_DEPOT_9223 | 869223 | 2020-01-22 05:45 | 2020-01-22 05:45 | 0 | 2 | 0 | 0 | 1 | CANCELLED | 57 | CANCELLED | 0 | 0 | CMI_MOMENTARY | YES | NO | NO | 860969 | 114349 | 71182 | 1906 | 1476 | 0 | 2.323e-06 | 0 | 1 | 0 | Mainline | 204811-1 | Switch | SwitchDefault | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008101 | PD-01222020-00011 | METRO WEST | WEST | 8157:MACARTHUR | MACARTHUR_5722 | 815722 | 2020-01-22 05:47 | 2020-01-22 15:00 | 553.32 | 1 | 1 | 553.3167 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | 7100 Terminal Drive | CMI_NORMAL | NO | NO | NO | 860969 | 128782 | 116027 | 1853 | 347 | 0.00064267 | 1.1615e-06 | 553.3167 | 1 | 310 | Customer | 406533 | Load | Tran1phPad | HOWARD GETCHELL | 530-410-8920 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008105 | PD-01222020-00013 | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5421 | 865421 | 2020-01-22 05:49 | 2020-01-22 13:33 | 463.97 | 15 | 9 | 6809.25 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | MOORE | 2408 E HILLS DR | CMI_NORMAL | NO | NO | NO | 860969 | 159107 | 102139 | 9807 | 1880 | 0.0079088 | 1.7422e-05 | 453.95 | 1 | 310 | Load | 71914 | Load | Tran1phPad | DAVID M CLEMMONS | 405-777-8355 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008107 | PD-01222020-00015 | METRO EAST | EAST | 8618:BARNES | BARNES_1822 | 861822 | 2020-01-22 06:16 | 2020-01-22 07:34 | 78.17 | 2 | 2 | 136.4667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | LOT 13 BLK 2 SADDLEBACK EST | CMI_NORMAL | NO | NO | NO | 860969 | 114349 | 71182 | 952 | 420 | 0.0001585 | 2.323e-06 | 68.2333 | 1 | 310 | Secondary | 74319 | Load | Tran1phOH | STEVEN CASKEY | 405-777-8855 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008330 | PD-01222020-00016 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_622 | 870622 | 2020-01-22 06:37 | 2020-01-22 12:36 | 358.85 | 3 | 1 | 980.4 | 4 | DETERIORATION | 12 | POLE | NORMAN | 24TH S OF LINDSEY | CMI_NORMAL | NO | NO | NO | 860969 | 159107 | 56968 | 7367 | 1260 | 0.0011387 | 3.4844e-06 | 326.8 | 1 | 310 | Tap | 29474 | Fuse | FuseOH | JASON CLARK | 405-420-5186 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008119 | PD-01222020-00024 | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_621 | 410621 | 2020-01-22 07:20 | 2020-01-22 08:32 | 72.03 | 1 | 1 | 72.0333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ENID | 926 N.DAVIS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 53522 | 37580 | 6011 | 1102 | 8.3665e-05 | 1.1615e-06 | 72.0333 | 1 | 320 | Customer | 4604 | Load | Tran1phOH | KEVIN N PERRYMAN | 601-528-2473 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008142 | PD-01222020-00045 | ARKANSAS | POTEAU | 3514:HEAVENER | HEAVENER 22 | 351422 | 2020-01-22 07:44 | 2020-01-22 11:17 | 213.25 | 1 | 2 | 68.15 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | HEAVENER | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 0 | 0 | 0 | 0 | 7.9155e-05 | 1.1615e-06 | 68.15 | 1 | 310 | Customer |  | 0 | 0 | TOBY C MEAD | 918-658-5596 |  |  |  |  | 06/02/2020 note from burchamc. Reference J2001.008142 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | OK - 2021
J2001.008123 | PD-01222020-00040 | ARKANSAS | POTEAU | 3514:HEAVENER | HEAVENER 22 | 351422 | 2020-01-22 07:44 | 2020-01-22 08:52 | 68.2 | 284 | 77 | 18651.9167 | 13 | PREMATURE FAILURE | 23 | FUSE - PRIMARY | HEAVENER | WEST 5 NORTH OF AVE I | CMI_NORMAL | NO | NO | NO | 860969 | 82198 | 13483 | 1770 | 1307 | 0.021664 | 0.00032986 | 65.6758 | 1 | 310 | Mainline | 29218 | Fuse | FuseOH | TOBY C MEAD | 918-658-5596 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | OK - 2021
J2001.008128 | PD-01222020-00035 | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2522 | 512522 | 2020-01-22 07:48 | 2020-01-22 09:31 | 103.27 | 1 | 1 | 102.2 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | LONE GROVE | 5N MERIDIAN RD 1/4W | CMI_NORMAL | NO | NO | NO | 860969 | 77597 | 23587 | 3305 | 562 | 0.0001187 | 1.1615e-06 | 102.2 | 1 | 310 | Customer | 3488 | Load | Tran1phOH | RANDAL G CALLAWAY | 580-220-8449 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | OK - 2021
J2001.008136 | PD-01222020-02265 | ARKANSAS | FORT SMITH | 9111:MASSARD | MASSARD_1123 | 911123 | 2020-01-22 07:50 | 2020-01-22 11:58 | 247.53 | 1 | 3 | 303.3 | 4 | DETERIORATION | 50 | CONNECTOR | FORT SMITH | SEE EXTENDED ADDRESS | CMI_NORMAL | NO | NO | NO | 860969 | 82198 | 61170 | 4985 | 555 | 0.00035228 | 1.1615e-06 | 303.3 | 1 | 321 | Customer | 15882 | Load | TranOpenDelta | MARK A. SAWYER | 479-462-4457 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-22 | 2020 |  | Ark - Series 3
J2001.008140 | PD-01222020-00042 | SOUTHERN | HEALDTON | 5319:FOX | FOX 21 | 531921 | 2020-01-22 07:55 | 2020-01-22 10:15 | 140.32 | 1 | 2 | 144.0833 | 25 | LIGHTNING | 17 | JUMPER | HEALDTON | 76/53E 3W 1N .4W .2N | CMI_NORMAL | NO | NO | NO | 860969 | 77597 | 6796 | 706 | 341 | 0.00016735 | 1.1615e-06 | 144.0833 | 1 | 310 | Load | 90366 | Load | 0 | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008154 |  | METRO WEST | WEST | 8157:MACARTHUR | MACARTHUR_5722 | 815722 | 2020-01-22 08:21 | 2020-01-22 08:21 | 0.02 | 345 | 0 | 5.75 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 3710 N MACARTHUR | CMI_MOMENTARY | YES | NO | NO | 860969 | 128782 | 116027 | 1853 | 347 | 6.6785e-06 | 0.00040071 | 0.016667 | 1 | 0 | Feeder | MACARTHR_5722 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008155 |  | METRO WEST | WEST | 8157:MACARTHUR | MACARTHUR_5722 | 815722 | 2020-01-22 08:25 | 2020-01-22 08:26 | 0.83 | 345 | 0 | 287.5 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 3710 N MACARTHUR | CMI_MOMENTARY | YES | NO | NO | 860969 | 128782 | 116027 | 1853 | 347 | 0.00033393 | 0.00040071 | 0.83333 | 1 | 0 | Feeder | MACARTHR_5722 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008160 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-22 08:35 | 2020-01-22 16:02 | 446.75 | 4 | 2 | 229.4333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | ARKOMA | 612 ARKANSAS | CMI_NORMAL | NO | NO | NO | 860969 | 82198 | 61170 | 2934 | 875 | 0.00026648 | 4.6459e-06 | 57.3583 | 1 | 308 | Load | 4362 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-22 | 2020 |  | Ark - Series 2
J2001.008170 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1024 | 541024 | 2020-01-22 08:54 | 2020-01-22 09:44 | 50.43 | 662 | 69 | 30352.7 | 17 | TRANSMISSION OPERATION | 45 | SUBSTATION CIRCUIT | MADILL | 12537 HIGHWAY 199 | CMI_NORMAL | NO | NO | NO | 860969 | 77597 | 7199 | 2378 | 662 | 0.035254 | 0.0007689 | 45.85 | 1 | 310 | Mainline | GLASSES_1024L | Switch | SWITCH | [7 empty] | Equipment | N | TRANSMISSION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008185 | PD-01222020-01235 | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1022 | 541022 | 2020-01-22 08:54 | 2020-01-22 09:44 | 50.52 | 873 | 101 | 40012.5 | 17 | TRANSMISSION OPERATION | 45 | SUBSTATION CIRCUIT | MADILL | 12537 HIGHWAY 199 | CMI_NORMAL | NO | NO | NO | 860969 | 77597 | 7199 | 2378 | 873 | 0.046474 | 0.001014 | 45.8333 | 1 | 310 | Mainline | GLASSES_1022L | Switch | SWITCH | [7 empty] | Equipment | N | TRANSMISSION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008270 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1023 | 541023 | 2020-01-22 08:54 | 2020-01-22 09:44 | 50.57 | 843 | 109 | 38609.4 | 17 | TRANSMISSION OPERATION | 45 | SUBSTATION CIRCUIT | MADILL | 12537 HIGHWAY 199 | CMI_NORMAL | NO | NO | NO | 860969 | 77597 | 7199 | 2378 | 842 | 0.044844 | 0.00097913 | 45.8 | 1 | 310 | Mainline | GLASSES_1023L | Switch | SWITCH | [7 empty] | Equipment | N | TRANSMISSION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008291 |  | SOUTHERN | MADILL | 5407:MADILL INDUSTR | MADILL_INDUS_741 | 540741 | 2020-01-22 08:54 | 2020-01-22 14:15 | 321.23 | 1 | 1 | 213.25 | 17 | TRANSMISSION OPERATION | 45 | SUBSTATION CIRCUIT | MADILL | 1329 SMILEY RD | CMI_NORMAL | NO | NO | NO | 860969 | 77597 | 7199 | 2 | 1 | 0.00024769 | 1.1615e-06 | 213.25 | 1 | 308 | Feeder | MADILL_INDUS_741 | Recloser | 0 | [7 empty] | Equipment | N | TRANSMISSION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008289 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1021 | 541021 | 2020-01-22 08:54 | 2020-01-22 09:39 | 45.52 | 1 | 0 | 45.5167 | 17 | TRANSMISSION OPERATION | 45 | SUBSTATION CIRCUIT | MADILL | 12537 HIGHWAY 199 | CMI_NORMAL | NO | NO | NO | 860969 | 77597 | 7199 | 2378 | 1 | 5.2867e-05 | 1.1615e-06 | 45.5167 | 1 | 0 | Mainline | GLASSES_1021L | Switch | SWITCH | [7 empty] | Equipment | N | TRANSMISSION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008290 |  | SOUTHERN | MADILL | 5407:MADILL INDUSTR | MADILL_INDUS_742 | 540742 | 2020-01-22 08:56 | 2020-01-22 16:59 | 482.15 | 1 | 0 | 482.15 | 17 | TRANSMISSION OPERATION | 45 | SUBSTATION CIRCUIT | MADILL | 1329 SMILEY RD | CMI_NORMAL | NO | NO | NO | 860969 | 77597 | 7199 | 2 | 1 | 0.00056001 | 1.1615e-06 | 482.15 | 1 | 0 | Mainline | MADILL_INDUS_742L | Switch | 0 | [7 empty] | Equipment | N | TRANSMISSION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008186 | PD-01222020-00658 | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-01-22 09:00 | 2020-01-22 09:59 | 59.5 | 1 | 1 | 59.5 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ADA | 720 N Texas | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 77597 | 11512 | 2518 | 1090 | 6.9108e-05 | 1.1615e-06 | 59.5 | 1 | 310 | Customer | 16372 | Load | TranOpenDelta | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008240 |  | SOUTHERN | MADILL | 5408:CANEY CREEK | CANEY_CREEK_831 | 540831 | 2020-01-22 09:03 | 2020-01-22 10:33 | 89.52 | 1 | 1 | 89.5167 | 1 | CANCELLED | 57 | CANCELLED | KINGSTON | 2 BLKS E OF MAIN ON 1ST KNSTON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 77597 | 7199 | 1052 | 628 | 0.00010397 | 1.1615e-06 | 89.5167 | 1 | 310 | Customer | 5801 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008277 | PD-01222020-01342 | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_621 | 410621 | 2020-01-22 09:08 | 2020-01-22 10:32 | 84.15 | 1 | 1 | 84.15 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ENID | 926 N.DAVIS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 53522 | 37580 | 6011 | 1102 | 9.7739e-05 | 1.1615e-06 | 84.15 | 1 | 310 | Customer | 4604 | Load | Tran1phOH | KEVIN N PERRYMAN | 601-528-2473 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008301 | PD-01222020-01237 | METRO NORTH | NORTH | 8506:PARK PLACE | PARK_PLACE_623 | 850623 | 2020-01-22 09:25 | 2020-01-22 11:43 | 137.7 | 1 | 2 | 125.55 | 5 | ELECTRICAL TRACKING | 47 | ARRESTOR OH | OKLAHOMA CITY | 50 NE.23 | CMI_NORMAL | NO | NO | NO | 860969 | 168142 | 148325 | 830 | 266 | 0.00014582 | 1.1615e-06 | 125.55 | 1 | 310 | Load | 10338 | Load | Tran3phWye | CURTIS W PINKERTON | 405-464-8500 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008302 | PD-01222020-01323 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4823 | 824823 | 2020-01-22 09:26 | 2020-01-22 10:54 | 88.45 | 1 | 2 | 55.5515 | 22 | WIND | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 3507 CAMPBELL PL | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860969 | 168142 | 148325 | 4191 | 1796 | 6.4522e-05 | 1.1615e-06 | 55.5515 | 1 | 310 | Customer | 17967 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | OK - 2021
J2001.008307 |  | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_433 | 510433 | 2020-01-22 09:35 | 2020-01-22 10:53 | 78.15 | 1 | 1 | 4.2167 | 1 | CANCELLED | 57 | CANCELLED | ARDMORE | 606 PARK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 77597 | 23587 | 2317 | 1258 | 4.8976e-06 | 1.1615e-06 | 4.2167 | 1 | 310 | Customer | 17478 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008310 | PD-01222020-02211 | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2524 | 512524 | 2020-01-22 09:38 | 2020-01-22 10:50 | 72.2 | 1 | 1 | 72.2 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | LONE GROVE | 3MW I-35 ON 70 NS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 77597 | 23587 | 3305 | 999 | 8.3859e-05 | 1.1615e-06 | 72.2 | 1 | 310 | Customer | 22823 | Load | Tran1phOH | RANDAL G CALLAWAY | 580-220-8449 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008313 | PD-01222020-01923 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4122 | 814122 | 2020-01-22 09:43 | 2020-01-22 10:57 | 73.6 | 1 | 1 | 58.5236 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 5005 S. I-35 Service rd. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 159107 | 102139 | 5808 | 1271 | 6.7974e-05 | 1.1615e-06 | 58.5236 | 1 | 320 | Customer | 376567 | Load | Tran3phWye | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008312 | PD-01222020-02268 | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 22 | 570822 | 2020-01-22 09:43 | 2020-01-22 12:36 | 172.52 | 1 | 2 | 172.5167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DAVIS | 608 S. 2ND | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 77597 | 6811 | 1858 | 955 | 0.00020038 | 1.1615e-06 | 172.5167 | 1 | 310 | Customer | 4494 | Load | Tran1phOH | GARRID H BROWN | 405-207-3948 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | OK - 2021
J2001.008318 |  | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 22 | 570822 | 2020-01-22 09:56 | 2020-01-22 10:49 | 53.05 | 1 | 1 | 53.05 | 1 | CANCELLED | 57 | CANCELLED | DAVIS | 406 S.2 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 77597 | 6811 | 1858 | 955 | 6.1617e-05 | 1.1615e-06 | 53.05 | 1 | 310 | Customer | 197 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | OK - 2021
J2001.008324 |  | NORTHWEST | ENID | 4107:CLEVELAND AVE | CLEVELAND_AVE_723 | 410723 | 2020-01-22 10:06 | 2020-01-22 12:37 | 150.52 | 1 | 2 | 148.0667 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | ENID | 2206 W BROADWAY AVE | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860969 | 53522 | 37580 | 4461 | 1418 | 0.00017198 | 1.1615e-06 | 148.0667 | 1 | 310 | Customer | 345635 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008325 | PD-01222020-02216 | ARKANSAS | OZARK | 9406:HELBERG | HELBERG_621 | 940621 | 2020-01-22 10:08 | 2020-01-22 11:38 | 90.2 | 6 | 6 | 535.3 | 7 | ICE / SLEET / SNOW | 21 | FUSE - TRANSFORMER | OZARK | BTWN OAK + WALNUT-SS SPRING ST | CMI_NORMAL | NO | NO | NO | 860969 | 82198 | 7545 | 1720 | 834 | 0.00062174 | 6.9689e-06 | 89.2167 | 1 | 310 | Load | 4978 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | Ark - Series 3
J2001.008327 | PD-01222020-02217 | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4529 | 824529 | 2020-01-22 10:13 | 2020-01-22 11:31 | 77.73 | 1 | 1 | 5.3112 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 209 ALLIANCE CT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 128782 | 116027 | 3407 | 257 | 6.1689e-06 | 1.1615e-06 | 5.3112 | 1 | 310 | Customer | 65413 | Load | Tran3phWye | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008329 | PD-01222020-02245 | NORTHWEST | ENID | 4112:CHESTNUT | CHESTNUT_1221 | 411221 | 2020-01-22 10:23 | 2020-01-22 11:40 | 76.83 | 1 | 1 | 68.9667 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | ENID | 738 N 16TH | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860969 | 53522 | 37580 | 2858 | 1112 | 8.0104e-05 | 1.1615e-06 | 68.9667 | 1 | 320 | Customer | 3930 | Load | Tran1phOH | KEVIN N PERRYMAN | 601-528-2473 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008338 | PD-01222020-02257 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4026 | 834026 | 2020-01-22 10:46 | 2020-01-22 12:44 | 117.68 | 1 | 1 | 93.1333 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 5225 NW.111 TR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860969 | 128782 | 116027 | 10841 | 1209 | 0.00010817 | 1.1615e-06 | 93.1333 | 1 | 320 | Customer | 47449 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008347 | PD-01222020-02281 | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2923 | 812923 | 2020-01-22 11:06 | 2020-01-22 12:06 | 60.22 | 1 | 1 | 4.2634 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2808 SW.59 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 159107 | 102139 | 6380 | 1634 | 4.9519e-06 | 1.1615e-06 | 4.2634 | 1 | 310 | Customer | 44910 | Load | Tran1phPad | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008349 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-22 11:07 | 2020-01-22 12:25 | 77.55 | 1 | 1 | 55.1167 | 4 | DETERIORATION | 28 | CROSSARM | MOUNTAINBURG | RURAL | CMI_PLANNED | YES | NO | NO | 860969 | 82198 | 61170 | 3789 | 2585 | 6.4017e-05 | 1.1615e-06 | 55.1167 | 1 | 308 | Load | 9091 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-22 | 2020 |  | Ark - Series 2
J2001.008350 |  | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8124 | 838124 | 2020-01-22 11:10 | 2020-01-22 11:14 | 4.78 | 1 | 1 | 4.7833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 10522 HARVEST-MOON | CMI_MOMENTARY | YES | NO | NO | 860969 | 128782 | 116027 | 8955 | 1637 | 5.5558e-06 | 1.1615e-06 | 4.7833 | 1 | 310 | Customer | 58733 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008355 | PD-01222020-02388 | METRO NORTH | GUTHRIE | 8814:PINE STREET | PINE_STREET_1424 | 881424 | 2020-01-22 11:19 | 2020-01-22 12:51 | 92.32 | 1 | 1 | 92.3167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | GUTHRIE | 324 E.MANSUR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 168142 | 19817 | 3101 | 1237 | 0.00010722 | 1.1615e-06 | 92.3167 | 1 | 310 | Customer | 40163 | Load | Tran1phOH | JOSEPH WAYNE POOL | 405-919-2253 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008361 | PD-01222020-02409 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_869 | 830869 | 2020-01-22 11:47 | 2020-01-22 12:27 | 40.48 | 1 | 1 | 40.4833 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | NW 159th St Lot 13 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 168142 | 148325 | 19367 | 2464 | 4.7021e-05 | 1.1615e-06 | 40.4833 | 1 | 310 | Load | 406738 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008365 |  | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2622 | 862622 | 2020-01-22 11:58 | 2020-01-22 12:16 | 18.68 | 1 | 1 | 18.6833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1236 SE.21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 159107 | 102139 | 7416 | 349 | 2.17e-05 | 1.1615e-06 | 18.6833 | 1 | 310 | Customer | 31342 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008368 | PD-01222020-02430 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2029 | 862029 | 2020-01-22 12:16 | 2020-01-22 13:34 | 77.57 | 1 | 1 | 77.5667 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 424 SE 29TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 159107 | 102139 | 4745 | 983 | 9.0092e-05 | 1.1615e-06 | 77.5667 | 1 | 311 | Customer | 13319 | Load | TranOpenDelta | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008371 |  | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3723 | 913723 | 2020-01-22 12:26 | 2020-01-22 12:34 | 8.13 | 1 | 1 | 8.1333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | WALDRON RD AND GORDON LANE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 82198 | 61170 | 4566 | 734 | 9.4467e-06 | 1.1615e-06 | 8.1333 | 1 | 320 | Customer | 15593 | Load | Tran3phPadWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | Ark - Series 3
J2001.008372 | PD-01222020-02435 | METRO NORTH | GUTHRIE | 8807:CRESCENT | CRESCENT_721 | 880721 | 2020-01-22 12:28 | 2020-01-22 13:41 | 72.98 | 1 | 1 | 72.9833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | CRESCENT | N.OAK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 168142 | 19817 | 1764 | 872 | 8.4769e-05 | 1.1615e-06 | 72.9833 | 1 | 310 | Customer | 37404 | Load | Tran1phOH | KELLEY D WATSON | 405-763-8148 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008378 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1021 | 541021 | 2020-01-22 12:33 | 2020-01-22 12:37 | 4.33 | 844 | 9 | 3657.3333 | 4 | DETERIORATION | 47 | ARRESTOR OH | MADILL | 12537 HIGHWAY 199 | CMI_MOMENTARY | YES | NO | NO | 860969 | 77597 | 7199 | 2378 | 0 | 0.0042479 | 0.00098029 | 4.3333 | 1 | 310 | Substation | GLASSES_121 | Breaker | SubRecloser | [6 empty] | 06/02/2020 note from burchamc. Reference J2001.008378 in iDashboard report OSI_Job_Detail_Viewer. Manually completed blank Job Region, Job Area, etc. | Equipment | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008381 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1022 | 541022 | 2020-01-22 12:33 | 2020-01-22 12:48 | 15.22 | 1535 | 24 | 6447 | 17 | TRANSMISSION OPERATION | 45 | SUBSTATION CIRCUIT | MADILL | 12537 HIGHWAY 199 | CMI_NORMAL | NO | NO | NO | 860969 | 77597 | 7199 | 2378 | 0 | 0.0074881 | 0.0017829 | 4.2 | 1 | 310 | Substation | GLASSES_122 | Breaker | SubRecloser | [6 empty] | 06/02/2020 note from burchamc. Reference J2001.008381 in iDashboard report OSI_Job_Detail_Viewer. Manually completed blank Job Region, Job Area, etc. | Equipment | N | TRANSMISSION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008390 | PD-01222020-02433 | ARKANSAS | FORT SMITH | 9340:TWIN BRIDGES | TWIN_BRIDGES_4021 | 934021 | 2020-01-22 12:36 | 2020-01-22 13:47 | 71.48 | 1 | 1 | 71.4833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | VAN BUREN | 3102 OAK LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 82198 | 61170 | 1039 | 1039 | 8.3027e-05 | 1.1615e-06 | 71.4833 | 1 | 320 | Customer | 6421 | Load | TranOpenDelta | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-22 | 2020 |  | Ark - Series 1
J2001.008413 | PD-01222020-02438 | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8122 | 838122 | 2020-01-22 12:41 | 2020-01-22 14:56 | 135.07 | 1 | 1 | 81.0362 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 8219 NW 85TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 128782 | 116027 | 8955 | 971 | 9.4122e-05 | 1.1615e-06 | 81.0362 | 1 | 310 | Customer | 58493 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008422 | PD-01222020-02460 | ARKANSAS | POTEAU | 3608:MULDROW | MULDROW 23 | 360823 | 2020-01-22 13:00 | 2020-01-22 14:07 | 67.1 | 1 | 2 | 67.1 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MULDROW | WILSON ROCK RD-1 1/2MI S.HWY64 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 82198 | 13483 | 2270 | 486 | 7.7935e-05 | 1.1615e-06 | 67.1 | 1 | 320 | Load | 60103 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008424 | PD-01222020-02488 | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_521 | 890521 | 2020-01-22 13:02 | 2020-01-22 13:56 | 53.93 | 1 | 1 | 53.9333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | EL RENO | 205 N.WILLIAMS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 128782 | 12755 | 6943 | 2218 | 6.2643e-05 | 1.1615e-06 | 53.9333 | 1 | 310 | Customer | 41613 | Load | Tran1phOH | MICHAEL T MAHEN | 405-210-6029 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008434 | PD-01222020-02489 | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2222 | 882222 | 2020-01-22 13:36 | 2020-01-22 16:04 | 147.75 | 1 | 1 | 100.4 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | EDMOND | 1001 MESA TRAIL | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860969 | 168142 | 19817 | 5386 | 1160 | 0.00011661 | 1.1615e-06 | 100.4 | 1 | 320 | Customer | 49028 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008441 |  | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_624 | 410624 | 2020-01-22 13:49 | 2020-01-22 14:35 | 46.45 | 1 | 1 | 46.45 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ENID | 373 E.CHERRY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 53522 | 37580 | 6011 | 1860 | 5.3951e-05 | 1.1615e-06 | 46.45 | 1 | 310 | Customer | 224 | Load | TranOHDeltaSplitBank | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008448 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7021 | 817021 | 2020-01-22 14:09 | 2020-01-22 14:14 | 5.28 | 1 | 1 | 5.2833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 153B SW.74 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 159107 | 102139 | 9939 | 1790 | 6.1365e-06 | 1.1615e-06 | 5.2833 | 1 | 310 | Customer | 36312 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008449 | PD-01222020-02512 | METRO EAST | CHANDLER | 7117:JACKTOWN | JACKTOWN_1742 | 711742 | 2020-01-22 14:13 | 2020-01-22 15:46 | 92.65 | 1 | 1 | 92.65 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MEEKER | WHISPERING OAKS ADD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 114349 | 7462 | 1011 | 828 | 0.00010761 | 1.1615e-06 | 92.65 | 1 | 310 | Customer | 15842 | Load | Tran1phOH | SCOTT C PERRY | 405-258-6044 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008451 |  | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3925 | 833925 | 2020-01-22 14:18 | 2020-01-22 14:25 | 6.85 | 1 | 1 | 6.85 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 5412 WILLOWCLF RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 168142 | 148325 | 7850 | 2183 | 7.9562e-06 | 1.1615e-06 | 6.85 | 1 | 310 | Customer | 47743 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | OK - 2022
J2001.008464 |  | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6024 | 836024 | 2020-01-22 14:34 | 2020-01-22 18:05 | 211.3 | 5 | 3 | 940.375 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | NW 50 + COUNCIL RD | CMI_NORMAL | NO | NO | NO | 860969 | 128782 | 116027 | 5506 | 1343 | 0.0010922 | 5.8074e-06 | 188.075 | 1 | 310 | Tap | 37526 | Fuse | FuseOH | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | OK - 2022
J2001.008463 | PD-01222020-02539 | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5629 | 865629 | 2020-01-22 14:42 | 2020-01-22 15:49 | 67.47 | 1 | 1 | 67.4667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 5009 S.RHODE-ISL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 159107 | 102139 | 2751 | 731 | 7.8361e-05 | 1.1615e-06 | 67.4667 | 1 | 320 | Customer | 11205 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008465 |  | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_422 | 580422 | 2020-01-22 14:46 | 2020-01-22 14:59 | 13.77 | 1 | 1 | 13.7667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ADA | 500 E.20TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 77597 | 11512 | 3414 | 1428 | 1.599e-05 | 1.1615e-06 | 13.7667 | 1 | 310 | Customer | 15938 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008466 | PD-01222020-02558 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6024 | 836024 | 2020-01-22 14:49 | 2020-01-22 17:47 | 177.77 | 25 | 17 | 4323.75 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | NS,US-66/EAGLE LN. | CMI_NORMAL | NO | NO | NO | 860969 | 128782 | 116027 | 5506 | 1343 | 0.005022 | 2.9037e-05 | 172.95 | 1 | 310 | Mainline | 10209 | Fuse | FuseOH | TONY J ILG | 405-714-7441 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | OK - 2022
J2001.008469 | PD-01222020-02559 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4122 | 814122 | 2020-01-22 14:56 | 2020-01-22 17:00 | 124.13 | 1 | 1 | 124.1333 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 323 SW.45 | CMI_NORMAL | NO | NO | NO | 860969 | 159107 | 102139 | 5808 | 1271 | 0.00014418 | 1.1615e-06 | 124.1333 | 1 | 321 | Customer | 25074 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008471 | PD-01222020-02562 | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2724 | 872724 | 2020-01-22 14:59 | 2020-01-22 15:48 | 49.03 | 1 | 1 | 49.0333 | 4 | DETERIORATION | 15 | METER - SECONDARY | NORMAN | 800 LEXINGTON | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860969 | 159107 | 56968 | 6460 | 1255 | 5.6951e-05 | 1.1615e-06 | 49.0333 | 1 | 320 | Customer | 52623 | Load | Tran1phPad | GARRISON L COLE | 405-206-2908 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008475 |  | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6024 | 836024 | 2020-01-22 15:02 | 2020-01-22 18:06 | 183.68 | 1 | 1 | 183.6833 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | 4450 N.STINCHOMB | CMI_NORMAL | NO | NO | NO | 860969 | 128782 | 116027 | 5506 | 1343 | 0.00021334 | 1.1615e-06 | 183.6833 | 1 | 310 | Load | 89543 | Load | TranOpenDelta | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | OK - 2022
J2001.008481 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-22 15:22 | 2020-01-22 15:33 | 11.47 | 1 | 1 | 11.4667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | LAVACA | HOLT ADD.51300 EOF RIVER RD. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 82198 | 61170 | 2735 | 2123 | 1.3318e-05 | 1.1615e-06 | 11.4667 | 1 | 310 | Customer | 1400 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | Ark - Series 2
J2001.008484 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-22 15:31 | 2020-01-22 16:08 | 36.6 | 2 | 3 | 58.0166 | 4 | DETERIORATION | 28 | CROSSARM | MOUNTAINBURG | MTNBURG AR | CMI_PLANNED | YES | NO | NO | 860969 | 82198 | 61170 | 3789 | 2585 | 6.7385e-05 | 2.323e-06 | 29.0083 | 1 | 310 | Load | 8349 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-22 | 2020 |  | Ark - Series 2
J2001.008489 |  | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5629 | 865629 | 2020-01-22 15:49 | 2020-01-22 16:51 | 62.58 | 2 | 1 | 124.4 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | SEE 69TH AND TERRY | CMI_PLANNED | YES | NO | NO | 860969 | 159107 | 102139 | 2751 | 731 | 0.00014449 | 2.323e-06 | 62.2 | 1 | 308 | Load | 78054 | Load | Tran3phPadWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008493 |  | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1521 | 811521 | 2020-01-22 15:52 | 2020-01-22 16:00 | 7.85 | 1 | 1 | 7.85 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1412 SW.21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 159107 | 102139 | 6062 | 1243 | 9.1176e-06 | 1.1615e-06 | 7.85 | 1 | 310 | Customer | 6224 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | OK - 2022
J2001.008494 | PD-01222020-02669 | METRO WEST | WEST | 8359:YUKON | YUKON_5922 | 835922 | 2020-01-22 15:54 | 2020-01-22 18:31 | 156.95 | 1 | 1 | 156.95 | 4 | DETERIORATION | 50 | CONNECTOR | YUKON | 114 WALNUT | CMI_NORMAL | NO | NO | NO | 860969 | 128782 | 116027 | 6428 | 1637 | 0.00018229 | 1.1615e-06 | 156.95 | 1 | 310 | Customer | 19238 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008495 |  | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2922 | 812922 | 2020-01-22 15:56 | 2020-01-22 16:20 | 24.37 | 1 | 1 | 24.3667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 3504 S.GOFF | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 159107 | 102139 | 6380 | 1137 | 2.8301e-05 | 1.1615e-06 | 24.3667 | 1 | 310 | Customer | 36941 | Load | Tran1phOH | Ties | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008500 |  | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5424 | 865424 | 2020-01-22 16:05 | 2020-01-22 16:15 | 9.82 | 1 | 1 | 9.8167 | 1 | CANCELLED | 57 | CANCELLED | MOORE | 1116 BRYAN DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 159107 | 102139 | 9807 | 2010 | 1.1402e-05 | 1.1615e-06 | 9.8167 | 1 | 310 | Customer | 240866 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008501 | PD-01222020-02607 | METRO WEST | WEST | 8323:RICHARDS | RICHARDS_2324 | 832324 | 2020-01-22 16:06 | 2020-01-22 17:25 | 78.6 | 1 | 1 | 69.2 | 13 | PREMATURE FAILURE | 1 | TRANSFORMER UG | OKLAHOMA CITY | Carriage Way Blvd & NW 127th Lot 2 | CMI_NORMAL | NO | NO | NO | 860969 | 128782 | 116027 | 5013 | 1600 | 8.0375e-05 | 1.1615e-06 | 69.2 | 1 | 310 | Customer | 302678 | Load | Tran1phPad | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008505 | PD-01222020-02608 | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-01-22 16:13 | 2020-01-22 17:22 | 68.83 | 1 | 1 | 68.8333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 8741 HILLVIEW DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 159107 | 56968 | 4240 | 1005 | 7.9949e-05 | 1.1615e-06 | 68.8333 | 1 | 320 | Customer | 20154 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008509 |  | SOUTHERN | ARDMORE | 5106:HARRIS ST | HARRIS_ST_623 | 510623 | 2020-01-22 16:21 | 2020-01-22 16:25 | 4.42 | 1 | 1 | 4.4167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ARDMORE | NW OF HUDSON VLY/CIMMERON DR | CMI_MOMENTARY | YES | NO | NO | 860969 | 77597 | 23587 | 2069 | 900 | 5.1299e-06 | 1.1615e-06 | 4.4167 | 1 | 310 | Customer | 23963 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008518 | PD-01222020-02632 | METRO WEST | WEST | 8359:YUKON | YUKON_5923 | 835923 | 2020-01-22 16:43 | 2020-01-22 20:34 | 230.55 | 1 | 2 | 206.4667 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | YUKON | 25 CEDAR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860969 | 128782 | 116027 | 6428 | 1150 | 0.00023981 | 1.1615e-06 | 206.4667 | 1 | 320 | Customer | 41077 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008520 | PD-01222020-02644 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2024 | 862024 | 2020-01-22 16:51 | 2020-01-22 18:50 | 118.63 | 1 | 1 | 118.6333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3107 S BROADWAY AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 159107 | 102139 | 4745 | 770 | 0.00013779 | 1.1615e-06 | 118.6333 | 1 | 320 | Customer | 12431 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008522 | PD-01222020-02657 | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_626 | 550626 | 2020-01-22 16:53 | 2020-01-22 19:41 | 167.32 | 997 | 6 | 3090.85 | 5 | ELECTRICAL TRACKING | 28 | CROSSARM | DURANT | 1400 BRYAN DR | CMI_NORMAL | NO | NO | NO | 860969 | 77597 | 15485 | 6736 | 1000 | 0.00359 | 0.001158 | 3.1002 | 1 | 310 | Feeder | BODLE ST_626 | Recloser | SubRecloser | JEREMY L MULLENS | 580-775-3134 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008528 | PD-01222020-02656 | METRO WEST | WEST | 8335:BETHANY | BETHANY_3527 | 833527 | 2020-01-22 16:57 | 2020-01-22 18:05 | 68.47 | 5 | 9 | 330.9167 | 11 | OVERLOAD | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 4116 N.LIBBY | CMI_NORMAL | NO | NO | NO | 860969 | 128782 | 116027 | 7868 | 1662 | 0.00038435 | 5.8074e-06 | 66.1833 | 1 | 310 | Load | 50455 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | OK - 2022
J2001.008523 | PD-01222020-02658 | NORTHWEST | ALVA | 4528:SALINE | SALINE 23 | 452823 | 2020-01-22 16:57 | 2020-01-22 18:46 | 108.9 | 1 | 1 | 108.9 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | HELENA | 1ST and HINKLEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 53522 | 5520 | 668 | 318 | 0.00012649 | 1.1615e-06 | 108.9 | 1 | 310 | Customer | 1640 | Load | Tran1phOH | RANDY D MASON | 580-977-8823 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008525 |  | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4122 | 814122 | 2020-01-22 17:00 | 2020-01-22 17:13 | 12.2 | 1 | 1 | 12.2 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 2 W.ALPINE DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 159107 | 102139 | 5808 | 1271 | 1.417e-05 | 1.1615e-06 | 12.2 | 1 | 310 | Customer | 12564 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008530 | PD-01222020-02662 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-22 17:06 | 2020-01-23 00:55 | 469.18 | 80 | 60 | 35749.3333 | 22 | WIND | 37 | CONDUCTOR PRIMARY - OH | MOUNTAINBURG | 71 @ HL 7/16 | CMI_NORMAL | NO | NO | NO | 860969 | 82198 | 61170 | 3789 | 2585 | 0.041522 | 9.2919e-05 | 446.8667 | 1 | 311 | Mainline | 3644 | Fuse | FuseOH | DWAIN C CAUGHERN | 479-459-0231 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-22 | 2020 |  | Ark - Series 2
J2001.008537 | PD-01222020-02661 | METRO EAST | SEMINOLE | 7208:CYPRESS | CYPRESS_821 | 720821 | 2020-01-22 17:12 | 2020-01-22 18:16 | 64.38 | 1 | 1 | 45.9333 | 22 | WIND | 34 | CONDUCTOR SECONDARY - OH | HOLDENVILLE | W ON OAK ST | CMI_NORMAL | NO | NO | NO | 860969 | 114349 | 13604 | 2521 | 1089 | 5.3351e-05 | 1.1615e-06 | 45.9333 | 1 | 310 | Customer | 582 | Load | Tran1phOH | DELBERT HISAW | 405-683-1721 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008538 | PD-01222020-02664 | METRO EAST | SEMINOLE | 7208:CYPRESS | CYPRESS_822 | 720822 | 2020-01-22 17:13 | 2020-01-22 18:41 | 88.2 | 1 | 1 | 88.2 | 22 | WIND | 31 | CONDUCTOR SERVICE - OH | HOLDENVILLE | 118 S.CHERRY | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860969 | 114349 | 13604 | 2521 | 1432 | 0.00010244 | 1.1615e-06 | 88.2 | 1 | 310 | Customer | 11862 | Load | Tran1phOH | DELBERT HISAW | 405-683-1721 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | OK - 2020
J2001.008539 | PD-01222020-02666 | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1722 | 911722 | 2020-01-22 17:13 | 2020-01-22 19:44 | 150.55 | 1 | 1 | 150.55 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | NE of Rome Way | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 82198 | 61170 | 4241 | 1474 | 0.00017486 | 1.1615e-06 | 150.55 | 1 | 310 | Customer | 310734 | Load | Tran1phPad | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-22 | 2020 |  | #N/A
J2001.008543 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6126 | 836126 | 2020-01-22 17:20 | 2020-01-22 19:37 | 137.38 | 1 | 0 | 94.6667 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | 3228 N.SANTA-FE | CMI_PLANNED | YES | NO | NO | 860969 | 168142 | 148325 | 11100 | 456 | 0.00010995 | 1.1615e-06 | 94.6667 | 1 | 0 | Load | 28510 | Load | Tran3phPadWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | OK - 2022
J2001.008544 | PD-01222020-02667 | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1221 | 911221 | 2020-01-22 17:21 | 2020-01-22 18:04 | 43.48 | 3 | 3 | 472.15 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | FORT SMITH | 2110 S.L | CMI_NORMAL | NO | NO | NO | 860969 | 82198 | 61170 | 6595 | 1742 | 0.00054839 | 3.4844e-06 | 157.3833 | 1 | 310 | Secondary | 560 | Load | Tran1phOH | DWAIN C CAUGHERN | 479-459-0231 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | Ark - Series 1
J2001.008545 |  | METRO EAST | EAST | 8471:NE 30TH ST | NE_30TH_ST_7123 | 847123 | 2020-01-22 17:26 | 2020-01-22 18:13 | 46.83 | 8 | 6 | 309.4667 | 4 | DETERIORATION | 50 | CONNECTOR | FOREST PARK | 3117 N Forest Park Dr | CMI_NORMAL | NO | NO | NO | 860969 | 114349 | 71182 | 2401 | 1293 | 0.00035944 | 9.2919e-06 | 38.6833 | 1 | 310 | Load | 348867 | Load | TranOpenDelta | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | OK - 2022
J2001.008548 | PD-01222020-02670 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-22 17:32 | 2020-01-23 06:01 | 749.08 | 3 | 1 | 2231.25 | 29 | TREES : GROW IN | 37 | CONDUCTOR PRIMARY - OH | MOUNTAINBURG | 13583 ST HWY 348 | CMI_NORMAL | NO | NO | NO | 860969 | 82198 | 61170 | 3789 | 2585 | 0.0025916 | 3.4844e-06 | 743.75 | 1 | 310 | Mainline | 3074 | Fuse | FuseOH | DWAIN C CAUGHERN | 479-459-0231 | [5 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-22 | 2020 |  | Ark - Series 2
J2001.008549 | PD-01222020-02671 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3023 | 743023 | 2020-01-22 17:39 | 2020-01-22 18:30 | 50.9 | 1 | 1 | 50.9 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BETHEL ACRES | LOT 12 BLK 2-SQUIRREL CREEK ES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 114349 | 22101 | 6641 | 1137 | 5.9119e-05 | 1.1615e-06 | 50.9 | 1 | 310 | Customer | 18594 | Load | Tran1phPad | ADAM CLARK | 580-310-8924 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | OK - 2021
J2001.008553 | PD-01222020-02673 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3731 | 833731 | 2020-01-22 17:42 | 2020-01-22 19:48 | 125.65 | 2 | 2 | 251.3 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | THE VILLAGE | 1716 SHEFFIELD RD | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860969 | 168142 | 148325 | 5764 | 1903 | 0.00029188 | 2.323e-06 | 125.65 | 1 | 310 | Secondary | 23061 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | OK - 2020
J2001.008552 |  | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3923 | 833923 | 2020-01-22 17:47 | 2020-01-22 17:54 | 7.3 | 1 | 1 | 7.3 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3500 NW.51 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 168142 | 148325 | 7850 | 1246 | 8.4788e-06 | 1.1615e-06 | 7.3 | 1 | 310 | Customer | 24692 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | OK - 2022
J2001.008561 | PD-01222020-02677 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-22 18:27 | 2020-01-22 21:03 | 155.83 | 48 | 30 | 7320 | 7 | ICE / SLEET / SNOW | 23 | FUSE - PRIMARY | ALMA | NE 71 +NWBRY CH RD 1/4 | CMI_NORMAL | NO | NO | NO | 860969 | 82214 | 61184 | 3789 | 2585 | 0.008502 | 5.5751e-05 | 152.5 | 1 | 310 | Mainline | 3637 | Fuse | FuseOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-22 | 2020 |  | Ark - Series 2
J2001.008576 | PD-01222020-02676 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-22 18:33 | 2020-01-22 21:56 | 203.23 | 39 | 45 | 6730.75 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | MOUNTAINBURG | 71 @ HL 6/9 | CMI_NORMAL | NO | NO | NO | 860969 | 82214 | 61184 | 3789 | 2585 | 0.0078176 | 4.5298e-05 | 172.5833 | 1 | 310 | Mainline | 3642 | Fuse | FuseOH | DWAIN C CAUGHERN | 479-459-0231 | [5 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-22 | 2020 |  | Ark - Series 2
J2001.008589 | PD-01222020-02685 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4124 | 814124 | 2020-01-22 19:16 | 2020-01-22 21:21 | 124.65 | 1 | 1 | 114.55 | 27 | TREE:NON PREVENTABLE | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 801 SW.49 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860969 | 159116 | 102144 | 5808 | 2012 | 0.00013305 | 1.1615e-06 | 114.55 | 1 | 310 | Customer | 17449 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008591 |  | SOUTHERN | ARDMORE | 5106:HARRIS ST | HARRIS_ST_623 | 510623 | 2020-01-22 19:21 | 2020-01-22 19:56 | 35.05 | 1 | 1 | 35.05 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ARDMORE | NW OF HUDSON VLY/CIMMERON DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 77598 | 23585 | 2069 | 900 | 4.071e-05 | 1.1615e-06 | 35.05 | 1 | 310 | Customer | 23963 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008596 | PD-01222020-02687 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-22 19:52 | 2020-01-23 13:12 | 1040.43 | 11 | 14 | 11395.8167 | 7 | ICE / SLEET / SNOW | 23 | FUSE - PRIMARY | MOUNTAINBURG | 348 1 MILE E. HWY 71 | CMI_NORMAL | NO | NO | NO | 860969 | 82214 | 61184 | 3789 | 2585 | 0.013236 | 1.2776e-05 | 1035.9833 | 1 | 310 | Mainline | 3587 | Fuse | FuseOH | KRIS L HALMES | 479-430-9447 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-22 | 2020 |  | Ark - Series 2
J2001.008607 | PD-01222020-02693 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2263 | 852263 | 2020-01-22 20:15 | 2020-01-23 00:22 | 247.2 | 1 | 2 | 5.4833 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | JONES | 6900 N HIWASSEE | CMI_EQUIP_EXCLUSION | YES | NO | NO | 860969 | 114360 | 71188 | 11630 | 1535 | 6.3688e-06 | 1.1615e-06 | 5.4833 | 1 | 320 | Customer | 345674 | Load | Tran1phOH | DAVID M CLEMMONS | 405-777-8355 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | OK - 2021
J2001.008606 | PD-01222020-02695 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-22 20:15 | 2020-01-23 12:39 | 984.18 | 18 | 5 | 17715.6 | 27 | TREE:NON PREVENTABLE | 37 | CONDUCTOR PRIMARY - OH | WINSLOW | DEVILS DEN RD + HWY 71 | CMI_NORMAL | NO | NO | NO | 860969 | 82214 | 61184 | 3789 | 2585 | 0.020576 | 2.0907e-05 | 984.2 | 1 | 311 | Mainline | 2251 | Fuse | FuseOH | LANCE M BECKER | 479-883-5087 | [5 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-22 | 2020 |  | Ark - Series 2
J2001.008625 | PD-01222020-02702 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6022 | 836022 | 2020-01-22 21:17 | 2020-01-23 02:30 | 313.37 | 21 | 7 | 5641.3 | 4 | DETERIORATION | 28 | CROSSARM | BETHANY | WILBURN / NW 36TH | CMI_NORMAL | NO | NO | NO | 860969 | 128791 | 116036 | 5506 | 1232 | 0.0065523 | 2.4391e-05 | 268.6333 | 1 | 310 | Mainline | 13566 | Fuse | FuseOH | HOWARD GETCHELL | 530-410-8920 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | OK - 2022
J2001.008619 |  | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6022 | 836022 | 2020-01-22 21:21 | 2020-01-23 02:30 | 309.13 | 4 | 4 | 1056.9333 | 4 | DETERIORATION | 28 | CROSSARM | BETHANY | 3406 N.WILBURN DR | CMI_NORMAL | NO | NO | NO | 860969 | 128791 | 116036 | 5506 | 1232 | 0.0012276 | 4.6459e-06 | 264.2333 | 1 | 310 | Secondary | 21302 | Load | Tran1phOH | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | OK - 2022
J2001.008629 |  | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_624 | 410624 | 2020-01-22 21:32 | 2020-01-22 21:47 | 14.78 | 1 | 1 | 14.7833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ENID | 523 W.WALNUT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 53529 | 37585 | 6012 | 1859 | 1.7171e-05 | 1.1615e-06 | 14.7833 | 1 | 310 | Customer | 5118 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008643 | PD-01222020-02707 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-22 21:52 | 2020-01-23 06:24 | 512.13 | 32 | 25 | 16310.4 | 7 | ICE / SLEET / SNOW | 23 | FUSE - PRIMARY | MOUNTAINBURG | CAIN SCH.RD.E.-HWY 712 | CMI_NORMAL | NO | NO | NO | 860969 | 82214 | 61184 | 3789 | 2585 | 0.018944 | 3.7167e-05 | 509.7 | 1 | 310 | Mainline | 3132 | Fuse | FuseOH | DWAIN C CAUGHERN | 479-459-0231 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-22 | 2020 |  | Ark - Series 2
J2001.008651 | PD-01222020-02709 | ARKANSAS | POTEAU | 3608:MULDROW | MULDROW 21 | 360821 | 2020-01-22 21:57 | 2020-01-22 22:46 | 49.08 | 6 | 10 | 281.6 | 5 | ELECTRICAL TRACKING | 21 | FUSE - TRANSFORMER | MULDROW | 110 N.CADDO | CMI_NORMAL | NO | NO | NO | 860969 | 82214 | 13485 | 2270 | 1224 | 0.00032707 | 6.9689e-06 | 46.9333 | 1 | 310 | Load | 10225 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-22 | 2020 |  | #N/A
J2001.008654 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-22 22:11 | 2020-01-22 22:20 | 8.45 | 1 | 1 | 8.45 | 1 | CANCELLED | 57 | CANCELLED | ALMA | DOW JONES RD, 3/4 MI E-HWY 71 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 860969 | 82214 | 61184 | 3789 | 2585 | 9.8145e-06 | 1.1615e-06 | 8.45 | 1 | 310 | Customer | 17074 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-22 | 2020 |  | Ark - Series 2
J2001.008661 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-22 22:25 | 2020-01-23 00:28 | 122.65 | 1 | 0 | 56.9333 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | 0 | E OF HWY22 ON DOWJONES | CMI_NORMAL | NO | NO | NO | 860969 | 82214 | 61184 | 3789 | 2585 | 6.6127e-05 | 1.1615e-06 | 56.9333 | 1 | 0 | Tap | 4442 | Fuse | FuseOH | Crew | [6 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-22 | 2020 |  | Ark - Series 2
J2001.008663 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-22 22:34 | 2020-01-23 00:21 | 107.43 | 25 | 2 | 934.5833 | 29 | TREES : GROW IN | 37 | CONDUCTOR PRIMARY - OH | ALMA | 71 @ HL 6/12 | CMI_NORMAL | NO | NO | NO | 860969 | 82214 | 61184 | 3789 | 2585 | 0.0010855 | 2.9037e-05 | 37.3833 | 1 | 310 | Tap | 4388 | Fuse | FuseOH | 1187: NOT FOUND 1187: NOT FOUND | [6 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-22 | 2020 |  | Ark - Series 2
J2001.008672 | PD-01222020-02716 | SOUTHERN | DURANT | 5512:COLBERT | COLBERT_1221 | 551221 | 2020-01-22 23:12 | 2020-01-23 09:03 | 590.77 | 1 | 2 | 110.4333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | CALERA | 506 WILSON AVE | CMI_NORMAL | NO | NO | NO | 860969 | 77598 | 15486 | 2166 | 894 | 0.00012827 | 1.1615e-06 | 110.4333 | 1 | 310 | Customer | 22640 | Load | Tran1phOH | JEREMY L MULLENS | 580-775-3134 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-22 | 2020 |  | #N/A
J2001.008700 | PD-01232020-00002 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2021 | 822021 | 2020-01-23 04:22 | 2020-01-23 06:05 | 102.92 | 1 | 1 | 98.1667 | 4 | DETERIORATION | 20 | FUSE BARREL | OKLAHOMA CITY | 2901 NW.10 | CMI_NORMAL | NO | NO | NO | 861024 | 168155 | 148336 | 6037 | 1113 | 0.00011401 | 1.1614e-06 | 98.1667 | 1 | 310 | Load | 3111 | Load | TranOpenDelta | DARREN L STOCKTON | 918-777-1697 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | OK - 2020
J2001.008705 | PD-01232020-00003 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-23 04:40 | 2020-01-23 10:16 | 336.38 | 23 | 11 | 7354.9983 | 7 | ICE / SLEET / SNOW | 37 | CONDUCTOR PRIMARY - OH | MOUNTAINBURG | 3100 HARMONY RD | CMI_NORMAL | NO | NO | NO | 861024 | 82214 | 61184 | 3789 | 2585 | 0.0085422 | 2.6712e-05 | 319.7825 | 1 | 310 | Mainline | 355223 | Switch | SwitchOH | [7 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-23 | 2020 |  | Ark - Series 2
J2001.008712 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-23 05:03 | 2020-01-23 06:50 | 106.72 | 38 | 0 | 4055.6646 | 7 | ICE / SLEET / SNOW | 23 | FUSE - PRIMARY | 0 | 348 AND TURNER ROAD | CMI_NORMAL | NO | NO | NO | 861024 | 82214 | 61184 | 3789 | 2585 | 0.0047103 | 4.4133e-05 | 106.728 | 1 | 0 | Mainline | 6776 | Fuse | FuseOH | DWAIN C CAUGHERN | 479-459-0231 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-01-23 | 2020 |  | Ark - Series 2
J2001.008715 | PD-01232020-00005 | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-23 05:18 | 2020-01-23 08:58 | 220.12 | 4 | 2 | 867.4667 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | BLOOMER | FEATHER HILL RD,500N22 | CMI_NORMAL | NO | NO | NO | 861024 | 82214 | 61184 | 2735 | 2123 | 0.0010075 | 4.6456e-06 | 216.8667 | 1 | 310 | Mainline | 4324 | Fuse | FuseOH | [7 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | Ark - Series 2
J2001.008718 | PD-01232020-00004 | SOUTHERN | DURANT | 5504:BUTTERFIELD | BUTTERFIELD_429 | 550429 | 2020-01-23 05:26 | 2020-01-23 08:30 | 183.6 | 1 | 1 | 183.6 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DURANT | 614 SO 7TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 77598 | 15486 | 3485 | 1272 | 0.00021323 | 1.1614e-06 | 183.6 | 1 | 320 | Customer | 6155 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008724 | PD-01232020-00009 | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1421 | 911421 | 2020-01-23 06:02 | 2020-01-23 10:47 | 285.3 | 1 | 2 | 28.8833 | 12 | POOR CONNECTION | 50 | CONNECTOR | FORT SMITH | 2217 N.31, S-WARNER | CMI_NORMAL | NO | NO | NO | 861024 | 82214 | 61184 | 4738 | 1747 | 3.3545e-05 | 1.1614e-06 | 28.8833 | 1 | 310 | Customer | 5449 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-23 | 2020 |  | Ark - Series 1
J2001.008725 | PD-01232020-00010 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_866 | 830866 | 2020-01-23 06:06 | 2020-01-23 07:49 | 102.68 | 34 | 35 | 2442.9 | 5 | ELECTRICAL TRACKING | 39 | BUSHING | OKLAHOMA CITY | 14300 N. MAY AVE | CMI_NORMAL | NO | NO | NO | 861024 | 168155 | 148336 | 19368 | 4303 | 0.0028372 | 3.9488e-05 | 71.85 | 1 | 310 | Mainline | 189627 | Fuse | FuseRiser | JEFFREY T WARNER | 405-397-2026 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008727 | PD-01232020-00011 | SOUTHERN | PAULS VALLEY | 5620:PRAIRIE POINT | PRAIRIE_POINT_2021 | 562021 | 2020-01-23 06:17 | 2020-01-23 11:24 | 306.63 | 1 | 1 | 301.0333 | 4 | DETERIORATION | 47 | ARRESTOR OH | ELMORE CITY | 1MN SH29 ON SH74 | CMI_NORMAL | NO | NO | NO | 861024 | 77598 | 6207 | 607 | 569 | 0.00034962 | 1.1614e-06 | 301.0333 | 1 | 310 | Load | 30313 | Load | Tran1phOH | CAMERON BRADY | 580-307-7052 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2021
J2001.008733 | PD-01232020-00020 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7029 | 817029 | 2020-01-23 06:50 | 2020-01-23 07:58 | 68.15 | 1 | 1 | 40.1935 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | BLDG 1900 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 159116 | 102144 | 9938 | 1756 | 4.6681e-05 | 1.1614e-06 | 40.1935 | 1 | 310 | Customer | 200329 | Load | Tran1phPad | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2022
J2001.008736 | PD-01232020-00021 | METRO WEST | WEST | 8158:SARA | SARA_5871 | 815871 | 2020-01-23 07:11 | 2020-01-23 08:37 | 86.28 | 1 | 2 | 80.2167 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 11013 SW 35th St. | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861024 | 128791 | 116036 | 18246 | 5395 | 9.3164e-05 | 1.1614e-06 | 80.2167 | 1 | 320 | Customer | 384875 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2022
J2001.008742 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4031 | 834031 | 2020-01-23 07:42 | 2020-01-23 07:52 | 10.65 | 1 | 1 | 10.65 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 9212 N.MACARTHUR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 128791 | 116036 | 10841 | 1641 | 1.2369e-05 | 1.1614e-06 | 10.65 | 1 | 310 | Customer | 42418 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008743 |  | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6523 | 836523 | 2020-01-23 07:42 | 2020-01-23 07:48 | 6.12 | 1 | 1 | 6.1167 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 7305 LYREWOOD LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 128791 | 116036 | 7422 | 2258 | 7.1039e-06 | 1.1614e-06 | 6.1167 | 1 | 310 | Customer | 38608 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2022
J2001.008744 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-01-23 07:43 | 2020-01-23 07:51 | 8.48 | 1 | 1 | 8.4833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 317 NW.24 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 168155 | 148336 | 11100 | 2336 | 9.8526e-06 | 1.1614e-06 | 8.4833 | 1 | 310 | Customer | 1390 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2020
J2001.008745 | PD-01232020-00031 | METRO EAST | CHANDLER | 7118:KEY WEST | KEY_WEST_1847 | 711847 | 2020-01-23 07:51 | 2020-01-23 09:42 | 111.07 | 1 | 1 | 102.5167 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | DAVENPORT | BEHIND #19 NORTH PARK ESTATES | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861024 | 114360 | 7462 | 1212 | 743 | 0.00011906 | 1.1614e-06 | 102.5167 | 1 | 310 | Customer | 18064 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2021
J2001.008746 |  | ARKANSAS | FORT SMITH | 9508:WHITESIDE | WHITESIDE_822 | 950822 | 2020-01-23 07:54 | 2020-01-23 07:54 | 0 | 209 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | VAN BUREN | 2721 INDUSTRIAL PAR RD | CMI_MOMENTARY | YES | NO | NO | 861024 | 82214 | 61184 | 1919 | 209 | 0 | 0.00024273 | 0 | 1 | 0 | Feeder | WHITESIDE_822 | Recloser | 0 | [7 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-23 | 2020 |  | Ark - Series 2
J2001.008749 | PD-01232020-00053 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-01-23 08:03 | 2020-01-23 09:58 | 115.47 | 1 | 2 | 78.0794 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 2033 NW.21 | CMI_NORMAL | NO | NO | NO | 861024 | 168155 | 148336 | 11100 | 2037 | 9.0682e-05 | 1.1614e-06 | 78.0794 | 1 | 320 | Customer | 1117 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2021
J2001.008752 | PD-01232020-00064 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7029 | 817029 | 2020-01-23 08:13 | 2020-01-23 09:26 | 72.93 | 1 | 2 | 72.9333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | BLDG 1900 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 159116 | 102144 | 9938 | 1756 | 8.4705e-05 | 1.1614e-06 | 72.9333 | 1 | 310 | Customer | 200329 | Load | Tran1phPad | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2022
J2001.008757 | PD-01232020-00069 | SOUTHERN | SULPHUR | 5705:SULPHUR | SULPHUR_521 | 570521 | 2020-01-23 08:24 | 2020-01-23 08:54 | 30.23 | 1 | 1 | 30.2333 | 28 | OTHER (DESCRIBE) | 23 | FUSE - PRIMARY | SULPHUR | 914 E TULSA | CMI_NORMAL | NO | NO | NO | 861024 | 77598 | 6811 | 3630 | 754 | 3.5113e-05 | 1.1614e-06 | 30.2333 | 1 | 310 | Customer | 15594 | Load | Tran1phOH | CHAD A DOTSON | 405-488-5658 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008760 | PD-01232020-00073 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-01-23 08:33 | 2020-01-23 09:10 | 37.37 | 1 | 1 | 34.9879 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 317 NW.24 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 168155 | 148336 | 11100 | 2336 | 4.0635e-05 | 1.1614e-06 | 34.9879 | 1 | 310 | Customer | 1390 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2020
J2001.008761 | PD-01232020-00091 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-23 08:38 | 2020-01-23 13:54 | 316.07 | 1 | 2 | 316.0667 | 27 | TREE:NON PREVENTABLE | 37 | CONDUCTOR PRIMARY - OH | MOUNTAINBURG | RURAL ALMA-WINSLOW | CMI_NORMAL | NO | NO | NO | 861024 | 82214 | 61184 | 3789 | 2585 | 0.00036708 | 1.1614e-06 | 316.0667 | 1 | 310 | Customer | 2426 | Load | Tran1phOH | LANCE M BECKER | 479-883-5087 | [5 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-23 | 2020 |  | Ark - Series 2
J2001.008762 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-23 08:38 | 2020-01-23 09:35 | 56.67 | 3 | 4 | 170.95 | 29 | TREES : GROW IN | 37 | CONDUCTOR PRIMARY - OH | MOUNTAINBURG | 13583 ST HWY 348 | CMI_NORMAL | NO | NO | NO | 861024 | 82214 | 61184 | 3789 | 2585 | 0.00019854 | 3.4842e-06 | 56.9833 | 1 | 310 | Mainline | 3074 | Fuse | FuseOH | [7 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-23 | 2020 |  | Ark - Series 2
J2001.008765 | PD-01232020-00097 | ARKANSAS | POTEAU | 3508:SPIRO COAL | SPIRO COAL 21 | 350821 | 2020-01-23 08:54 | 2020-01-23 10:23 | 88.97 | 1 | 1 | 75.55 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | SPIRO | .75MS OF SPIRO COAL SUB ON P COLLINS RD | CMI_NORMAL | NO | NO | NO | 861024 | 82214 | 13485 | 380 | 377 | 8.7744e-05 | 1.1614e-06 | 75.55 | 1 | 310 | Load | 235525 | Load | Tran3phWye | JOHN MEEH | 918-413-0959 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | #N/A
J2001.008768 | PD-01232020-00103 | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-01-23 09:02 | 2020-01-23 11:44 | 161.68 | 1 | 1 | 21.8276 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | NORMAN | 13980 DEER CREEK ROAD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 159116 | 56972 | 4240 | 3071 | 2.5351e-05 | 1.1614e-06 | 21.8276 | 1 | 310 | Load | 74949 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008771 | PD-01232020-00104 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_722 | 870722 | 2020-01-23 09:08 | 2020-01-23 10:57 | 108.73 | 1 | 2 | 97.2833 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | NORMAN | 2112 BOIS-DE-ARC CI | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861024 | 159116 | 56972 | 11835 | 1582 | 0.00011299 | 1.1614e-06 | 97.2833 | 1 | 310 | Customer | 56757 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008770 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-01-23 09:10 | 2020-01-23 11:39 | 148.75 | 1 | 1 | 39.9 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 10717 S.RAYBURN | CMI_PLANNED | YES | NO | NO | 861024 | 159116 | 56972 | 4240 | 1005 | 4.634e-05 | 1.1614e-06 | 39.9 | 1 | 308 | Load | 56302 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008773 | PD-01232020-00114 | METRO EAST | EAST | 8542:RENO | RENO_4229 | 854229 | 2020-01-23 09:12 | 2020-01-23 10:34 | 81.57 | 4 | 6 | 318.1 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MIDWEST CITY | 5700 SE.8 | CMI_NORMAL | NO | NO | NO | 861024 | 114360 | 71188 | 5215 | 1344 | 0.00036944 | 4.6456e-06 | 79.525 | 1 | 310 | Load | 16716 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2022
J2001.008775 |  | METRO WEST | WEST | 8222:CZECH HALL | CZECH_HALL_2224 | 822224 | 2020-01-23 09:16 | 2020-01-23 09:26 | 9.48 | 1 | 1 | 9.4833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | YUKON | 633 VANDAMENT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 128791 | 116036 | 8605 | 1332 | 1.1014e-05 | 1.1614e-06 | 9.4833 | 1 | 310 | Customer | 50246 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008777 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-23 09:22 | 2020-01-23 11:08 | 105.77 | 26 | 9 | 2676.2667 | 4 | DETERIORATION | 1 | TRANSFORMER UG | ALMA | ALAMO DUPLEXES N-DYER | CMI_PLANNED | YES | NO | NO | 861024 | 82214 | 61184 | 3789 | 2585 | 0.0031082 | 3.0197e-05 | 102.9333 | 1 | 310 | Mainline | 3960 | Fuse | FuseRiser | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-23 | 2020 |  | Ark - Series 2
J2001.008778 | PD-01232020-00145 | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2131 | 332131 | 2020-01-23 09:25 | 2020-01-23 10:42 | 77.07 | 1 | 1 | 77.0667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKAY | OKAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 74032 | 33265 | 3336 | 1174 | 8.9506e-05 | 1.1614e-06 | 77.0667 | 1 | 310 | Customer | 3412 | Load | TranOpenDelta | JAMES C EVANS | 918-869-1174 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-23 | 2020 |  | #N/A
J2001.008782 | PD-01232020-00125 | NORTHWEST | ALVA | 4707:KNOBHILL | KNOBHILL_732 | 470732 | 2020-01-23 09:37 | 2020-01-23 12:24 | 166.77 | 1 | 1 | 166.7667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ALVA | ALVA 1439 YOUNG | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 53529 | 5520 | 1743 | 354 | 0.00019368 | 1.1614e-06 | 166.7667 | 1 | 310 | Customer | 9516 | Load | Tran1phOH | RANDY D MASON | 580-977-8823 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | #N/A
J2001.008787 | PD-01232020-00143 | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3722 | 913722 | 2020-01-23 09:43 | 2020-01-23 11:55 | 131.88 | 1 | 1 | 131.8833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 5900 KINKEAD AV 122 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 82214 | 61184 | 4569 | 1440 | 0.00015317 | 1.1614e-06 | 131.8833 | 1 | 310 | Customer | 12438 | Load | Tran1phPad | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | Ark - Series 3
J2001.008786 | PD-01232020-00144 | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2129 | 332129 | 2020-01-23 09:44 | 2020-01-23 11:17 | 93 | 1 | 1 | 93 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT GIBSON | WILEY ST, SOUTH OF HWY 62 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 74032 | 33265 | 3336 | 942 | 0.00010801 | 1.1614e-06 | 93 | 1 | 310 | Customer | 16878 | Load | Tran1phPad | JAMES C EVANS | 918-869-1174 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-23 | 2020 |  | #N/A
J2001.008790 | PD-01232020-00160 | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2724 | 872724 | 2020-01-23 09:51 | 2020-01-23 11:23 | 92.37 | 1 | 1 | 64.6315 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | 113 W.RICH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 159116 | 56972 | 6462 | 1255 | 7.5064e-05 | 1.1614e-06 | 64.6315 | 1 | 310 | Customer | 44688 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008793 | PD-01232020-00162 | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8131 | 838131 | 2020-01-23 10:02 | 2020-01-23 11:13 | 71.33 | 1 | 2 | 22.8897 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 7612 Lipizzan Rd | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861024 | 128791 | 116036 | 8955 | 1830 | 2.6584e-05 | 1.1614e-06 | 22.8897 | 1 | 310 | Customer | 401243 | Load | Tran1phPad | BAD ORDER UG RES COORD | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008795 | PD-01232020-00155 | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 21 | 570821 | 2020-01-23 10:03 | 2020-01-23 10:30 | 26.93 | 1 | 1 | 26.9333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DAVIS | TUMBLEWOOD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 77598 | 6811 | 1859 | 904 | 3.1281e-05 | 1.1614e-06 | 26.9333 | 1 | 310 | Customer | 21827 | Load | Tran1phOH | CHAD A DOTSON | 405-488-5658 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | OK - 2021
J2001.008800 | PD-01232020-00167 | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4524 | 824524 | 2020-01-23 10:10 | 2020-01-23 11:04 | 53.88 | 1 | 1 | 15.5403 | 4 | DETERIORATION | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 7220 W.RENO | CMI_NORMAL | NO | NO | NO | 861024 | 128791 | 116036 | 3407 | 290 | 1.8049e-05 | 1.1614e-06 | 15.5403 | 1 | 310 | Customer | 58793 | Load | Tran1phOH | STEVEN GILES | 405-227-2802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008804 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-01-23 10:23 | 2020-01-23 15:32 | 309.68 | 4 | 2 | 1224.2 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | 11025 S.WESTMINSTER | CMI_PLANNED | YES | NO | NO | 861024 | 159116 | 56972 | 4240 | 1005 | 0.0014218 | 4.6456e-06 | 306.05 | 1 | 308 | Load | 8364 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008805 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-01-23 10:23 | 2020-01-23 15:33 | 309.88 | 1 | 1 | 298.65 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | 9735 S. WESTMINSTER | CMI_PLANNED | YES | NO | NO | 861024 | 159116 | 56972 | 4240 | 1005 | 0.00034685 | 1.1614e-06 | 298.65 | 1 | 308 | Load | 83641 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008806 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-01-23 10:23 | 2020-01-23 15:36 | 313.17 | 1 | 1 | 295.1167 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | 4BNE104 ES DRAP DR | CMI_PLANNED | YES | NO | NO | 861024 | 159116 | 56972 | 4240 | 1005 | 0.00034275 | 1.1614e-06 | 295.1167 | 1 | 308 | Load | 44963 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008811 |  | NORTHWEST | ENID | 4414:HENNESSEY | HENNESSEY_1423 | 441423 | 2020-01-23 10:37 | 2020-01-23 11:59 | 81.77 | 2 | 1 | 162.0667 | 4 | DETERIORATION | 12 | POLE | HENNESSEY | .5 Mile West of N 2910 Rd & E 0630 Rd | CMI_PLANNED | YES | NO | NO | 861024 | 53529 | 37585 | 1954 | 287 | 0.00018823 | 2.3228e-06 | 81.0333 | 1 | 308 | Tap | 5078 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008809 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-23 10:38 | 2020-01-23 11:58 | 80.07 | 4 | 3 | 304.9333 | 4 | DETERIORATION | 12 | POLE | ARKOMA | 113.5 SUMNER | CMI_PLANNED | YES | NO | NO | 861024 | 82214 | 61184 | 2937 | 875 | 0.00035415 | 4.6456e-06 | 76.2333 | 1 | 308 | Load | 11823 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-23 | 2020 |  | Ark - Series 2
J2001.008812 | PD-01232020-00185 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7431 | 847431 | 2020-01-23 10:41 | 2020-01-23 11:08 | 26.73 | 1 | 1 | 26.7333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 138 NE.38 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 168155 | 148336 | 6161 | 373 | 3.1048e-05 | 1.1614e-06 | 26.7333 | 1 | 310 | Customer | 3706 | Load | TranOpenDelta | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2022
J2001.008841 | PD-01232020-00237 | NORTHEAST | MUSKOGEE | 3136:EUCLID | EUCLID_3631 | 313631 | 2020-01-23 11:09 | 2020-01-23 13:40 | 151.02 | 2 | 3 | 296.5667 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | MUSKOGEE | HARRIS RD | CMI_NORMAL | NO | NO | NO | 861024 | 74032 | 33265 | 984 | 352 | 0.00034443 | 2.3228e-06 | 148.2833 | 1 | 310 | Secondary | 12327 | Load | Tran1phOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-01-23 | 2020 |  | #N/A
J2001.008822 |  | NORTHEAST | MUSKOGEE | 3136:EUCLID | EUCLID_3631 | 313631 | 2020-01-23 11:09 | 2020-01-23 11:09 | 0 | 352 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MUSKOGEE | 2513 EUCLID AVE | CMI_MOMENTARY | YES | NO | NO | 861024 | 74032 | 33265 | 984 | 352 | 0 | 0.00040882 | 0 | 1 | 0 | Feeder | EUCLID_3631 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-23 | 2020 |  | #N/A
J2001.008826 |  | METRO EAST | EAST | 8416:DUNJEE | DUNJEE_1621 | 841621 | 2020-01-23 11:11 | 2020-01-23 11:56 | 44.22 | 8 | 6 | 326.4 | 4 | DETERIORATION | 2 | TRANSFORMER OH | CHOCTAW | 207 LARRY | CMI_PLANNED | YES | NO | NO | 861024 | 114360 | 71188 | 3541 | 1552 | 0.00037908 | 9.2913e-06 | 40.8 | 1 | 310 | Load | 14494 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008844 | PD-01232020-00218 | SOUTHERN | HEALDTON | 5319:FOX | FOX 21 | 531921 | 2020-01-23 11:29 | 2020-01-23 11:56 | 27.12 | 1 | 1 | 27.1167 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | HEALDTON | 11730 OIL CITY RD | CMI_NORMAL | NO | NO | NO | 861024 | 77598 | 6796 | 706 | 341 | 3.1494e-05 | 1.1614e-06 | 27.1167 | 1 | 310 | Load | 327052 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008845 |  | METRO SOUTH | SOUTH | 5606:WALNUT CREEK | WALNUT_CREEK_621 | 560621 | 2020-01-23 11:31 | 2020-01-23 13:41 | 129.67 | 1 | 1 | 77.8833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | PURCELL | 1MS 3/4W OF PURCELL | CMI_PLANNED | YES | NO | NO | 861024 | 159116 | 56972 | 1106 | 1106 | 9.0454e-05 | 1.1614e-06 | 77.8833 | 1 | 308 | Load | 28954 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008848 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-01-23 11:34 | 2020-01-23 12:20 | 45.95 | 3 | 2 | 128.6 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | S OF 149 ON ANDERSON | CMI_PLANNED | YES | NO | NO | 861024 | 159116 | 56972 | 4240 | 1005 | 0.00014936 | 3.4842e-06 | 42.8667 | 1 | 308 | Mainline | 9711 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008860 | PD-01232020-00258 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_621 | 870621 | 2020-01-23 12:05 | 2020-01-23 12:52 | 47.42 | 1 | 1 | 22.7463 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 300 HAL-MULDROW DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 159116 | 56972 | 7367 | 925 | 2.6418e-05 | 1.1614e-06 | 22.7463 | 1 | 310 | Customer | 33688 | Load | Tran1phPad | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008871 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5921 | 835921 | 2020-01-23 12:41 | 2020-01-23 12:48 | 7.62 | 1 | 1 | 7.6167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | YUKON | 55 RANCHWOOD BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 128791 | 116036 | 6429 | 1818 | 8.8461e-06 | 1.1614e-06 | 7.6167 | 1 | 310 | Customer | 47689 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | #N/A
J2001.008873 | PD-01232020-00272 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4031 | 834031 | 2020-01-23 12:44 | 2020-01-23 14:30 | 106.23 | 1 | 1 | 94.1833 | 15 | SQUIRREL | 27 | CUTOUT | OKLAHOMA CITY | 35 N.HARBOR DR | CMI_NORMAL | NO | NO | NO | 861024 | 128791 | 116036 | 10841 | 1641 | 0.00010939 | 1.1614e-06 | 94.1833 | 1 | 310 | Customer | 9521 | Load | Tran1phOH | DENNY J MORGAN | 405-501-1556 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008874 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-01-23 12:44 | 2020-01-23 12:46 | 2.05 | 1 | 1 | 2.05 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7566 NW.10 | CMI_MOMENTARY | YES | NO | NO | 861024 | 128791 | 116036 | 3407 | 2037 | 2.3809e-06 | 1.1614e-06 | 2.05 | 1 | 310 | Customer | 42160 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008875 |  | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_621 | 550621 | 2020-01-23 12:47 | 2020-01-23 14:03 | 75.82 | 13 | 4 | 936 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | DURANT | TOWN + CO MBL PK | CMI_PLANNED | YES | NO | NO | 861024 | 77598 | 15486 | 6736 | 901 | 0.0010871 | 1.5098e-05 | 72 | 1 | 308 | Load | 15635 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008879 | PD-01232020-00280 | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1221 | 911221 | 2020-01-23 12:53 | 2020-01-23 14:50 | 117.13 | 1 | 2 | 117.1333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | FORT SMITH | 709 S.21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 82214 | 61184 | 6598 | 1742 | 0.00013604 | 1.1614e-06 | 117.1333 | 1 | 310 | Customer | 1229 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | Ark - Series 1
J2001.008883 |  | METRO EAST | EAST | 8542:RENO | RENO_4222 | 854222 | 2020-01-23 13:04 | 2020-01-23 13:04 | 0 | 1689 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 300 S SUNNYLAND RD | CMI_MOMENTARY | YES | NO | NO | 861024 | 114360 | 71188 | 5215 | 1689 | 0 | 0.0019616 | 0 | 1 | 0 | Feeder | RENO_4222 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008886 | PD-01232020-00319 | METRO EAST | EAST | 8542:RENO | RENO_4222 | 854222 | 2020-01-23 13:06 | 2020-01-23 15:35 | 148.67 | 1 | 1 | 148.6667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MIDWEST CITY | 400 CHAR LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 114360 | 71188 | 5215 | 1689 | 0.00017266 | 1.1614e-06 | 148.6667 | 1 | 310 | Customer | 12573 | Load | Tran1phOH | KYLE L GOODIN | 405-426-9802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008889 | PD-01232020-00312 | METRO EAST | EAST | 8542:RENO | RENO_4222 | 854222 | 2020-01-23 13:12 | 2020-01-23 15:26 | 133.85 | 5 | 3 | 662.2917 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MIDWEST CITY | 108 S.BELL DR | CMI_NORMAL | NO | NO | NO | 861024 | 114360 | 71188 | 5215 | 1689 | 0.00076919 | 5.807e-06 | 132.4583 | 1 | 310 | Load | 5956 | Load | Tran1phOH | KYLE L GOODIN | 405-426-9802 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008891 | PD-01232020-00299 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5021 | 865021 | 2020-01-23 13:15 | 2020-01-23 15:04 | 109.47 | 10 | 9 | 1087.3333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MIDWEST CITY | 2421 N.KEY BL | CMI_NORMAL | NO | NO | NO | 861024 | 114360 | 71188 | 8628 | 1291 | 0.0012628 | 1.1614e-05 | 108.7333 | 1 | 310 | Load | 10920 | Load | Tran1phOH | KYLE L GOODIN | 405-426-9802 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008898 | PD-01232020-00303 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2224 | 852224 | 2020-01-23 13:16 | 2020-01-23 16:23 | 186.58 | 1 | 2 | 174.55 | 3 | DAMAGED BY PUBLIC | 30 | CONDUCTOR SERVICE - UG | CHOCTAW | 810 BUCKWOOD DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 114360 | 71188 | 11630 | 1523 | 0.00020272 | 1.1614e-06 | 174.55 | 1 | 310 | Customer | 66165 | Load | Tran1phPad | BAD ORDER UG RES COORD | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008894 | PD-01232020-00292 | METRO WEST | WEST | 8359:YUKON | YUKON_5921 | 835921 | 2020-01-23 13:22 | 2020-01-23 14:02 | 39.5 | 1 | 1 | 10.0788 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | YUKON | 55 RANCHWOOD BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 128791 | 116036 | 6429 | 1818 | 1.1706e-05 | 1.1614e-06 | 10.0788 | 1 | 310 | Customer | 47689 | Load | Tran1phPad | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | #N/A
J2001.008895 | PD-01232020-00298 | METRO EAST | SHAWNEE | 7435:MISSION HILL | MISSION HILL 24 | 743524 | 2020-01-23 13:28 | 2020-01-23 14:36 | 68.23 | 1 | 1 | 68.2333 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | SHAWNEE | 2025 S GORDON COOPER DR | CMI_NORMAL | NO | NO | NO | 861024 | 114360 | 22105 | 948 | 948 | 7.9247e-05 | 1.1614e-06 | 68.2333 | 1 | 320 | Customer | 367478 | Load | Tran3phWye | BRYAN K TATUM | 405-659-0746 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | OK - 2021
J2001.008909 | PD-01232020-00421 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_524 | 510524 | 2020-01-23 13:29 | 2020-01-23 16:53 | 203.75 | 1 | 2 | 195.25 | 27 | TREE:NON PREVENTABLE | 31 | CONDUCTOR SERVICE - OH | ARDMORE | 317 LAKE MURRAY DR E | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861024 | 77598 | 23585 | 4774 | 1432 | 0.00022676 | 1.1614e-06 | 195.25 | 1 | 310 | Customer | 8390 | Load | Tran1phOH | ANDREW CHAVERS | 580-504-0524 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | OK - 2021
J2001.008902 |  | ARKANSAS | FORT SMITH | 9340:TWIN BRIDGES | TWIN_BRIDGES_4021 | 934021 | 2020-01-23 13:31 | 2020-01-23 13:48 | 16.92 | 1 | 1 | 16.9167 | 1 | CANCELLED | 57 | CANCELLED | VAN BUREN | 3102 OAK LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 82214 | 61184 | 1039 | 1039 | 1.9647e-05 | 1.1614e-06 | 16.9167 | 1 | 310 | Customer | 6421 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-23 | 2020 |  | Ark - Series 1
J2001.008908 | PD-01232020-00315 | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5629 | 865629 | 2020-01-23 13:42 | 2020-01-23 19:12 | 329.7 | 1 | 1 | 318.6333 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | SHELTER III MHP | CMI_NORMAL | NO | NO | NO | 861024 | 159116 | 102144 | 2752 | 732 | 0.00037006 | 1.1614e-06 | 318.6333 | 1 | 320 | Customer | 74539 | Load | Tran1phOH | COLBY T LLOYD | 405-312-0110 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008907 | PD-01232020-00314 | METRO WEST | WEST | 8222:CZECH HALL | CZECH_HALL_2223 | 822223 | 2020-01-23 13:43 | 2020-01-23 17:05 | 201.82 | 1 | 2 | 133.8 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | YUKON | 107 CHESTNUT DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861024 | 128791 | 116036 | 8605 | 1177 | 0.0001554 | 1.1614e-06 | 133.8 | 1 | 320 | Customer | 42937 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008914 |  | METRO SOUTH | SOUTH CENTRAL | 8194:WESTMOORE | WESTMOORE_9429 | 819429 | 2020-01-23 14:01 | 2020-01-23 14:01 | 0 | 1133 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 12406 S PENNSYLVANIA AVE | CMI_MOMENTARY | YES | NO | NO | 861024 | 159116 | 102144 | 8101 | 1133 | 0 | 0.0013159 | 0 | 1 | 0 | Feeder | WESTMORE_9429 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008920 | PD-01232020-00347 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6124 | 836124 | 2020-01-23 14:01 | 2020-01-23 15:19 | 78.1 | 1 | 2 | 63.9333 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 811 NW.22 | CMI_NORMAL | NO | NO | NO | 861024 | 168155 | 148336 | 11100 | 1764 | 7.4253e-05 | 1.1614e-06 | 63.9333 | 1 | 310 | Customer | 23298 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2020
J2001.008918 | PD-01232020-00338 | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_521 | 560521 | 2020-01-23 14:03 | 2020-01-23 14:40 | 36.85 | 6 | 6 | 207.8 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | PAULS VALLEY | 1118 EVERGREEN DR | CMI_NORMAL | NO | NO | NO | 861024 | 77598 | 6207 | 2458 | 468 | 0.00024134 | 6.9684e-06 | 34.6333 | 1 | 310 | Secondary | 5482 | Load | Tran1phOH | BRUCE E BEAM | 405-626-0490 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | OK - 2022
J2001.008915 |  | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_521 | 560521 | 2020-01-23 14:03 | 2020-01-23 14:03 | 0.02 | 468 | 0 | 7.8 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | PAULS VALLEY | 121 E BRADLEY | CMI_MOMENTARY | YES | NO | NO | 861024 | 77598 | 6207 | 2458 | 468 | 9.059e-06 | 0.00054354 | 0.016667 | 1 | 0 | Feeder | PAULS_VALLEY_521 | Recloser | 0 | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-23 | 2020 |  | OK - 2022
J2001.008921 | PD-01232020-00376 | METRO WEST | EL RENO | 8908:ROMAN NOSE | ROMAN_NOSE_847 | 890847 | 2020-01-23 14:14 | 2020-01-23 16:09 | 114.78 | 1 | 1 | 27.3264 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | WATONGA | WATONGA>1MN-33 ON LAND WSR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 128791 | 12755 | 525 | 214 | 3.1737e-05 | 1.1614e-06 | 27.3264 | 1 | 310 | Load | 34073 | Load | Tran1phOH | MICHAEL T MAHEN | 405-210-6029 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2020
J2001.008925 | PD-01232020-00377 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2122 | 822122 | 2020-01-23 14:37 | 2020-01-23 15:05 | 27.72 | 1 | 1 | 27.7167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 3949 NW.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 168155 | 148336 | 9250 | 1838 | 3.219e-05 | 1.1614e-06 | 27.7167 | 1 | 310 | Customer | 16933 | Load | Tran1phOH | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2020
J2001.008927 | PD-01232020-00443 | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_624 | 460624 | 2020-01-23 14:44 | 2020-01-23 16:40 | 115.8 | 1 | 1 | 115.8 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | WOODWARD | 2503 1ST-WOODWARD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 53529 | 10424 | 5683 | 488 | 0.00013449 | 1.1614e-06 | 115.8 | 1 | 310 | Customer | 11382 | Load | Tran1phPad | MICHAEL W CAREY | 580-216-1158 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | #N/A
J2001.008934 | PD-01232020-00419 | NORTHWEST | ENID | 4219:BUNCH CREEK | BUNCH CREEK 41 | 421941 | 2020-01-23 14:47 | 2020-01-23 18:13 | 205.8 | 27 | 5 | 5450.4 | 22 | WIND | 37 | CONDUCTOR PRIMARY - OH | BILLINGS | PEARL + WEAVER-SOUTH | CMI_NORMAL | NO | NO | NO | 861024 | 53529 | 37585 | 910 | 910 | 0.0063301 | 3.1358e-05 | 201.8667 | 1 | 310 | Mainline | 2976 | Fuse | FuseOH | BRIAN L KAISER | 580-402.4510 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008930 | PD-01232020-00410 | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5822 | 845822 | 2020-01-23 14:49 | 2020-01-23 15:45 | 56.02 | 1 | 1 | 54.6833 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | .5ME AIRDEPOT NS66 | CMI_NORMAL | NO | NO | NO | 861024 | 114360 | 71188 | 2986 | 934 | 6.351e-05 | 1.1614e-06 | 54.6833 | 1 | 310 | Load | 2633 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Other | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | #N/A
J2001.008931 |  | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_622 | 880622 | 2020-01-23 14:51 | 2020-01-23 14:51 | 0 | 1166 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | GUTHRIE | 800 W INDUSTRIAL RD | CMI_MOMENTARY | YES | NO | NO | 861024 | 168155 | 19819 | 5165 | 1165 | 0 | 0.0013542 | 0 | 1 | 0 | Feeder | COTWD CK_622 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008936 | PD-01232020-00434 | SOUTHERN | HEALDTON | 5311:RATLIFF | RATLIFF_1121 | 531121 | 2020-01-23 15:04 | 2020-01-23 17:22 | 137.75 | 1 | 1 | 137.75 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | RATLIFF CITY | 7/76 2N 1E | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 77598 | 6796 | 449 | 123 | 0.00015998 | 1.1614e-06 | 137.75 | 1 | 310 | Customer | 28889 | Load | TranOpenDelta | RANDAL G CALLAWAY | 580-220-8449 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008939 | PD-01232020-00436 | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_524 | 560524 | 2020-01-23 15:26 | 2020-01-23 16:28 | 62.32 | 1 | 1 | 62.3167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | PAULS VALLEY | 413 S.PECAN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 77598 | 6207 | 2458 | 602 | 7.2375e-05 | 1.1614e-06 | 62.3167 | 1 | 310 | Customer | 7520 | Load | Tran1phOH | BRUCE E BEAM | 405-626-0490 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | OK - 2022
J2001.008942 |  | ARKANSAS | POTEAU | 3505:POTEAU | POTEAU_522 | 350522 | 2020-01-23 15:36 | 2020-01-23 15:42 | 5.93 | 1 | 1 | 5.9333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | CAMERON | 200 N. OF CHURCH ST.ON W. 2ND | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 82214 | 13485 | 2298 | 358 | 6.891e-06 | 1.1614e-06 | 5.9333 | 1 | 310 | Customer | 979 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | #N/A
J2001.008944 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2122 | 822122 | 2020-01-23 15:39 | 2020-01-23 15:46 | 7 | 1 | 1 | 7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3949 NW.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 168155 | 148336 | 9250 | 1838 | 8.1299e-06 | 1.1614e-06 | 7 | 1 | 320 | Customer | 16933 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2020
J2001.008945 |  | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_921 | 910921 | 2020-01-23 15:47 | 2020-01-23 15:53 | 6.2 | 1 | 1 | 6.2 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 2700 MAY-BRANCH DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 82214 | 61184 | 5010 | 1427 | 7.2007e-06 | 1.1614e-06 | 6.2 | 1 | 310 | Customer | 734 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | Ark - Series 3
J2001.008952 | PD-01232020-00482 | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_524 | 560524 | 2020-01-23 16:13 | 2020-01-23 16:44 | 31 | 1 | 1 | 31 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | PAULS VALLEY | 118 BURR AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 77598 | 6207 | 2458 | 602 | 3.6004e-05 | 1.1614e-06 | 31 | 1 | 320 | Customer | 8865 | Load | Tran3phWye | ANDREW CHAVERS | 580-504-0524 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | OK - 2022
J2001.008953 | PD-01232020-00489 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_631 | 870631 | 2020-01-23 16:20 | 2020-01-23 17:33 | 73.13 | 1 | 1 | 73.1333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 1207 CROWN-POINT AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 159116 | 56972 | 7367 | 1262 | 8.4938e-05 | 1.1614e-06 | 73.1333 | 1 | 310 | Customer | 33694 | Load | Tran1phPad | THOMAS E COLE | 405-623-9338 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008956 |  | NORTHWEST | ENID | 4219:BUNCH CREEK | BUNCH CREEK 41 | 421941 | 2020-01-23 16:22 | 2020-01-23 18:29 | 127.05 | 1 | 1 | 106.2667 | 22 | WIND | 37 | CONDUCTOR PRIMARY - OH | BILLINGS | HW 15, .5BE-YOUNG--BILLINGS | CMI_NORMAL | NO | NO | NO | 861024 | 53529 | 37585 | 910 | 910 | 0.00012342 | 1.1614e-06 | 106.2667 | 1 | 310 | Customer | 6573 | Load | Tran1phOH | [7 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008955 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5921 | 835921 | 2020-01-23 16:23 | 2020-01-23 16:40 | 16.2 | 1 | 1 | 16.2 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | YUKON | 55 RANCHWOOD BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 128791 | 116036 | 6429 | 1818 | 1.8815e-05 | 1.1614e-06 | 16.2 | 1 | 310 | Customer | 47689 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | #N/A
J2001.008965 |  | ARKANSAS | OZARK | 9406:HELBERG | HELBERG_621 | 940621 | 2020-01-23 16:38 | 2020-01-23 16:52 | 13.92 | 1 | 1 | 13.9167 | 1 | CANCELLED | 57 | CANCELLED | OZARK | 307 OAK ST + WARNER ST, OZARK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 82214 | 7545 | 1720 | 834 | 1.6163e-05 | 1.1614e-06 | 13.9167 | 1 | 310 | Customer | 4977 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | Ark - Series 3
J2001.008966 | PD-01232020-00499 | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_646 | 730646 | 2020-01-23 16:38 | 2020-01-23 17:52 | 74.17 | 1 | 1 | 74.1667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | EARLSBORO | 224 N LAYTON AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 114360 | 13605 | 4063 | 282 | 8.6138e-05 | 1.1614e-06 | 74.1667 | 1 | 310 | Customer | 1370 | Load | Tran1phOH | KEVIN M RICH | 405-802-2121 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2021
J2001.008969 |  | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8123 | 838123 | 2020-01-23 16:40 | 2020-01-23 16:47 | 6.97 | 1 | 1 | 6.9667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 8301 N. COUNCIL # 111 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 128791 | 116036 | 8955 | 1216 | 8.0911e-06 | 1.1614e-06 | 6.9667 | 1 | 310 | Customer | 73554 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008967 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3823 | 913823 | 2020-01-23 16:40 | 2020-01-23 20:20 | 219.52 | 2 | 1 | 347.5333 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | S. 4 N. S. K ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 82214 | 61184 | 2937 | 75 | 0.00040363 | 2.3228e-06 | 173.7667 | 1 | 308 | Mainline | 1609 | Fuse | FuseRiser | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-23 | 2020 |  | Ark - Series 2
J2001.008970 |  | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-01-23 16:49 | 2020-01-23 16:49 | 0 | 1090 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ADA | 1806 A ST | CMI_MOMENTARY | YES | NO | NO | 861024 | 77598 | 11513 | 2518 | 1090 | 0 | 0.0012659 | 0 | 1 | 0 | Feeder | VALLEY_VIEW_623 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-23 | 2020 |  | #N/A
J2001.008972 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2122 | 822122 | 2020-01-23 16:59 | 2020-01-23 17:08 | 9.7 | 1 | 1 | 9.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3949 NW.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 168155 | 148336 | 9250 | 1838 | 1.1266e-05 | 1.1614e-06 | 9.7 | 1 | 320 | Customer | 16933 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2020
J2001.008973 | PD-01232020-00506 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4823 | 824823 | 2020-01-23 17:04 | 2020-01-23 19:00 | 116.43 | 1 | 1 | 116.4333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3230 SW.19 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 168155 | 148336 | 4192 | 1796 | 0.00013523 | 1.1614e-06 | 116.4333 | 1 | 310 | Customer | 5789 | Load | Tran1phOH | THOMAS E COLE | 405-623-9338 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2021
J2001.008981 | PD-01232020-00511 | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-01-23 17:28 | 2020-01-23 17:53 | 25.15 | 2 | 2 | 34.9833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ADA | 1427 NORTHCREST DR | CMI_NORMAL | NO | NO | NO | 861024 | 77598 | 11513 | 2518 | 1090 | 4.063e-05 | 2.3228e-06 | 17.4917 | 1 | 310 | Secondary | 19 | Load | Tran1phOH | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | #N/A
J2001.008987 |  | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1522 | 811522 | 2020-01-23 17:40 | 2020-01-23 17:51 | 11.05 | 1 | 1 | 11.05 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2321 SW.32 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 159116 | 102144 | 6061 | 1941 | 1.2834e-05 | 1.1614e-06 | 11.05 | 1 | 310 | Customer | 25468 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | OK - 2022
J2001.008990 | PD-01232020-00512 | SOUTHERN | ARDMORE | 5108:WOLF CREEK | WOLF CREEK 22 | 510822 | 2020-01-23 17:42 | 2020-01-23 18:15 | 33.3 | 2 | 4 | 66.8333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | LONE GROVE | HWY 70 AND THOUSAND OAKS DR .4N .2W | CMI_NORMAL | NO | NO | NO | 861024 | 77598 | 23585 | 448 | 236 | 7.7621e-05 | 2.3228e-06 | 33.4167 | 1 | 310 | Load | 378523 | Load | Tran1phOH | RANDAL G CALLAWAY | 580-220-8449 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008991 | PD-01232020-00513 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6023 | 836023 | 2020-01-23 17:55 | 2020-01-23 19:12 | 77.03 | 1 | 1 | 77.0333 | 4 | DETERIORATION | 50 | CONNECTOR | BETHANY | 4311 N BEAVER ST | CMI_NORMAL | NO | NO | NO | 861024 | 128791 | 116036 | 5506 | 1480 | 8.9467e-05 | 1.1614e-06 | 77.0333 | 1 | 320 | Customer | 18837 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | OK - 2022
J2001.008999 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2126 | 822126 | 2020-01-23 17:59 | 2020-01-23 22:13 | 254.05 | 4 | 3 | 492.6 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | RENO + PORTLAND | CMI_PLANNED | YES | NO | NO | 861024 | 168155 | 148336 | 9250 | 676 | 0.00057211 | 4.6456e-06 | 123.15 | 1 | 308 | Load | 78825 | Load | Tran3phWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.008994 | PD-01232020-00514 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-01-23 18:04 | 2020-01-23 19:26 | 81.57 | 1 | 1 | 81.5667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DEL CITY | 4412 SE.21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 159119 | 102148 | 7416 | 2238 | 9.4732e-05 | 1.1614e-06 | 81.5667 | 1 | 310 | Customer | 6113 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2022
J2001.008996 |  | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_621 | 410621 | 2020-01-23 18:10 | 2020-01-23 18:27 | 16.63 | 1 | 1 | 16.6333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ENID | 414 E MAINE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 53534 | 37591 | 6015 | 1104 | 1.9318e-05 | 1.1614e-06 | 16.6333 | 1 | 310 | Customer | 384 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | #N/A
J2001.009000 | PD-01232020-00515 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2022 | 822022 | 2020-01-23 18:19 | 2020-01-23 23:47 | 328.23 | 1 | 2 | 323.1333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 501 N MILLER | CMI_NORMAL | NO | NO | NO | 861024 | 168193 | 148371 | 6037 | 2120 | 0.00037529 | 1.1614e-06 | 323.1333 | 1 | 310 | Load | 78414 | Load | Tran3phWye | COLBY T LLOYD | 405-312-0110 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | OK - 2020
J2001.009005 | PD-01232020-00517 | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2222 | 882222 | 2020-01-23 18:54 | 2020-01-24 00:32 | 337.97 | 2 | 2 | 662.7333 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | EDMOND | 7008 NIBLICK WAY | CMI_NORMAL | NO | NO | NO | 861024 | 168193 | 19822 | 5387 | 1160 | 0.0007697 | 2.3228e-06 | 331.3667 | 1 | 310 | Secondary | 66370 | Load | Tran1phPad | SHAWN HILL | 405-308-1695 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | #N/A
J2001.009013 | PD-01232020-00518 | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 22 | 570822 | 2020-01-23 20:08 | 2020-01-23 21:32 | 83.92 | 1 | 1 | 78.4333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DAVIS | 608 S. 2ND | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 77606 | 6813 | 1859 | 955 | 9.1093e-05 | 1.1614e-06 | 78.4333 | 1 | 310 | Customer | 4494 | Load | Tran1phOH | BRUCE E BEAM | 405-626-0490 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | OK - 2021
J2001.009017 | PD-01232020-00520 | NORTHEAST | SAPULPA | 3218:BEGGS | BEGGS_1824 | 321824 | 2020-01-23 20:12 | 2020-01-23 21:44 | 91.82 | 1 | 1 | 91.8167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | BEGGS | 1-1/4E, .5MS, 1/4E OF BEGGS NS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 74037 | 40769 | 1837 | 938 | 0.00010664 | 1.1614e-06 | 91.8167 | 1 | 310 | Load | 48217 | Load | Tran1phOH | JOSHUA N MCKINNEY | 918-863-6313 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2020
J2001.009018 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3831 | 913831 | 2020-01-23 20:21 | 2020-01-23 21:56 | 95.12 | 2 | 2 | 149.6333 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 901 FRESNO ST.- FORT SMITH ARK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 82216 | 61184 | 2936 | 486 | 0.00017379 | 2.3228e-06 | 74.8167 | 1 | 308 | Load | 15324 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-23 | 2020 |  | Ark - Series 2
J2001.009026 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-01-23 21:50 | 2020-01-23 21:57 | 7.1 | 1 | 1 | 7.1 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 317 NW.24 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861024 | 168193 | 148371 | 11121 | 2336 | 8.246e-06 | 1.1614e-06 | 7.1 | 1 | 310 | Customer | 1390 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-23 | 2020 |  | OK - 2020
J2001.009028 | PD-01232020-00536 | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3721 | 913721 | 2020-01-23 21:54 | 2020-01-24 01:56 | 241.7 | 10 | 11 | 2286.6667 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | FORT SMITH | S.46 ST- N OF S. U ST | CMI_NORMAL | NO | NO | NO | 861024 | 82216 | 61184 | 4569 | 1498 | 0.0026558 | 1.1614e-05 | 228.6667 | 1 | 310 | Mainline | 2592 | Fuse | FuseRiser | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-23 | 2020 |  | Ark - Series 3
J2001.009027 |  | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3721 | 913721 | 2020-01-23 21:54 | 2020-01-23 21:54 | 0 | 1498 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | FT SMITH | 418 N 51ST ST | CMI_MOMENTARY | YES | NO | NO | 861024 | 82216 | 61184 | 4569 | 1498 | 0 | 0.0017398 | 0 | 1 | 0 | Feeder | PARKVIEW_3721 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-23 | 2020 |  | Ark - Series 3
J2001.009036 |  | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3723 | 913723 | 2020-01-23 23:15 | 2020-01-23 23:15 | 0 | 734 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | FT SMITH | 418 N 51ST ST | CMI_MOMENTARY | YES | NO | NO | 861024 | 82216 | 61184 | 4569 | 734 | 0 | 0.00085247 | 0 | 1 | 0 | Feeder | PARKVIEW_3723 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-23 | 2020 |  | Ark - Series 3
J2001.009044 | PD-01242020-00013 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2029 | 862029 | 2020-01-24 01:25 | 2020-01-24 02:55 | 90.08 | 2 | 3 | 166.6167 | 22 | WIND | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 409 SE 27TH ST | CMI_NORMAL | NO | NO | NO | 861024 | 159119 | 102148 | 4748 | 983 | 0.00019351 | 2.3228e-06 | 83.3083 | 1 | 310 | Load | 7389 | Load | Tran1phOH | DARREN L STOCKTON | 918-777-1697 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009058 | PD-01242020-00018 | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1721 | 861721 | 2020-01-24 05:00 | 2020-01-24 16:17 | 677.02 | 73 | 63 | 48046.1667 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | E/O.SHALIMAR SS.OAKCLI | CMI_NORMAL | NO | NO | NO | 861073 | 114369 | 71190 | 6950 | 1505 | 0.055798 | 8.4778e-05 | 658.1667 | 1 | 310 | Mainline | 4779 | Fuse | FuseRiser | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | #N/A
J2001.009076 | PD-01242020-00024 | METRO EAST | CHANDLER | 7119:WARWICK | WARWICK_1941 | 711941 | 2020-01-24 06:40 | 2020-01-24 10:29 | 228.65 | 1 | 1 | 154.3333 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | WELLSTON | 1/4MS OF 66, ES PINECREST | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861073 | 114369 | 7463 | 2418 | 1462 | 0.00017923 | 1.1613e-06 | 154.3333 | 1 | 310 | Load | 23984 | Load | Tran1phOH | KELLEY D WATSON | 405-763-8148 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | OK - 2021
J2001.009070 | PD-01242020-00022 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3670 | 853670 | 2020-01-24 06:48 | 2020-01-24 06:48 | 0.02 | 1 | 1 | 0.016667 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | 755 RESEARCH PARKWAY | CMI_MOMENTARY | YES | NO | NO | 861073 | 168193 | 148371 | 5926 | 1565 | 1.9356e-08 | 1.1613e-06 | 0.016667 | 1 | 310 | Customer | 145927 | Load | Tran3phPadWye | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | OK - 2022
J2001.009084 |  | METRO NORTH | NORTH | 8535:OU MED CENTER | OU_MEDICAL_CEN_3572 | 853572 | 2020-01-24 06:48 | 2020-01-24 14:22 | 454.02 | 4 | 0 | 1648.0667 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | NE 8th & Geary Ave. Approx 400''W of Geary on SS of NE8th | CMI_NORMAL | NO | NO | NO | 861073 | 168193 | 148371 | 524 | 498 | 0.001914 | 4.6454e-06 | 412.0167 | 1 | 0 | Mainline | 245443 | Fuse | 0 | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009074 | PD-01242020-00023 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9921 | 829921 | 2020-01-24 06:56 | 2020-01-24 09:54 | 178.45 | 21 | 15 | 2804.55 | 13 | PREMATURE FAILURE | 36 | CONDUCTOR PRIMARY - UG | BETHANY | 16TH + ROCKWELL 900 E | CMI_NORMAL | NO | NO | NO | 861073 | 128800 | 116045 | 9232 | 1636 | 0.003257 | 2.4388e-05 | 133.55 | 1 | 310 | Mainline | 27822 | Fuse | FuseRiser | DERICK WINSETT | 405-650-6102 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009072 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9921 | 829921 | 2020-01-24 06:56 | 2020-01-24 06:56 | 0.03 | 1636 | 0 | 54.5333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 1101 N CHISHOLM RD | CMI_MOMENTARY | YES | NO | NO | 861073 | 128800 | 116045 | 9232 | 1636 | 6.3332e-05 | 0.0019 | 0.033333 | 1 | 0 | Feeder | WESTOAKS_9921 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009080 | PD-01242020-00020 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2224 | 852224 | 2020-01-24 07:08 | 2020-01-24 10:49 | 221 | 2 | 3 | 405.3667 | 13 | PREMATURE FAILURE | 2 | TRANSFORMER OH | CHOCTAW | 14201 E.RENO | CMI_NORMAL | NO | NO | NO | 861073 | 114369 | 71190 | 11630 | 1523 | 0.00047077 | 2.3227e-06 | 202.6833 | 1 | 310 | Load | 29429 | Load | Tran1phOH | GARY D FRANKLIN | 405-637-2002 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009077 |  | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_624 | 550624 | 2020-01-24 07:14 | 2020-01-24 08:06 | 52.47 | 3 | 3 | 128.3 | 4 | DETERIORATION | 2 | TRANSFORMER OH | DURANT | 1005 W.MAIN | CMI_PLANNED | YES | NO | NO | 861073 | 77606 | 15489 | 6737 | 1155 | 0.000149 | 3.484e-06 | 42.7667 | 1 | 308 | Load | 16700 | Load | Tran3phWye | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009085 | PD-01242020-00050 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6961 | 846961 | 2020-01-24 08:04 | 2020-01-24 09:50 | 105.67 | 1 | 1 | 105.6667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 417 NW 145TH TERR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 168193 | 148371 | 7722 | 1387 | 0.00012272 | 1.1613e-06 | 105.6667 | 1 | 310 | Customer | 85940 | Load | Tran1phPad | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009087 | PD-01242020-00052 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3729 | 833729 | 2020-01-24 08:07 | 2020-01-24 09:20 | 72.85 | 9 | 9 | 573.3 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1011 NW.89 | CMI_NORMAL | NO | NO | NO | 861073 | 168193 | 148371 | 5766 | 1400 | 0.0006658 | 1.0452e-05 | 63.7 | 1 | 310 | Load | 4595 | Load | TranOHDeltaSplitBank | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | OK - 2021
J2001.009089 | PD-01242020-00062 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-01-24 08:19 | 2020-01-24 09:52 | 92.65 | 1 | 1 | 62.7293 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 915 NW.30 | CMI_NORMAL | NO | NO | NO | 861073 | 168193 | 148371 | 11121 | 2336 | 7.285e-05 | 1.1613e-06 | 62.7293 | 1 | 320 | Customer | 12414 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | OK - 2020
J2001.009091 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3823 | 913823 | 2020-01-24 08:26 | 2020-01-24 11:46 | 200.03 | 1 | 0 | 192.3667 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | FORT SMITH | S.E + S. 3 ST . | CMI_PLANNED | YES | NO | NO | 861073 | 82216 | 61184 | 2936 | 75 | 0.0002234 | 1.1613e-06 | 192.3667 | 1 | 0 | Mainline | 1663 | Fuse | FuseRiser | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-24 | 2020 |  | Ark - Series 2
J2001.009093 | PD-01242020-00070 | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1823 | 931823 | 2020-01-24 08:27 | 2020-01-24 10:32 | 125.1 | 1 | 1 | 125.1 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ALMA | 1218 ALMA NORTH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 82216 | 61184 | 2836 | 1228 | 0.00014528 | 1.1613e-06 | 125.1 | 1 | 320 | Customer | 90 | Load | Tran1phOH | KRIS L HALMES | 479-430-9447 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | Ark - Series 2
J2001.009094 | PD-01242020-00067 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2022 | 822022 | 2020-01-24 08:28 | 2020-01-24 10:38 | 130.25 | 1 | 1 | 118.2602 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 501 N MILLER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 168193 | 148371 | 6037 | 2120 | 0.00013734 | 1.1613e-06 | 118.2602 | 1 | 320 | Load | 78414 | Load | Tran3phWye | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | OK - 2020
J2001.009097 | PD-01242020-00081 | SOUTHERN | HEALDTON | 5311:RATLIFF | RATLIFF_1121 | 531121 | 2020-01-24 08:37 | 2020-01-24 10:00 | 82.72 | 1 | 1 | 157.25 | 4 | DETERIORATION | 27 | CUTOUT | TATUMS | 2E RAT COR | CMI_NORMAL | NO | NO | NO | 861073 | 77606 | 6797 | 449 | 123 | 0.00018262 | 1.1613e-06 | 157.25 | 1 | 310 | Load | 28856 | Load | TranOH3phDelta | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009098 |  | SOUTHERN | DURANT | 5504:BUTTERFIELD | BUTTERFIELD_422 | 550422 | 2020-01-24 08:39 | 2020-01-24 09:48 | 69.28 | 1 | 1 | 62.9833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | DURANT | W END N3270 RD | CMI_PLANNED | YES | NO | NO | 861073 | 77606 | 15489 | 3485 | 561 | 7.3145e-05 | 1.1613e-06 | 62.9833 | 1 | 308 | Load | 13844 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009101 |  | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_629 | 870629 | 2020-01-24 08:56 | 2020-01-24 11:00 | 123.5 | 2 | 2 | 224.0167 | 4 | DETERIORATION | 2 | TRANSFORMER OH | NORMAN | 1433 W.BOYD | CMI_PLANNED | YES | NO | NO | 861073 | 159119 | 56971 | 7367 | 1373 | 0.00026016 | 2.3227e-06 | 112.0083 | 1 | 308 | Load | 46441 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009105 | PD-01242020-00122 | METRO EAST | CHANDLER | 7119:WARWICK | WARWICK_1942 | 711942 | 2020-01-24 09:03 | 2020-01-24 10:13 | 70.35 | 1 | 1 | 68.55 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | AGRA | AGRA OK NORTH OF GRANT ON 8TH | CMI_NORMAL | NO | NO | NO | 861073 | 114369 | 7463 | 2418 | 956 | 7.961e-05 | 1.1613e-06 | 68.55 | 1 | 310 | Customer | 4658 | Load | Tran1phOH | BRAD WRIGHT | 918-629-1747 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | OK - 2022
J2001.009106 | PD-01242020-00121 | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_621 | 410621 | 2020-01-24 09:03 | 2020-01-24 09:34 | 30.82 | 1 | 1 | 30.8167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ENID | 1419 E OKLAHOMA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 53534 | 37591 | 6015 | 1104 | 3.5789e-05 | 1.1613e-06 | 30.8167 | 1 | 320 | Customer | 2450 | Load | Tran1phOH | KEVIN N PERRYMAN | 601-528-2473 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | #N/A
J2001.009108 | PD-01242020-00124 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5021 | 865021 | 2020-01-24 09:07 | 2020-01-24 09:55 | 48.02 | 1 | 1 | 48.0167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 2522 GLENHAVEN DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 114369 | 71190 | 8629 | 1291 | 5.5764e-05 | 1.1613e-06 | 48.0167 | 1 | 310 | Customer | 32919 | Load | Tran1phPad | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009112 | PD-01242020-00159 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_723 | 870723 | 2020-01-24 09:09 | 2020-01-24 10:41 | 91.88 | 7 | 10 | 572.0167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | NORMAN | 1710 OAKCLIFF RD | CMI_NORMAL | NO | NO | NO | 861073 | 159119 | 56971 | 11832 | 2044 | 0.00066431 | 8.1294e-06 | 81.7167 | 1 | 310 | Load | 48526 | Load | Tran1phOH | MARK A PALMORE | 405-512-1933 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009113 |  | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_621 | 870621 | 2020-01-24 09:16 | 2020-01-24 09:50 | 33.92 | 1 | 1 | 24.3333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | NORMAN | 104 FOREMAN AV | CMI_PLANNED | YES | NO | NO | 861073 | 159119 | 56971 | 7367 | 925 | 2.8259e-05 | 1.1613e-06 | 24.3333 | 1 | 308 | Load | 44238 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009116 | PD-01242020-00170 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3925 | 833925 | 2020-01-24 09:24 | 2020-01-24 11:17 | 113.13 | 1 | 1 | 113.1333 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | WARR ACRES | 5521 N.DONALD | CMI_NORMAL | NO | NO | NO | 861073 | 168193 | 148371 | 7851 | 2183 | 0.00013139 | 1.1613e-06 | 113.1333 | 1 | 310 | Customer | 12342 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | OK - 2022
J2001.009117 |  | METRO WEST | WEST | 8297:MORGAN ROAD | MORGAN_ROAD_9731 | 829731 | 2020-01-24 09:26 | 2020-01-24 11:42 | 135.15 | 4 | 3 | 508.7333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 1120 N VALLEYVIEW | CMI_PLANNED | YES | NO | NO | 861073 | 128800 | 116045 | 2504 | 660 | 0.00059081 | 4.6454e-06 | 127.1833 | 1 | 308 | Load | 27141 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009133 | PD-01242020-00232 | NORTHEAST | SAPULPA | 3213:BOWDEN | BOWDEN_1329 | 321329 | 2020-01-24 10:03 | 2020-01-24 15:19 | 316.25 | 2 | 4 | 529.6333 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | SAPULPA | REGENCY M/H PARK HWY 97 N. | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861073 | 74037 | 40769 | 3372 | 1517 | 0.00061509 | 2.3227e-06 | 264.8167 | 1 | 320 | Secondary | 46516 | Load | Tran1phOH | CGI ADMIN | 918-261-6802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | OK - 2020
J2001.009138 |  | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1424 | 911424 | 2020-01-24 10:10 | 2020-01-24 10:38 | 28.27 | 4 | 4 | 88.1667 | 4 | DETERIORATION | 1 | TRANSFORMER UG | FORT SMITH | 5221 JOHNSON 79 | CMI_PLANNED | YES | NO | NO | 861073 | 82216 | 61184 | 4738 | 255 | 0.00010239 | 4.6454e-06 | 22.0417 | 1 | 308 | Secondary | 12701 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-24 | 2020 |  | Ark - Series 1
J2001.009137 |  | NORTHEAST | SAPULPA | 3213:BOWDEN | BOWDEN_1321 | 321321 | 2020-01-24 10:26 | 2020-01-24 18:33 | 486.77 | 2 | 1 | 939.7833 | 4 | DETERIORATION | 1 | TRANSFORMER UG | SAPULPA | 6800 S 65 W AVE(BRYANT IND) | CMI_PLANNED | YES | NO | NO | 861073 | 74037 | 40769 | 3372 | 820 | 0.0010914 | 2.3227e-06 | 469.8917 | 1 | 308 | Load | 20578 | Load | Tran3phPadWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009149 | PD-01242020-00212 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-01-24 10:32 | 2020-01-24 16:14 | 342.63 | 10 | 11 | 3283.8333 | 29 | TREES : GROW IN | 27 | CUTOUT | DEL CITY | 3313 CHEEK DR | CMI_NORMAL | NO | NO | NO | 861073 | 159119 | 102148 | 7416 | 2238 | 0.0038137 | 1.1613e-05 | 328.3833 | 1 | 310 | Load | 7373 | Load | Tran1phOH | JACOB SHANDY | 918-623-6369 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | OK - 2022
J2001.009145 |  | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_723 | 510723 | 2020-01-24 10:41 | 2020-01-24 11:43 | 61.98 | 3 | 4 | 166.3 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | ARDMORE | 1212 HARGROVE | CMI_PLANNED | YES | NO | NO | 861073 | 77606 | 23586 | 4509 | 1215 | 0.00019313 | 3.484e-06 | 55.4333 | 1 | 310 | Load | 16 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | #N/A
J2001.009150 |  | NORTHEAST | MUSKOGEE | 3313:ILLINOIS RIVER | ILLINOIS_RIVER_1321 | 331321 | 2020-01-24 10:48 | 2020-01-24 16:21 | 332.78 | 1 | 1 | 71.0167 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | WEBBERS FALLS | HWY 64 + ARK RIV BRDG | CMI_PLANNED | YES | NO | NO | 861073 | 74037 | 33268 | 791 | 791 | 8.2475e-05 | 1.1613e-06 | 71.0167 | 1 | 308 | Tap | 25801 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | OK - 2020
J2001.009154 | PD-01242020-00258 | NORTHEAST | SAPULPA | 7605:DRUMRIGHT | DRUMRIGHT_544 | 760544 | 2020-01-24 10:48 | 2020-01-24 12:34 | 105.82 | 1 | 1 | 103.0667 | 12 | POOR CONNECTION | 50 | CONNECTOR | OILTON | 109 W.FIRST | CMI_NORMAL | NO | NO | NO | 861073 | 74037 | 40769 | 1694 | 1114 | 0.0001197 | 1.1613e-06 | 103.0667 | 1 | 310 | Customer | 45096 | Load | Tran1phOH | NICHOLAS MANION | 918-290-1327 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | #N/A
J2001.009159 | PD-01242020-00243 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2222 | 832222 | 2020-01-24 10:51 | 2020-01-24 12:03 | 71.53 | 1 | 1 | 47.4841 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 4001 39th and penn | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 168193 | 148371 | 9175 | 1556 | 5.5145e-05 | 1.1613e-06 | 47.4841 | 1 | 310 | Customer | 226640 | Load | Tran3phWye | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | OK - 2022
J2001.009160 | PD-01242020-00248 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6021 | 836021 | 2020-01-24 10:54 | 2020-01-24 12:09 | 75.23 | 1 | 1 | 75.2333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | BETHANY | 3004 TROPICANA AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 128800 | 116045 | 5506 | 1451 | 8.7372e-05 | 1.1613e-06 | 75.2333 | 1 | 310 | Customer | 24705 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | #N/A
J2001.009162 |  | METRO SOUTH | SOUTH | 8705:NORMAN | NORMAN 22 | 870522 | 2020-01-24 10:58 | 2020-01-24 11:31 | 33.7 | 12 | 11 | 377 | 4 | DETERIORATION | 2 | TRANSFORMER OH | NORMAN | 125 W.SYMMES | CMI_PLANNED | YES | NO | NO | 861073 | 159119 | 56971 | 401 | 312 | 0.00043783 | 1.3936e-05 | 31.4167 | 1 | 310 | Load | 33532 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-01-24 | 2020 |  | #N/A
J2001.009164 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-01-24 11:07 | 2020-01-24 11:58 | 50.98 | 1 | 1 | 48.5 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | 7301 SE. 164TH | CMI_PLANNED | YES | NO | NO | 861073 | 159119 | 56971 | 4240 | 3071 | 5.6325e-05 | 1.1613e-06 | 48.5 | 1 | 308 | Load | 81130 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009174 | PD-01242020-00273 | METRO SOUTH | SOUTH CENTRAL | 8717:TURNER | TURNER_1723 | 871723 | 2020-01-24 11:16 | 2020-01-24 15:54 | 277.93 | 7 | 7 | 1869.9333 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | MOORE | 17205 S SANTA FE AV | CMI_NORMAL | NO | NO | NO | 861073 | 159119 | 102148 | 3083 | 1098 | 0.0021716 | 8.1294e-06 | 267.1333 | 1 | 310 | Load | 219244 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009167 |  | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_433 | 510433 | 2020-01-24 11:17 | 2020-01-24 13:52 | 155.17 | 11 | 9 | 1650.3667 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | ARDMORE | 0 | CMI_PLANNED | YES | NO | NO | 861073 | 77606 | 23586 | 2317 | 1258 | 0.0019166 | 1.2775e-05 | 150.0333 | 1 | 310 | Mainline |  | 0 | 0 | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009169 | PD-01242020-00266 | SOUTHERN | ARDMORE | 5117:MARIETTA | MARIETTA_1721 | 511721 | 2020-01-24 11:18 | 2020-01-24 16:28 | 310.13 | 1 | 1 | 303.05 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | ARDMORE | SW COR 77+77S | CMI_NORMAL | NO | NO | NO | 861073 | 77606 | 23586 | 1595 | 638 | 0.00035194 | 1.1613e-06 | 303.05 | 1 | 310 | Load | 8032 | Load | TranPad3phDelta | MICHAEL W JENNINGS | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | #N/A
J2001.009171 | PD-01242020-00271 | METRO NORTH | NORTH | 8209:CLASSEN | CLASSEN_963 | 820963 | 2020-01-24 11:22 | 2020-01-24 12:38 | 75.83 | 1 | 2 | 75.8333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | Alley on SS of Library(Park Ave) & East of Hudson approx 350 feet | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 168193 | 148371 | 3884 | 211 | 8.8068e-05 | 1.1613e-06 | 75.8333 | 1 | 310 | Customer | 320366 | Load | Tran3phPadWye | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009173 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-01-24 11:30 | 2020-01-24 12:19 | 49.1 | 2 | 0 | 89.1 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | 11508 SE.152 | CMI_PLANNED | YES | NO | NO | 861073 | 159119 | 56971 | 4240 | 3071 | 0.00010348 | 2.3227e-06 | 44.55 | 1 | 0 | Load | 54014 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009176 | PD-01242020-00283 | NORTHEAST | MUSKOGEE | 3312:CHECOTAH | CHECOTAH 21 | 331221 | 2020-01-24 11:34 | 2020-01-24 12:18 | 43.82 | 1 | 1 | 43.8167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | CHECOTAH | NW COR APTS @ SW 5 + AUDD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 74037 | 33268 | 2889 | 1359 | 5.0886e-05 | 1.1613e-06 | 43.8167 | 1 | 310 | Customer | 17192 | Load | Tran1phPad | NICHOLAS SELVIDGE | 918-652-1986 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | OK - 2020
J2001.009177 | PD-01242020-00280 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2229 | 852229 | 2020-01-24 11:37 | 2020-01-24 13:47 | 129.67 | 1 | 1 | 89.4333 | 4 | DETERIORATION | 50 | CONNECTOR | HARRAH | 6100 ACADEMY LN | CMI_NORMAL | NO | NO | NO | 861073 | 114369 | 71190 | 11630 | 1389 | 0.00010386 | 1.1613e-06 | 89.4333 | 1 | 320 | Load | 77188 | Load | Tran3phWye | CHRIS PROCELL | 405-831-2791 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009178 |  | NORTHWEST | WOODWARD | 4616:NEWMAN AVE | NEWMAN_AVE_1641 | 461641 | 2020-01-24 11:43 | 2020-01-24 11:52 | 9.07 | 1 | 1 | 9.0667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SHATTUCK | JENKINS+BUCHANAN SHATTUCK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 53534 | 10423 | 2012 | 2012 | 1.0529e-05 | 1.1613e-06 | 9.0667 | 1 | 310 | Customer | 11596 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | OK - 2020
J2001.009189 |  | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_629 | 870629 | 2020-01-24 11:59 | 2020-01-24 14:32 | 153.85 | 8 | 8 | 342.6667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | NORMAN | 1227 WESTLAWN DR | CMI_PLANNED | YES | NO | NO | 861073 | 159119 | 56971 | 7367 | 1373 | 0.00039795 | 9.2907e-06 | 42.8333 | 1 | 310 | Load | 31896 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009182 |  | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3624 | 853624 | 2020-01-24 12:02 | 2020-01-24 12:12 | 10.65 | 1 | 1 | 10.65 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1300 NE.7 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 168193 | 148371 | 5926 | 928 | 1.2368e-05 | 1.1613e-06 | 10.65 | 1 | 310 | Customer | 7705 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009186 | PD-01242020-00310 | NORTHEAST | MUSKOGEE | 3325:WELLS | WELLS_2542 | 332542 | 2020-01-24 12:03 | 2020-01-24 13:17 | 74.32 | 1 | 2 | 74.3167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | EUFAULA | 121 CLEVELAND EUFAULA,OK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 74037 | 33268 | 2378 | 1323 | 8.6307e-05 | 1.1613e-06 | 74.3167 | 1 | 310 | Customer | 1242 | Load | Tran1phOH | NICHOLAS SELVIDGE | 918-652-1986 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | OK - 2022
J2001.009185 | PD-01242020-00290 | METRO EAST | EAST | 8416:DUNJEE | DUNJEE_1621 | 841621 | 2020-01-24 12:03 | 2020-01-24 15:48 | 224.53 | 1 | 1 | 224.5333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | CHOCTAW | 14317 NE 23rd | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 114369 | 71190 | 3541 | 1552 | 0.00026076 | 1.1613e-06 | 224.5333 | 1 | 310 | Customer | 400761 | Load | Tran3phPadWye | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009195 | PD-01242020-00307 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3631 | 833631 | 2020-01-24 12:17 | 2020-01-24 13:06 | 48.55 | 3 | 3 | 137.65 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2613 NW.110 | CMI_NORMAL | NO | NO | NO | 861073 | 168193 | 148371 | 8788 | 1337 | 0.00015986 | 3.484e-06 | 45.8833 | 1 | 310 | Secondary | 10204 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | OK - 2021
J2001.009197 | PD-01242020-00316 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3624 | 853624 | 2020-01-24 12:22 | 2020-01-24 12:56 | 34.15 | 1 | 1 | 34.15 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1300 NE.7 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 168193 | 148371 | 5926 | 928 | 3.966e-05 | 1.1613e-06 | 34.15 | 1 | 310 | Customer | 7705 | Load | TranOpenDelta | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009198 | PD-01242020-00318 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-01-24 12:28 | 2020-01-24 13:10 | 42.37 | 1 | 1 | 42.3667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DEL CITY | 2417 S.MANSFIELD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 159119 | 102148 | 7416 | 2238 | 4.9202e-05 | 1.1613e-06 | 42.3667 | 1 | 310 | Customer | 6270 | Load | Tran1phOH | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | OK - 2022
J2001.009199 | PD-01242020-00313 | METRO WEST | WEST | 8297:MORGAN ROAD | MORGAN_ROAD_9722 | 829722 | 2020-01-24 12:29 | 2020-01-24 14:45 | 135.65 | 1 | 1 | 135.65 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 400 N. MORGAN RD. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 128800 | 116045 | 2504 | 664 | 0.00015754 | 1.1613e-06 | 135.65 | 1 | 320 | Load | 200414 | Load | Tran3phPadWye | GARY J WATSON | 405-517-3524 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009202 | PD-01242020-00319 | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_622 | 730622 | 2020-01-24 12:32 | 2020-01-24 13:27 | 55.27 | 1 | 1 | 55.2667 | 1 | CANCELLED | 57 | CANCELLED | SEMINOLE | 1224 N JEFFERSON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 114369 | 13605 | 4063 | 1253 | 6.4183e-05 | 1.1613e-06 | 55.2667 | 1 | 310 | Customer | 5329 | Load | Tran1phOH | BRADY A HUFF | 405-519-0701 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | OK - 2020
J2001.009204 | PD-01242020-00329 | METRO SOUTH | SOUTH | 8726:NOBLE | NOBLE_2621 | 872621 | 2020-01-24 12:45 | 2020-01-24 15:05 | 140.35 | 1 | 1 | 115.4667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | NOBLE | 707 HOLSEY DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861073 | 159119 | 56971 | 2968 | 1447 | 0.0001341 | 1.1613e-06 | 115.4667 | 1 | 310 | Customer | 62483 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009207 | PD-01242020-00330 | METRO SOUTH | SOUTH | 8719:PLEASANT VLY | PLEASANT_VAL_1924 | 871924 | 2020-01-24 12:51 | 2020-01-24 13:36 | 44.52 | 1 | 1 | 42.0962 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | W side Lorings Ci | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 159119 | 56971 | 2108 | 929 | 4.8888e-05 | 1.1613e-06 | 42.0962 | 1 | 310 | Customer | 350874 | Load | Tran1phPad | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009208 |  | NORTHEAST | SAPULPA | 7605:DRUMRIGHT | DRUMRIGHT_544 | 760544 | 2020-01-24 12:55 | 2020-01-24 16:35 | 219.78 | 2 | 2 | 431.55 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OILTON | 514 W.BDWY | CMI_PLANNED | YES | NO | NO | 861073 | 74037 | 40769 | 1694 | 1114 | 0.00050118 | 2.3227e-06 | 215.775 | 1 | 308 | Load | 41091 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | #N/A
J2001.009213 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-01-24 13:06 | 2020-01-24 13:19 | 12.32 | 1 | 1 | 12.3167 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | FORT SMITH | 605 CEDAR LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 82216 | 61184 | 1456 | 1238 | 1.4304e-05 | 1.1613e-06 | 12.3167 | 1 | 310 | Customer | 9963 | Load | Tran1phOH | Cancel | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | Ark - Series 2
J2001.009212 |  | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_621 | 870621 | 2020-01-24 13:08 | 2020-01-24 15:10 | 121.38 | 4 | 2 | 298.9 | 4 | DETERIORATION | 2 | TRANSFORMER OH | NORMAN | 1504 ANN ARBOR | CMI_PLANNED | YES | NO | NO | 861073 | 159119 | 56971 | 7367 | 925 | 0.00034713 | 4.6454e-06 | 74.725 | 1 | 310 | Load | 46434 | Load | TranOHDeltaSplitBank | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009214 | PD-01242020-00338 | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2223 | 882223 | 2020-01-24 13:09 | 2020-01-24 15:05 | 115.82 | 1 | 1 | 115.8167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | EDMOND | 2521 N.VALLEYVIEW | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 168193 | 19822 | 5387 | 1203 | 0.0001345 | 1.1613e-06 | 115.8167 | 1 | 310 | Load | 40864 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009215 |  | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1021 | 311021 | 2020-01-24 13:10 | 2020-01-24 13:10 | 0 | 299 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MUSKOGEE | 1541 COUNTRY CLUB PLACE | CMI_MOMENTARY | YES | NO | NO | 861073 | 74037 | 33268 | 2903 | 299 | 0 | 0.00034724 | 0 | 1 | 0 | Feeder | RIVERSIDE_1021 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-24 | 2020 |  | #N/A
J2001.009218 | PD-01242020-00341 | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1021 | 311021 | 2020-01-24 13:10 | 2020-01-24 14:23 | 72.65 | 3 | 2 | 204.35 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | MUSKOGEE | 3507 bona villa dr muskogee | CMI_NORMAL | NO | NO | NO | 861073 | 74037 | 33268 | 2903 | 299 | 0.00023732 | 3.484e-06 | 68.1167 | 1 | 310 | Load | 9806 | Load | Tran1phPad | NORTHEAST BOUG | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | #N/A
J2001.009219 | PD-01242020-00342 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4123 | 814123 | 2020-01-24 13:19 | 2020-01-24 13:45 | 25.7 | 1 | 1 | 25.7 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 216 SE.53 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 159119 | 102148 | 5808 | 1324 | 2.9846e-05 | 1.1613e-06 | 25.7 | 1 | 310 | Customer | 20356 | Load | Tran1phOH | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | #N/A
J2001.009221 | PD-01242020-00345 | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 22 | 570822 | 2020-01-24 13:26 | 2020-01-24 14:51 | 84.93 | 1 | 1 | 84.9333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DAVIS | 309 W.MAIN DAVIS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 77606 | 6813 | 1859 | 955 | 9.8637e-05 | 1.1613e-06 | 84.9333 | 1 | 310 | Customer | 9167 | Load | Tran1phOH | GARRID H BROWN | 405-207-3948 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | OK - 2021
J2001.009225 | PD-01242020-00358 | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-24 13:41 | 2020-01-24 14:48 | 66.85 | 1 | 1 | 66.85 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | LAVACA | 1101 RALEIGH ST. | CMI_NORMAL | NO | NO | NO | 861073 | 82216 | 61184 | 2735 | 2123 | 7.7636e-05 | 1.1613e-06 | 66.85 | 1 | 320 | Load | 158676 | Load | TranOpenDelta | ANDREW SCOTT LONG | 479-739-1879 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | Ark - Series 2
J2001.009231 |  | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_521 | 890521 | 2020-01-24 14:04 | 2020-01-24 15:13 | 68.43 | 1 | 1 | 68.4333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | EL RENO | 415 S.BARKER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 128800 | 12755 | 6943 | 2218 | 7.9474e-05 | 1.1613e-06 | 68.4333 | 1 | 310 | Customer | 34145 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009232 | PD-01242020-00364 | NORTHWEST | ENID | 4153:IMO | IMO_5322 | 415322 | 2020-01-24 14:04 | 2020-01-24 14:49 | 44.82 | 1 | 1 | 44.8167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ENID | 1111 S.OAKWOOD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 53534 | 37591 | 1177 | 506 | 5.2047e-05 | 1.1613e-06 | 44.8167 | 1 | 310 | Customer | 7794 | Load | Tran1phPad | RONALD K GOSE | 580-541-3131 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009236 | PD-01242020-00387 | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_921 | 910921 | 2020-01-24 14:08 | 2020-01-24 15:59 | 110.82 | 7 | 7 | 751.9167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | FORT SMITH | 3223 S.27 | CMI_NORMAL | NO | NO | NO | 861073 | 82216 | 61184 | 5010 | 1427 | 0.00087323 | 8.1294e-06 | 107.4167 | 1 | 310 | Load | 9264 | Load | Tran1phOH | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | Ark - Series 3
J2001.009237 | PD-01242020-00378 | METRO EAST | SEMINOLE | 7312:JUMPER CREEK | JUMPER_CREEK_1227 | 731227 | 2020-01-24 14:13 | 2020-01-24 15:40 | 86.5 | 1 | 1 | 86.1167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | SEMINOLE | ,5 MS OF EW 144 ON NS 350 | CMI_NORMAL | NO | NO | NO | 861073 | 114369 | 13605 | 1217 | 886 | 0.00010001 | 1.1613e-06 | 86.1167 | 1 | 310 | Load | 335268 | Load | Tran1phOH | BRADY A HUFF | 405-519-0701 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | OK - 2021
J2001.009238 | PD-01242020-00375 | SOUTHERN | HEALDTON | 5322:DUNDEE | DUNDEE 22 | 532222 | 2020-01-24 14:14 | 2020-01-24 15:01 | 47.4 | 1 | 1 | 47.4 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | RINGLING | 217 E.MAIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 77606 | 6797 | 1013 | 1002 | 5.5048e-05 | 1.1613e-06 | 47.4 | 1 | 310 | Customer | 9480 | Load | TranOpenDelta | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009248 | PD-01242020-00399 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3923 | 833923 | 2020-01-24 14:30 | 2020-01-24 15:59 | 89.03 | 25 | 22 | 3471.25 | 22 | WIND | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | NW.52 + GRAND BLVD | CMI_NORMAL | NO | NO | NO | 861073 | 168193 | 148371 | 7851 | 1246 | 0.0040313 | 2.9034e-05 | 138.85 | 1 | 311 | Mainline | 1672 | Fuse | FuseRiser | SHAWN HILL | 405-308-1695 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | OK - 2022
J2001.009245 | PD-01242020-00403 | METRO SOUTH | SOUTH | 8726:NOBLE | NOBLE_2621 | 872621 | 2020-01-24 14:33 | 2020-01-24 15:31 | 58.12 | 1 | 1 | 58.1167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NOBLE | 706 HALSEY DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 159119 | 56971 | 2968 | 1447 | 6.7493e-05 | 1.1613e-06 | 58.1167 | 1 | 320 | Customer | 62482 | Load | Tran1phPad | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009247 | PD-01242020-00400 | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5222 | 835222 | 2020-01-24 14:36 | 2020-01-24 15:50 | 73.93 | 1 | 1 | 73.9333 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 13317 PLAZA TERR APT 137 | CMI_NORMAL | NO | NO | NO | 861073 | 168193 | 148371 | 6517 | 1353 | 8.5862e-05 | 1.1613e-06 | 73.9333 | 1 | 320 | Customer | 69574 | Load | Tran1phPad | SHAWN HILL | 405-308-1695 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009252 | PD-01242020-00402 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3729 | 833729 | 2020-01-24 14:44 | 2020-01-24 16:34 | 109.97 | 1 | 1 | 109.9667 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 512 NW.95 | CMI_NORMAL | NO | NO | NO | 861073 | 168193 | 148371 | 5766 | 1400 | 0.00012771 | 1.1613e-06 | 109.9667 | 1 | 310 | Customer | 21694 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | OK - 2021
J2001.009253 | PD-01242020-00407 | METRO SOUTH | SOUTH CENTRAL | 8717:TURNER | TURNER_1723 | 871723 | 2020-01-24 14:47 | 2020-01-24 16:22 | 94.6 | 1 | 1 | 94.6 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | NORMAN | 2855 INDIAN HILLS RD | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861073 | 159119 | 102148 | 3083 | 1098 | 0.00010986 | 1.1613e-06 | 94.6 | 1 | 310 | Load | 419192 | Load | Tran3phPadWye | MONTY WISELEY | 405-471-2592 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009258 |  | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6523 | 836523 | 2020-01-24 15:11 | 2020-01-24 15:19 | 7.4 | 1 | 1 | 7.4 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7305 LYREWOOD LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 128800 | 116045 | 7421 | 2257 | 8.5939e-06 | 1.1613e-06 | 7.4 | 1 | 310 | Customer | 38608 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | OK - 2022
J2001.009262 | PD-01242020-00430 | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5222 | 835222 | 2020-01-24 15:29 | 2020-01-24 16:16 | 46.78 | 1 | 1 | 46.7833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | w memorial rd & n may ave | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 168193 | 148371 | 6517 | 1353 | 5.4331e-05 | 1.1613e-06 | 46.7833 | 1 | 310 | Customer | 376875 | Load | Tran3phPadWye | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009265 |  | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3923 | 833923 | 2020-01-24 15:32 | 2020-01-24 15:37 | 4.68 | 1222 | 83 | 5723.0333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 4107 NW 55TH ST | CMI_MOMENTARY | YES | NO | NO | 861073 | 168193 | 148371 | 7851 | 1246 | 0.0066464 | 0.0014192 | 4.6833 | 1 | 310 | Feeder | TULSA_3923 | Recloser | SubRecloser | Crew | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-24 | 2020 |  | OK - 2022
J2001.009268 |  | SOUTHERN | HEALDTON | 5122:DILLARD | DILLARD_2222 | 512222 | 2020-01-24 15:43 | 2020-01-24 15:43 | 0.07 | 698 | 0 | 46.5333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | WILSON | 7460 DILLARD RD | CMI_MOMENTARY | YES | NO | NO | 861073 | 77606 | 6797 | 1189 | 698 | 5.4041e-05 | 0.00081062 | 0.066667 | 1 | 0 | Feeder | DILLARD_2222 | Breaker | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009272 | PD-01242020-00450 | SOUTHERN | HEALDTON | 5122:DILLARD | DILLARD_2222 | 512222 | 2020-01-24 15:56 | 2020-01-24 16:58 | 61.92 | 1 | 1 | 61.9167 | 5 | ELECTRICAL TRACKING | 21 | FUSE - TRANSFORMER | WILSON | ALLEY E OF 3RD + N OF CEDAR | CMI_NORMAL | NO | NO | NO | 861073 | 77606 | 6797 | 1189 | 698 | 7.1906e-05 | 1.1613e-06 | 61.9167 | 1 | 310 | Customer | 20717 | Load | Tran1phOH | RANDAL G CALLAWAY | 580-220-8449 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009281 |  | METRO EAST | EAST | 8417:ROUND BARN | ROUND_BARN_1723 | 841723 | 2020-01-24 16:11 | 2020-01-24 18:48 | 156.35 | 3 | 1 | 131.325 | 4 | DETERIORATION | 2 | TRANSFORMER OH | ARCADIA | 120 NE.5 | CMI_PLANNED | YES | NO | NO | 861073 | 114369 | 71190 | 1007 | 1007 | 0.00015251 | 3.484e-06 | 43.775 | 1 | 310 | Load | 15468 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009283 |  | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3721 | 913721 | 2020-01-24 16:40 | 2020-01-24 17:02 | 21.67 | 10 | 0 | 60.6667 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | S.46 ST- N OF S. U ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 82216 | 61184 | 4569 | 1498 | 7.0455e-05 | 1.1613e-05 | 6.0667 | 1 | 0 | Mainline | 2592 | Fuse | FuseRiser | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | Ark - Series 3
J2001.009288 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1231 | 831231 | 2020-01-24 16:58 | 2020-01-24 16:58 | 0 | 455 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 5529 CLASSEN BLVD | CMI_MOMENTARY | YES | NO | NO | 861073 | 168193 | 148371 | 7744 | 467 | 0 | 0.00052841 | 0 | 1 | 0 | Feeder | BEL ISLE_1231 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-24 | 2020 |  | OK - 2022
J2001.009289 | PD-01242020-00489 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1122 | 511122 | 2020-01-24 17:04 | 2020-01-24 18:07 | 63.2 | 1 | 1 | 63.2 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | DICKSON | 4.5E 1/4N HWY 70E | CMI_NORMAL | NO | NO | NO | 861073 | 77606 | 23586 | 2209 | 1207 | 7.3397e-05 | 1.1613e-06 | 63.2 | 1 | 310 | Load | 20421 | Load | Tran1phOH | ANDREW CHAVERS | 580-504-0524 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009290 | PD-01242020-00490 | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_723 | 510723 | 2020-01-24 17:08 | 2020-01-24 18:32 | 83.83 | 1 | 1 | 83.8333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ARDMORE | 22 BROADLAWN-VL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 77606 | 23586 | 4509 | 1215 | 9.7359e-05 | 1.1613e-06 | 83.8333 | 1 | 310 | Customer | 9753 | Load | Tran3phWye | ANDREW CHAVERS | 580-504-0524 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | #N/A
J2001.009296 | PD-01242020-00493 | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_661 | 550661 | 2020-01-24 17:44 | 2020-01-24 18:32 | 48.5 | 1 | 1 | 48.5 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DURANT | MI N OP HDQ ON ES OF HWY 78 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 77606 | 15489 | 6737 | 446 | 5.6325e-05 | 1.1613e-06 | 48.5 | 1 | 310 | Customer | 5234 | Load | Tran1phOH | SHAD BARNETT | 580-258-0077 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009297 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-24 17:44 | 2020-01-24 17:53 | 8.62 | 1 | 1 | 8.6167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ARKOMA | 425 MAIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 82216 | 61184 | 2936 | 875 | 1.0007e-05 | 1.1613e-06 | 8.6167 | 1 | 310 | Customer | 13782 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-24 | 2020 |  | Ark - Series 2
J2001.009307 | PD-01242020-00497 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1523 | 811523 | 2020-01-24 18:30 | 2020-01-24 20:07 | 97.08 | 1 | 3 | 81.05 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 2217 SW.19 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861073 | 159125 | 102154 | 6061 | 805 | 9.4127e-05 | 1.1613e-06 | 81.05 | 1 | 311 | Customer | 5738 | Load | TranOpenDelta | COLIN B BROWN | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | OK - 2022
J2001.009308 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1221 | 831221 | 2020-01-24 18:39 | 2020-01-24 19:01 | 21.87 | 1 | 1 | 21.8667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2725 NW.65 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 168207 | 148386 | 7745 | 989 | 2.5395e-05 | 1.1613e-06 | 21.8667 | 1 | 310 | Customer | 28787 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | OK - 2022
J2001.009315 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-01-24 19:51 | 2020-01-24 19:57 | 5.37 | 1 | 1 | 5.3667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 806 NW.25 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 168207 | 148386 | 11124 | 2336 | 6.2325e-06 | 1.1613e-06 | 5.3667 | 1 | 310 | Customer | 437 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | OK - 2020
J2001.009318 | PD-01242020-00501 | ARKANSAS | OZARK | 9406:HELBERG | HELBERG_621 | 940621 | 2020-01-24 20:00 | 2020-01-24 21:47 | 106.8 | 1 | 2 | 105.75 | 5 | ELECTRICAL TRACKING | 20 | FUSE BARREL | OZARK | OZARK AR ON KING MOUNTAIN | CMI_NORMAL | NO | NO | NO | 861073 | 82221 | 7546 | 1721 | 834 | 0.00012281 | 1.1613e-06 | 105.75 | 1 | 310 | Load | 4880 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | Ark - Series 3
J2001.009322 | PD-01242020-00506 | METRO WEST | WEST | 8222:CZECH HALL | CZECH_HALL_2222 | 822222 | 2020-01-24 21:06 | 2020-01-24 22:43 | 96.75 | 1 | 1 | 82.3667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 416 PUMPKIN CI | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861073 | 128809 | 116052 | 8606 | 2027 | 9.5656e-05 | 1.1613e-06 | 82.3667 | 1 | 310 | Customer | 53131 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009333 | PD-01242020-00509 | METRO NORTH | NORTH | 8464:BRYANT | BRYANT_6421 | 846421 | 2020-01-24 21:20 | 2020-01-24 22:30 | 70.13 | 1 | 2 | 50.9833 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 3600 N E 115TH | CMI_NORMAL | NO | NO | NO | 861073 | 168207 | 148386 | 1894 | 1265 | 5.9209e-05 | 1.1613e-06 | 50.9833 | 1 | 310 | Load | 72244 | Load | Tran1phOH | CAMERON PITTS | 405-537-6633 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009327 |  | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1721 | 861721 | 2020-01-24 21:23 | 2020-01-24 22:34 | 70.72 | 6 | 4 | 180.2 | 12 | POOR CONNECTION | 1 | TRANSFORMER UG | OKLAHOMA CITY | 5524 SHALIMAR DR | CMI_NORMAL | NO | NO | NO | 861073 | 114380 | 71194 | 6950 | 1505 | 0.00020927 | 6.9681e-06 | 30.0333 | 1 | 308 | Load | 56126 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | #N/A
J2001.009329 |  | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1721 | 861721 | 2020-01-24 21:24 | 2020-01-24 22:32 | 68.6 | 1 | 2 | 29.3833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 5508 SHALIMAK DR | CMI_NORMAL | NO | NO | NO | 861073 | 114380 | 71194 | 6950 | 1505 | 3.4124e-05 | 1.1613e-06 | 29.3833 | 1 | 310 | Customer | 56127 | Load | Tran1phPad | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | #N/A
J2001.009330 |  | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1721 | 861721 | 2020-01-24 21:24 | 2020-01-24 22:32 | 67.47 | 6 | 8 | 174.6 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | 5620 SHALIMAR DR | CMI_NORMAL | NO | NO | NO | 861073 | 114380 | 71194 | 6950 | 1505 | 0.00020277 | 6.9681e-06 | 29.1 | 1 | 310 | Load | 56125 | Load | Tran1phPad | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | #N/A
J2001.009332 |  | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1721 | 861721 | 2020-01-24 21:24 | 2020-01-24 22:31 | 66.68 | 6 | 5 | 173.75 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | 3612 SE.57 | CMI_NORMAL | NO | NO | NO | 861073 | 114380 | 71194 | 6950 | 1505 | 0.00020178 | 6.9681e-06 | 28.9583 | 1 | 310 | Load | 56123 | Load | Tran1phPad | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | #N/A
J2001.009328 |  | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1721 | 861721 | 2020-01-24 21:24 | 2020-01-24 21:24 | 0 | 1485 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 3600 S SUNNYLANE RD | CMI_MOMENTARY | YES | NO | NO | 861073 | 114380 | 71194 | 6950 | 1505 | 0 | 0.0017246 | 0 | 1 | 0 | Feeder | SUNNYLAN_1721 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-24 | 2020 |  | #N/A
J2001.009334 |  | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1721 | 861721 | 2020-01-24 21:37 | 2020-01-24 22:30 | 52.88 | 1 | 1 | 15.8667 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | 5708 SHALIMAR DR | CMI_NORMAL | NO | NO | NO | 861073 | 114380 | 71194 | 6950 | 1505 | 1.8427e-05 | 1.1613e-06 | 15.8667 | 1 | 310 | Customer | 56124 | Load | Tran1phPad | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-24 | 2020 |  | #N/A
J2001.009336 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4529 | 824529 | 2020-01-24 21:55 | 2020-01-24 22:03 | 7.6 | 1 | 1 | 7.6 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 8031 W. Reno Ave. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 128809 | 116052 | 3408 | 256 | 8.8262e-06 | 1.1613e-06 | 7.6 | 1 | 310 | Customer | 311146 | Load | Tran3phPadWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | #N/A
J2001.009339 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-01-24 22:05 | 2020-01-24 22:15 | 9.9 | 1 | 1 | 9.9 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1225 W.HEFNER RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861073 | 168207 | 148386 | 8788 | 1952 | 1.1497e-05 | 1.1613e-06 | 9.9 | 1 | 310 | Customer | 35733 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-24 | 2020 |  | OK - 2021
J2001.009358 |  | ARKANSAS | FORT SMITH | 9508:WHITESIDE | WHITESIDE_821 | 950821 | 2020-01-25 00:17 | 2020-01-25 01:28 | 70.92 | 8 | 8 | 446.5333 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | VAN BUREN | 814 N.25, N-EMMA AVE | CMI_NORMAL | NO | NO | NO | 861073 | 82221 | 61188 | 1920 | 1281 | 0.00051858 | 9.2907e-06 | 55.8167 | 1 | 310 | Load | 5635 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-25 | 2020 |  | Ark - Series 2
J2001.009363 | PD-01252020-00004 | NORTHWEST | ALVA | 4705:ALVA | ALVA_521 | 470521 | 2020-01-25 00:46 | 2020-01-25 03:00 | 134.48 | 1 | 1 | 147.05 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | ALVA | 918 MAPLE--ALVA | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861073 | 53540 | 5520 | 2439 | 738 | 0.00017078 | 1.1613e-06 | 147.05 | 1 | 310 | Customer | 9066 | Load | Tran1phOH | PATRICK LYONS | 580-395-4171 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-25 | 2020 |  | #N/A
J2001.009364 | PD-01252020-00006 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3923 | 833923 | 2020-01-25 01:22 | 2020-01-25 02:59 | 97.02 | 1 | 1 | 97.0167 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 5117 COLFAX PL | CMI_NORMAL | NO | NO | NO | 861073 | 168207 | 148386 | 7852 | 1247 | 0.00011267 | 1.1613e-06 | 97.0167 | 1 | 310 | Customer | 21235 | Load | Tran1phOH | CAMERON PITTS | 405-537-6633 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | OK - 2022
J2001.009393 | PD-01252020-00013 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6121 | 836121 | 2020-01-25 06:42 | 2020-01-25 08:35 | 112.98 | 1 | 1 | 112.9833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1824 NW.37 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168207 | 148386 | 11124 | 1638 | 0.00013121 | 1.1613e-06 | 112.9833 | 1 | 310 | Customer | 459 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | OK - 2021
J2001.009401 | PD-01252020-00017 | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2163 | 892163 | 2020-01-25 07:51 | 2020-01-25 10:52 | 180.58 | 1 | 2 | 42.95 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | UNION CITY | 5ME OF HWY81 .25N OF HWY152 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 128809 | 12757 | 3189 | 1138 | 4.9877e-05 | 1.1613e-06 | 42.95 | 1 | 320 | Load | 79527 | Load | Tran1phOH | MICHAEL T MAHEN | 405-210-6029 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | OK - 2021
J2001.009402 |  | METRO NORTH | NORTH | 8347:WILSHIRE | WILSHIRE_4721 | 834721 | 2020-01-25 07:59 | 2020-01-25 09:17 | 77.73 | 1 | 0 | 77.7362 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | BROOKLINE + NW.EXPWY | CMI_PLANNED | YES | NO | NO | 861113 | 168207 | 148386 | 4624 | 927 | 9.0274e-05 | 1.1613e-06 | 77.7362 | 1 | 0 | Mainline | 7271 | Fuse | FuseRiser | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | OK - 2022
J2001.009408 | PD-01252020-00020 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2229 | 852229 | 2020-01-25 08:38 | 2020-01-25 13:13 | 275.42 | 1 | 1 | 14.3881 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | HARRAH | 19110 E WILSHIRE BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 114380 | 71194 | 11632 | 1390 | 1.6709e-05 | 1.1613e-06 | 14.3881 | 1 | 320 | Load | 51103 | Load | Tran1phOH | STEPHEN R MEADOWS | 405-641-5657 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009411 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1862 | 941862 | 2020-01-25 08:43 | 2020-01-25 17:05 | 501.68 | 5 | 2 | 632.25 | 4 | DETERIORATION | 12 | POLE | LAMAR | SHROPSHIRE AND COZORT | CMI_PLANNED | YES | NO | NO | 861113 | 82221 | 7546 | 730 | 730 | 0.00073422 | 5.8064e-06 | 126.45 | 1 | 308 | Tap | 6080 | Fuse | FuseOH | Contractor | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-25 | 2020 |  | Ark - Series 2
J2001.009417 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3831 | 913831 | 2020-01-25 08:44 | 2020-01-25 16:53 | 488.85 | 4 | 3 | 1501.1 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | WHEELER N VICKSBURG | CMI_PLANNED | YES | NO | NO | 861113 | 82221 | 61188 | 2936 | 486 | 0.0017432 | 4.6452e-06 | 375.275 | 1 | 308 | Mainline | 6636 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-25 | 2020 |  | Ark - Series 2
J2001.009414 |  | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3024 | 743024 | 2020-01-25 08:53 | 2020-01-25 12:36 | 223.28 | 1 | 0 | 133.2 | 4 | DETERIORATION | 1 | TRANSFORMER UG | SHAWNEE | 3P S 10TH BTW BDWY+BRD | CMI_PLANNED | YES | NO | NO | 861113 | 114380 | 22114 | 6646 | 1640 | 0.00015468 | 1.1613e-06 | 133.2 | 1 | 0 | Tap | 2314 | Fuse | FuseRiser | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009415 |  | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2729 | 872729 | 2020-01-25 08:53 | 2020-01-25 12:02 | 189.02 | 1 | 0 | 183.8167 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | NORMAN | 1550 O''BANNON LANE | CMI_PLANNED | YES | NO | NO | 861113 | 159125 | 56971 | 6464 | 1265 | 0.00021346 | 1.1613e-06 | 183.8167 | 1 | 0 | Load | 187935 | Load | Tran3phPadWye | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009420 | PD-01252020-00022 | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_661 | 550661 | 2020-01-25 08:57 | 2020-01-25 10:28 | 91.4 | 1 | 2 | 82.3167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DURANT | MI N OP HDQ ON ES OF HWY 78 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 77609 | 15489 | 6737 | 446 | 9.5593e-05 | 1.1613e-06 | 82.3167 | 1 | 310 | Customer | 5234 | Load | Tran1phOH | SHAD BARNETT | 580-258-0077 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009419 |  | ARKANSAS | OZARK | 9412:ALTUS | ALTUS_1229 | 941229 | 2020-01-25 09:09 | 2020-01-25 09:23 | 14.08 | 1 | 1 | 14.0833 | 1 | CANCELLED | 57 | CANCELLED | OZARK | 1 M. SOUTH POND CREEK 1/4M. W. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 82221 | 7546 | 865 | 865 | 1.6355e-05 | 1.1613e-06 | 14.0833 | 1 | 310 | Load | 17744 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-25 | 2020 |  | Ark - Series 2
J2001.009424 |  | METRO EAST | SEMINOLE | 7321:LETHA | LETHA_2122 | 732122 | 2020-01-25 09:27 | 2020-01-25 09:42 | 14.55 | 1 | 1 | 14.55 | 1 | CANCELLED | 57 | CANCELLED | MAUD | 35169 E 126 RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 114380 | 13607 | 1262 | 833 | 1.6897e-05 | 1.1613e-06 | 14.55 | 1 | 310 | Load | 90153 | Load | 0 | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-25 | 2020 |  | #N/A
J2001.009435 | PD-01252020-00025 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2231 | 852231 | 2020-01-25 10:11 | 2020-01-25 12:22 | 131.32 | 1 | 1 | 131.3167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 14525 SE.44 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 114380 | 71194 | 11632 | 1437 | 0.0001525 | 1.1613e-06 | 131.3167 | 1 | 310 | Customer | 68452 | Load | Tran1phOH | STEPHEN R MEADOWS | 405-641-5657 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | OK - 2021
J2001.009436 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-25 10:15 | 2020-01-25 10:15 | 0.02 | 875 | 0 | 14.5833 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | FT SMITH | 1904 SOUTH 7TH ST | CMI_MOMENTARY | YES | NO | NO | 861113 | 82221 | 61188 | 2936 | 875 | 1.6935e-05 | 0.0010161 | 0.016667 | 1 | 0 | Feeder | ARKOMA_3824 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-25 | 2020 |  | Ark - Series 2
J2001.009439 | PD-01252020-00026 | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_661 | 550661 | 2020-01-25 10:21 | 2020-01-25 17:21 | 419.7 | 1 | 1 | 395.1167 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | DURANT | 107 MILLS DR,ROLLING WD HILLS | CMI_NORMAL | NO | NO | NO | 861113 | 77609 | 15489 | 6737 | 446 | 0.00045884 | 1.1613e-06 | 395.1167 | 1 | 310 | Customer | 21317 | Load | Tran1phPad | SHAD BARNETT | 580-258-0077 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009447 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-01-25 10:38 | 2020-01-25 10:51 | 12.63 | 1 | 1 | 12.6333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1301 W.HEFNER RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168207 | 148386 | 8788 | 1952 | 1.4671e-05 | 1.1613e-06 | 12.6333 | 1 | 310 | Customer | 75584 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | OK - 2021
J2001.009450 | PD-01252020-00030 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6021 | 836021 | 2020-01-25 10:50 | 2020-01-25 18:11 | 441.1 | 13 | 29 | 5690.1 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | BETHANY | 7604 NW.25 | CMI_NORMAL | NO | NO | NO | 861113 | 128809 | 116052 | 5506 | 1451 | 0.0066078 | 1.5097e-05 | 437.7 | 1 | 310 | Load | 9631 | Load | Tran1phOH | STEVEN GILES | 405-227-2802 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-25 | 2020 |  | #N/A
J2001.009452 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7421 | 847421 | 2020-01-25 11:01 | 2020-01-25 11:01 | 0.03 | 407 | 0 | 13.5667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 1131 NE 33RD ST | CMI_MOMENTARY | YES | NO | NO | 861113 | 168207 | 148386 | 6165 | 407 | 1.5755e-05 | 0.00047264 | 0.033333 | 1 | 0 | Feeder | STONEWALL_7421 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-25 | 2020 |  | OK - 2022
J2001.009454 | PD-01252020-00031 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_623 | 870623 | 2020-01-25 11:08 | 2020-01-25 13:42 | 153.73 | 1 | 1 | 23.3833 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | NORMAN | 1429 AVONDALE DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 159125 | 56971 | 7367 | 1900 | 2.7155e-05 | 1.1613e-06 | 23.3833 | 1 | 310 | Customer | 46526 | Load | Tran1phOH | MARK A PALMORE | 405-512-1933 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | OK - 2021
J2001.009457 | PD-01252020-00037 | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1021 | 311021 | 2020-01-25 11:13 | 2020-01-25 13:42 | 148.87 | 1 | 1 | 148.8667 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | MUSKOGEE | 1125 SKYVIEW DR | CMI_NORMAL | NO | NO | NO | 861113 | 74036 | 33270 | 2903 | 299 | 0.00017288 | 1.1613e-06 | 148.8667 | 1 | 310 | Load | 12873 | Load | Tran1phOH | JOSH CHENEY | 918-619-3590 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-25 | 2020 |  | #N/A
J2001.009458 | PD-01252020-00032 | NORTHWEST | ENID | 4518:MENO TAP | MENO TAP 22 | 451822 | 2020-01-25 11:16 | 2020-01-25 13:48 | 152.27 | 1 | 1 | 152.2667 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 21 | FUSE - TRANSFORMER | LAHOMA | FROM MENO 2ME 1.75MN WS | CMI_NORMAL | NO | NO | NO | 861113 | 53540 | 37597 | 1332 | 830 | 0.00017683 | 1.1613e-06 | 152.2667 | 1 | 310 | Load | 2138 | Load | Tran1phOH | RONALD K GOSE | 580-541-3131 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009462 |  | METRO WEST | WEST | 8321:PIEDMONT | PIEDMONT_2169 | 832169 | 2020-01-25 11:26 | 2020-01-25 11:26 | 0 | 1656 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | PIEDMONT | 2401 WASHINGTON AVE NE | CMI_MOMENTARY | YES | NO | NO | 861113 | 128809 | 116052 | 6294 | 1656 | 0 | 0.0019231 | 0 | 1 | 0 | Feeder | PIEDMONT_2169 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009463 |  | METRO WEST | WEST | 8321:PIEDMONT | PIEDMONT_2164 | 832164 | 2020-01-25 11:26 | 2020-01-25 11:26 | 0 | 3007 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | PIEDMONT | 2401 WASHINGTON AVE NE | CMI_MOMENTARY | YES | NO | NO | 861113 | 128809 | 116052 | 6294 | 3008 | 0 | 0.003492 | 0 | 1 | 0 | Feeder | PIEDMONT_2164 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009464 |  | METRO WEST | WEST | 8321:PIEDMONT | PIEDMONT_2162 | 832162 | 2020-01-25 11:26 | 2020-01-25 11:26 | 0 | 1630 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | PIEDMONT | 2401 WASHINGTON AVE NE | CMI_MOMENTARY | YES | NO | NO | 861113 | 128809 | 116052 | 6294 | 1630 | 0 | 0.0018929 | 0 | 1 | 0 | Feeder | PIEDMONT_2162 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009471 |  | METRO EAST | SEMINOLE | 7321:LETHA | LETHA_2122 | 732122 | 2020-01-25 11:32 | 2020-01-25 19:02 | 449.35 | 1 | 1 | 120.3 | 12 | POOR CONNECTION | 17 | JUMPER | SEMINOLE | 3.5W MAUDY.1S.9W NS | CMI_NORMAL | NO | NO | NO | 861113 | 114380 | 13607 | 1262 | 833 | 0.0001397 | 1.1613e-06 | 120.3 | 1 | 310 | Load | 15740 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-25 | 2020 |  | #N/A
J2001.009470 | PD-01252020-00035 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5024 | 865024 | 2020-01-25 11:33 | 2020-01-25 14:32 | 179.25 | 2 | 2 | 317.0833 | 12 | POOR CONNECTION | 17 | JUMPER | MIDWEST CITY | 535 E.GRUMAN DR | CMI_NORMAL | NO | NO | NO | 861113 | 114380 | 71194 | 8629 | 1075 | 0.00036822 | 2.3226e-06 | 158.5417 | 1 | 310 | Secondary | 7168 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | OK - 2022
J2001.009476 | PD-01252020-00040 | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1723 | 911723 | 2020-01-25 11:41 | 2020-01-25 12:57 | 75.73 | 1 | 2 | 71.8 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | BARLING | 2205 MOODY RD | CMI_NORMAL | NO | NO | NO | 861113 | 82221 | 61188 | 4242 | 1625 | 8.338e-05 | 1.1613e-06 | 71.8 | 1 | 310 | Customer | 9571 | Load | Tran1phOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-01-25 | 2020 |  | #N/A
J2001.009477 | PD-01252020-00039 | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1724 | 911724 | 2020-01-25 11:41 | 2020-01-25 13:01 | 79.73 | 2 | 3 | 143.5833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | BARLING | 2202.5 MOODY RD | CMI_NORMAL | NO | NO | NO | 861113 | 82221 | 61188 | 4242 | 611 | 0.00016674 | 2.3226e-06 | 71.7917 | 1 | 310 | Load | 12658 | Load | Tran1phOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-01-25 | 2020 |  | #N/A
J2001.009480 | PD-01252020-00036 | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2223 | 882223 | 2020-01-25 11:59 | 2020-01-25 17:21 | 322.33 | 1 | 1 | 316 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | EDMOND | 2000 E.TIMBERWOLF | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 168207 | 19821 | 5386 | 1202 | 0.00036697 | 1.1613e-06 | 316 | 1 | 310 | Customer | 45183 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009481 | PD-01252020-00041 | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2131 | 332131 | 2020-01-25 12:12 | 2020-01-25 14:13 | 121.2 | 1 | 1 | 93.7923 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKAY | OKAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 74036 | 33270 | 3336 | 1174 | 0.00010892 | 1.1613e-06 | 93.7923 | 1 | 310 | Customer | 3412 | Load | TranOpenDelta | JOSH CHENEY | 918-619-3590 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-25 | 2020 |  | #N/A
J2001.009482 | PD-01252020-00042 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-01-25 12:13 | 2020-01-25 16:05 | 232.32 | 1 | 1 | 232.3167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1225 W.HEFNER RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168207 | 148386 | 8788 | 1952 | 0.00026979 | 1.1613e-06 | 232.3167 | 1 | 310 | Customer | 35733 | Load | Tran1phPad | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | OK - 2021
J2001.009484 | PD-01252020-00045 | NORTHEAST | MUSKOGEE | 3316:WARNER | WARNER_1621 | 331621 | 2020-01-25 12:16 | 2020-01-25 13:58 | 101.73 | 1 | 1 | 101.7333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | WARNER | 1MI N WARNER SUB ON ES HWY 64 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 74036 | 33270 | 882 | 423 | 0.00011814 | 1.1613e-06 | 101.7333 | 1 | 310 | Load | 362 | Load | Tran1phOH | JAMES MCDONALD | 405-361-7186 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-25 | 2020 |  | #N/A
J2001.009489 | PD-01252020-00046 | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 22 | 570822 | 2020-01-25 12:25 | 2020-01-25 13:57 | 91.63 | 1 | 2 | 85.15 | 13 | PREMATURE FAILURE | 47 | ARRESTOR OH | DAVIS | .5N DAVIS ON HWY77 | CMI_NORMAL | NO | NO | NO | 861113 | 77609 | 6814 | 1859 | 955 | 9.8884e-05 | 1.1613e-06 | 85.15 | 1 | 310 | Load | 3124 | Load | Tran1phOH | GARRID H BROWN | 405-207-3948 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-25 | 2020 |  | OK - 2021
J2001.009495 |  | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_623 | 870623 | 2020-01-25 12:43 | 2020-01-25 15:04 | 140.87 | 5 | 4 | 185.8333 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 1429 AVONDALE DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 159125 | 56971 | 7367 | 1900 | 0.00021581 | 5.8064e-06 | 37.1667 | 1 | 310 | Load | 46526 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | OK - 2021
J2001.009491 |  | METRO EAST | SEMINOLE | 7321:LETHA | LETHA_2122 | 732122 | 2020-01-25 12:49 | 2020-01-25 19:04 | 374.62 | 26 | 10 | 1171.7333 | 29 | TREES : GROW IN | 17 | JUMPER | SEMINOLE | 4MW MAUD "Y" ON HWY 59 | CMI_NORMAL | NO | NO | NO | 861113 | 114380 | 13607 | 1262 | 833 | 0.0013607 | 3.0193e-05 | 45.0667 | 1 | 310 | Mainline | 6846 | Recloser | Rec3phHydralic | Crew | [6 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-25 | 2020 |  | #N/A
J2001.009592 |  | METRO WEST | WEST | 8342:BRADEN PARK | BRADEN_PARK_4223 | 834223 | 2020-01-25 12:56 | 2020-01-25 14:28 | 92 | 1 | 0 | 92 | 15 | SQUIRREL | 5 | SWITCH - AIR | OKLAHOMA CITY | 7103 NW 133 | CMI_NORMAL | NO | NO | NO | 861113 | 128809 | 116052 | 3401 | 1783 | 0.00010684 | 1.1613e-06 | 92 | 1 | 0 | Load | BRADN PK_4223 | Recloser | SubRecloser | Cancel | [6 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | OK - 2022
J2001.009493 | PD-01252020-00049 | METRO WEST | WEST | 8342:BRADEN PARK | BRADEN_PARK_4223 | 834223 | 2020-01-25 12:57 | 2020-01-25 16:04 | 187.58 | 1806 | 579 | 202627.0667 | 15 | SQUIRREL | 5 | SWITCH - AIR | OKLAHOMA CITY | 7103 NW 133 | CMI_NORMAL | NO | NO | NO | 861113 | 128809 | 116052 | 3401 | 1783 | 0.23531 | 0.0020973 | 112.1966 | 1 | 310 | Feeder | BRADN PK_4223 | Recloser | SubRecloser | KAEL GUTHERY | 405-428-1818 | [5 empty] | Animals | N | SUBSTATION | 138kV | 2020-01-25 | 2020 |  | OK - 2022
J2001.009526 |  | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5223 | 835223 | 2020-01-25 12:57 | 2020-01-25 16:54 | 236.98 | 22 | 23 | 2430.75 | 15 | SQUIRREL | 5 | SWITCH - AIR | OKLAHOMA CITY | 5521 NW 130th St | CMI_NORMAL | NO | NO | NO | 861113 | 168207 | 148386 | 6517 | 868 | 0.0028228 | 2.5548e-05 | 110.4886 | 1 | 310 | Customer | 304375 | Load | Tran1phPad | Wrong Circuit | [6 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009511 | PD-01252020-00056 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5024 | 865024 | 2020-01-25 13:17 | 2020-01-25 14:26 | 69.12 | 10 | 13 | 479.3333 | 1 | CANCELLED | 57 | CANCELLED | MIDWEST CITY | 535 E.GRUMAN DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 114380 | 71194 | 8629 | 1075 | 0.00055664 | 1.1613e-05 | 47.9333 | 1 | 310 | Load | 7168 | Load | Tran1phOH | STEPHEN R MEADOWS | 405-641-5657 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | OK - 2022
J2001.009513 |  | SOUTHERN | SULPHUR | 5709:PRICES FALLS | PRICES_FALLS_923 | 570923 | 2020-01-25 13:27 | 2020-01-25 13:27 | 0.03 | 183 | 0 | 6.1 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | DAVIS | 5175 KAY STARR TRAIL | CMI_MOMENTARY | YES | NO | NO | 861113 | 77609 | 6814 | 373 | 183 | 7.0839e-06 | 0.00021252 | 0.033333 | 1 | 0 | Feeder | PRIC FAL_923 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009520 | PD-01252020-00057 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_771 | 870771 | 2020-01-25 13:45 | 2020-01-25 14:53 | 68.37 | 1 | 2 | 13.603 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | NOBLE | 506 CRESTDALE LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 159125 | 56971 | 11832 | 1815 | 1.5797e-05 | 1.1613e-06 | 13.603 | 1 | 320 | Customer | 39525 | Load | Tran1phOH | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009531 | PD-01252020-00063 | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5621 | 865621 | 2020-01-25 14:18 | 2020-01-25 15:30 | 71.75 | 1 | 1 | 71.75 | 27 | TREE:NON PREVENTABLE | 31 | CONDUCTOR SERVICE - OH | VALLEY BROOK | 1616 SE.61 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 159125 | 102154 | 2754 | 538 | 8.3322e-05 | 1.1613e-06 | 71.75 | 1 | 310 | Customer | 54250 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009542 | PD-01252020-00067 | METRO WEST | WEST | 8321:PIEDMONT | PIEDMONT_2164 | 832164 | 2020-01-25 14:48 | 2020-01-25 17:25 | 156.57 | 1 | 1 | 156.5667 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | Lot 4 Block 10 Sw Corner of Siloa AAv and NW 158th st | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 128809 | 116052 | 6294 | 3008 | 0.00018182 | 1.1613e-06 | 156.5667 | 1 | 310 | Customer | 370510 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009549 |  | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_623 | 410623 | 2020-01-25 15:30 | 2020-01-25 16:30 | 60.33 | 1 | 1 | 60.3333 | 1 | CANCELLED | 57 | CANCELLED | ENID | 715 QUAPAW | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 53540 | 37597 | 6016 | 1546 | 7.0064e-05 | 1.1613e-06 | 60.3333 | 1 | 310 | Customer | 7560 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-25 | 2020 |  | #N/A
J2001.009552 | PD-01252020-00069 | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2729 | 872729 | 2020-01-25 15:37 | 2020-01-25 18:48 | 190.8 | 1 | 2 | 173.0167 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | NORMAN | 3411 MOUNT MITCHELL LN | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 159125 | 56971 | 6464 | 1265 | 0.00020092 | 1.1613e-06 | 173.0167 | 1 | 310 | Customer | 362656 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009556 | PD-01252020-00072 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4823 | 824823 | 2020-01-25 15:40 | 2020-01-25 20:21 | 280.93 | 15 | 16 | 3851.5 | 3 | DAMAGED BY PUBLIC | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 3119 SW.18 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168207 | 148386 | 4194 | 1796 | 0.0044727 | 1.7419e-05 | 256.7667 | 1 | 311 | Load | 2000 | Load | Tran1phOH | COLBY T LLOYD | 405-312-0110 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | OK - 2021
J2001.009553 | PD-01252020-00071 | METRO EAST | SEMINOLE | 7208:CYPRESS | CYPRESS_822 | 720822 | 2020-01-25 15:42 | 2020-01-25 17:53 | 131.5 | 1 | 1 | 103.3833 | 22 | WIND | 31 | CONDUCTOR SERVICE - OH | HOLDENVILLE | 218 N.WALNUT | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 114380 | 13607 | 2520 | 1431 | 0.00012006 | 1.1613e-06 | 103.3833 | 1 | 310 | Customer | 14659 | Load | Tran1phOH | KEVIN M RICH | 405-802-2121 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-25 | 2020 |  | OK - 2020
J2001.009562 | PD-01252020-00076 | METRO SOUTH | SOUTH CENTRAL | 8194:WESTMOORE | WESTMOORE_9422 | 819422 | 2020-01-25 16:11 | 2020-01-25 22:19 | 368.25 | 1 | 2 | 362.2833 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | LT 79 BK 4 KINGSRIDGE SEC 2 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 159125 | 102154 | 8102 | 1014 | 0.00042072 | 1.1613e-06 | 362.2833 | 1 | 310 | Customer | 74813 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009606 |  | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4823 | 824823 | 2020-01-25 16:32 | 2020-01-25 20:20 | 228.55 | 17 | 20 | 3363.45 | 3 | DAMAGED BY PUBLIC | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 3145 SW.18 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168207 | 148386 | 4194 | 1796 | 0.0039059 | 1.9742e-05 | 197.85 | 1 | 310 | Load | 36188 | Load | Tran1phOH | Crew | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | OK - 2021
J2001.009575 | PD-01252020-00094 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2123 | 822123 | 2020-01-25 17:00 | 2020-01-25 17:54 | 54.5 | 1 | 1 | 54.5 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1301 N.DREXEL | CMI_NORMAL | NO | NO | NO | 861113 | 168207 | 148386 | 9250 | 1667 | 6.329e-05 | 1.1613e-06 | 54.5 | 1 | 310 | Load | 85560 | Load | Tran3phWye | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | OK - 2020
J2001.009578 | PD-01252020-00095 | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2721 | 872721 | 2020-01-25 17:11 | 2020-01-25 19:59 | 167.63 | 1 | 1 | 167.6333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | NORMAN | 405 MIMOSA DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 159125 | 56971 | 6464 | 934 | 0.00019467 | 1.1613e-06 | 167.6333 | 1 | 310 | Customer | 54039 | Load | Tran1phOH | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009586 | PD-01252020-00100 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7022 | 817022 | 2020-01-25 17:32 | 2020-01-25 20:01 | 149.1 | 1 | 1 | 147.9167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MOORE | 2500 NOTTINGHAM WY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 159125 | 102154 | 9938 | 2104 | 0.00017177 | 1.1613e-06 | 147.9167 | 1 | 310 | Customer | 20664 | Load | Tran1phOH | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009588 | PD-01252020-00101 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1221 | 831221 | 2020-01-25 17:34 | 2020-01-25 18:35 | 60.78 | 50 | 23 | 2960 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | NW.65 + MILLER | CMI_NORMAL | NO | NO | NO | 861113 | 168207 | 148386 | 7745 | 989 | 0.0034374 | 5.8064e-05 | 59.2 | 1 | 310 | Tap | 21858 | Fuse | FuseOH | CAMERON PITTS | 405-537-6633 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | OK - 2022
J2001.009589 | PD-01252020-00103 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2023 | 822023 | 2020-01-25 17:43 | 2020-01-25 19:08 | 85.07 | 2 | 2 | 165.7667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 3116 NW.26 | CMI_NORMAL | NO | NO | NO | 861113 | 168207 | 148386 | 6038 | 1028 | 0.0001925 | 2.3226e-06 | 82.8833 | 1 | 310 | Secondary | 27538 | Load | Tran1phOH | CAMERON PITTS | 405-537-6633 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-25 | 2020 |  | OK - 2022
J2001.009605 | PD-01252020-00107 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_771 | 870771 | 2020-01-25 18:58 | 2020-01-25 20:49 | 111.47 | 1 | 1 | 111.4667 | 13 | PREMATURE FAILURE | 15 | METER - SECONDARY | NOBLE | 506 CRESTDALE LN | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 159135 | 56974 | 11832 | 1815 | 0.00012944 | 1.1613e-06 | 111.4667 | 1 | 320 | Customer | 39525 | Load | Tran1phOH | MARK A PALMORE | 405-512-1933 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | #N/A
J2001.009619 |  | NORTHWEST | ALVA | 4528:SALINE | SALINE 23 | 452823 | 2020-01-25 20:04 | 2020-01-25 20:21 | 17.2 | 1 | 1 | 17.2 | 1 | CANCELLED | 57 | CANCELLED | HELENA | Crabtree Correctional Center Helena | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 53545 | 5520 | 668 | 318 | 1.9974e-05 | 1.1613e-06 | 17.2 | 1 | 320 | Load | 317113 | Load | Tran3phPadWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-25 | 2020 |  | #N/A
J2001.009620 |  | ARKANSAS | POTEAU | 3516:TARBY | TARBY_1625 | 351625 | 2020-01-25 20:08 | 2020-01-25 22:14 | 125.75 | 38 | 10 | 4468.8 | 5 | ELECTRICAL TRACKING | 27 | CUTOUT | POTEAU | 1/2MN/COGGINS ON HW271 | CMI_PLANNED | YES | NO | NO | 861113 | 82225 | 13488 | 1676 | 1196 | 0.0051896 | 4.4129e-05 | 117.6 | 1 | 310 | Mainline | 27796 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-25 | 2020 |  | #N/A
J2001.009625 | PD-01252020-00119 | METRO SOUTH | SOUTH | 8714:LITTLE AXE | LITTLE_AXE_1421 | 871421 | 2020-01-25 20:30 | 2020-01-25 23:00 | 149.97 | 257 | 161 | 30484.4833 | 3 | DAMAGED BY PUBLIC | 37 | CONDUCTOR PRIMARY - OH | NORMAN | N OF LITTLE AXE SUBSTATION | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 159135 | 56974 | 616 | 616 | 0.035401 | 0.00029845 | 118.6167 | 1 | 310 | Mainline | 1421 | Recloser | Rec3phHydralic | COLBY T LLOYD | 405-312-0110 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-25 | 2020 |  | #N/A
J2001.009629 |  | METRO SOUTH | SOUTH | 8714:LITTLE AXE | LITTLE_AXE_1421 | 871421 | 2020-01-25 20:37 | 2020-01-25 23:34 | 177.17 | 2 | 2 | 222.6833 | 3 | DAMAGED BY PUBLIC | 26 | DOWN GUY | NORMAN | 1200 DON RAY RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 159135 | 56974 | 616 | 616 | 0.0002586 | 2.3226e-06 | 111.3417 | 1 | 310 | Customer | 143500 | Load | Tran1phOH | Crew | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-25 | 2020 |  | #N/A
J2001.009635 | PD-01252020-00123 | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2923 | 812923 | 2020-01-25 21:20 | 2020-01-25 23:06 | 106.45 | 1 | 2 | 98.8 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 3130 SW.64 | CMI_NORMAL | NO | NO | NO | 861113 | 159135 | 102161 | 6385 | 1636 | 0.00011474 | 1.1613e-06 | 98.8 | 1 | 320 | Customer | 11969 | Load | Tran1phOH | STEVEN GILES | 405-227-2802 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-25 | 2020 |  | #N/A
J2001.009637 | PD-01252020-00125 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-01-25 21:26 | 2020-01-25 23:40 | 134.27 | 10 | 15 | 1321 | 4 | DETERIORATION | 21 | FUSE - TRANSFORMER | DEL CITY | 4624 SE.26 | CMI_NORMAL | NO | NO | NO | 861113 | 159135 | 102161 | 7416 | 2238 | 0.0015341 | 1.1613e-05 | 132.1 | 1 | 310 | Load | 6047 | Load | Tran1phOH | STEVEN GILES | 405-227-2802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | OK - 2022
J2001.009639 |  | ARKANSAS | POTEAU | 3516:TARBY | TARBY_1625 | 351625 | 2020-01-25 21:51 | 2020-01-25 22:08 | 16.38 | 550 | 121 | 8185.8333 | 5 | ELECTRICAL TRACKING | 27 | CUTOUT | SHADY POINT | 21081 280TH ST | CMI_NORMAL | NO | NO | NO | 861113 | 82225 | 13488 | 1676 | 1196 | 0.0095061 | 0.00063871 | 14.8833 | 1 | 310 | Mainline | 9777 | Recloser | Rec3phHydralic | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-25 | 2020 |  | #N/A
J2001.009640 |  | ARKANSAS | POTEAU | 3516:TARBY | TARBY_1625 | 351625 | 2020-01-25 21:55 | 2020-01-25 22:12 | 16.53 | 1 | 1 | 10.5167 | 4 | DETERIORATION | 27 | CUTOUT | POTEAU | 3/4MW HY 271 SS RD | CMI_NORMAL | NO | NO | NO | 861113 | 82225 | 13488 | 1676 | 1196 | 1.2213e-05 | 1.1613e-06 | 10.5167 | 1 | 310 | Load | 2840 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-25 | 2020 |  | #N/A
J2001.009641 |  | ARKANSAS | POTEAU | 3516:TARBY | TARBY_1625 | 351625 | 2020-01-25 22:04 | 2020-01-25 22:19 | 14.4 | 1 | 1 | 14.4 | 5 | ELECTRICAL TRACKING | 27 | CUTOUT | SHADY POINT | 500 W-HWY 271 ON COGGINS RD | CMI_NORMAL | NO | NO | NO | 861113 | 82225 | 13488 | 1676 | 1196 | 1.6723e-05 | 1.1613e-06 | 14.4 | 1 | 310 | Customer | 60002 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-25 | 2020 |  | #N/A
J2001.009650 | PD-01252020-00127 | NORTHWEST | ENID | 4353:OTTER | OTTER_5342 | 435342 | 2020-01-25 23:50 | 2020-01-26 03:01 | 190.88 | 147 | 39 | 28309.75 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | LUCIEN | 1W LUCIEN ON HWY 164 | CMI_NORMAL | NO | NO | NO | 861113 | 53545 | 37600 | 962 | 169 | 0.032876 | 0.00017071 | 192.5833 | 1 | 310 | Mainline | 203215 | Fuse | FuseOH | BRIAN L KAISER | 580-402.4510 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-25 | 2020 |  | OK - 2022
J2001.009666 | PD-01262020-00002 | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_721 | 510721 | 2020-01-26 00:30 | 2020-01-26 01:44 | 74.15 | 1 | 1 | 70.2667 | 12 | POOR CONNECTION | 50 | CONNECTOR | ARDMORE | 1410 9 NW. | CMI_NORMAL | NO | NO | NO | 861113 | 77613 | 23588 | 4509 | 684 | 8.16e-05 | 1.1613e-06 | 70.2667 | 1 | 320 | Customer | 8307 | Load | Tran1phOH | RANDAL G CALLAWAY | 580-220-8449 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-26 | 2020 |  | #N/A
J2001.009677 |  | METRO SOUTH | SOUTH | 8728:CHERRY CREEK | CHERRY_CREEK_2823 | 872823 | 2020-01-26 02:26 | 2020-01-26 04:24 | 117.8 | 20 | 17 | 2007.6667 | 28 | OTHER (DESCRIBE) | 1 | TRANSFORMER UG | NORMAN | INTERSTATE DR + CROSSROADS BL | CMI_PLANNED | YES | NO | NO | 861113 | 159135 | 56974 | 7104 | 1298 | 0.0023315 | 2.3226e-05 | 100.3833 | 1 | 308 | Load | 78618 | Load | Tran3phPadWye | Crew | [6 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | #N/A
J2001.009681 | PD-01262020-00007 | NORTHWEST | ENID | 4353:OTTER | OTTER_5342 | 435342 | 2020-01-26 03:26 | 2020-01-26 17:50 | 864.48 | 127 | 39 | 103320.85 | 4 | DETERIORATION | 11 | REGULATOR | LUCIEN | .25Mile west of HWY 164 and Champlin Rd. | CMI_NORMAL | NO | NO | NO | 861113 | 53545 | 37600 | 962 | 169 | 0.11999 | 0.00014748 | 813.55 | 1 | 310 | Mainline | 315661 | Fuse | FuseRiser | BRIAN L KAISER | 580-402.4510 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | OK - 2022
J2001.009686 |  | NORTHWEST | ENID | 4353:OTTER | OTTER_5342 | 435342 | 2020-01-26 03:44 | 2020-01-26 17:08 | 803.68 | 1 | 6 | 794.6 | 4 | DETERIORATION | 11 | REGULATOR | LUCIEN | LUCIEN STA.-1BLK N,1 SPAN W. | CMI_NORMAL | NO | NO | NO | 861113 | 53545 | 37600 | 962 | 169 | 0.00092276 | 1.1613e-06 | 794.6 | 1 | 310 | Customer | 13722 | Load | Tran1phOH | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | OK - 2022
J2001.009712 | PD-01262020-00010 | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6223 | 866223 | 2020-01-26 08:10 | 2020-01-26 09:16 | 65.55 | 1 | 2 | 59.95 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MIDWEST CITY | 11241 Roefan Rd. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 114385 | 71195 | 7210 | 2235 | 6.9619e-05 | 1.1613e-06 | 59.95 | 1 | 320 | Customer | 370189 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | #N/A
J2001.009723 | PD-01262020-00012 | NORTHEAST | MUSKOGEE | 3109:HONOR HEIGHTS | HONOR_HEIGHTS_921 | 310921 | 2020-01-26 09:18 | 2020-01-26 10:59 | 100.8 | 8 | 8 | 794.6667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MUSKOGEE | 4405 FONDULAC | CMI_NORMAL | NO | NO | NO | 861113 | 74040 | 33269 | 1178 | 1156 | 0.00092284 | 9.2903e-06 | 99.3333 | 1 | 310 | Load | 8571 | Load | Tran1phOH | JOSH CHENEY | 918-619-3590 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-26 | 2020 |  | OK - 2020
J2001.009726 | PD-01262020-00014 | NORTHEAST | SAPULPA | 3213:BOWDEN | BOWDEN_1329 | 321329 | 2020-01-26 09:34 | 2020-01-26 12:02 | 147.97 | 1 | 2 | 141.3 | 4 | DETERIORATION | 50 | CONNECTOR | SAPULPA | 1501 N.9 19 | CMI_NORMAL | NO | NO | NO | 861113 | 74040 | 40771 | 3373 | 1517 | 0.00016409 | 1.1613e-06 | 141.3 | 1 | 310 | Customer | 46515 | Load | Tran1phOH | JOSHUA N MCKINNEY | 918-863-6313 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | OK - 2020
J2001.009727 | PD-01262020-00013 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3627 | 833627 | 2020-01-26 09:48 | 2020-01-26 14:12 | 263.52 | 1 | 1 | 263.5167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2204 NW.118 TR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 8788 | 1494 | 0.00030602 | 1.1613e-06 | 263.5167 | 1 | 310 | Customer | 10457 | Load | Tran1phPad | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | #N/A
J2001.009734 | PD-01262020-00018 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2123 | 822123 | 2020-01-26 09:56 | 2020-01-26 10:56 | 60.18 | 1 | 2 | 60.1833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3815 NW.15 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 9252 | 1667 | 6.989e-05 | 1.1613e-06 | 60.1833 | 1 | 310 | Customer | 3768 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | OK - 2020
J2001.009728 | PD-01262020-00015 | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5221 | 835221 | 2020-01-26 09:56 | 2020-01-26 19:52 | 596.18 | 102 | 128 | 60333 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | SE.COR-NW.122+PONY RD | CMI_NORMAL | NO | NO | NO | 861113 | 168221 | 148400 | 6517 | 1500 | 0.070064 | 0.00011845 | 591.5 | 1 | 310 | Mainline | 20704 | Fuse | FuseRiser | SHAWN HILL | 405-308-1695 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | #N/A
J2001.009735 | PD-01262020-00016 | NORTHWEST | ALVA | 4528:SALINE | SALINE 23 | 452823 | 2020-01-26 10:27 | 2020-01-26 12:51 | 144.22 | 1 | 1 | 144.2167 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | HELENA | Crabtree Correctional Center Helena | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 53545 | 5520 | 668 | 318 | 0.00016748 | 1.1613e-06 | 144.2167 | 1 | 320 | Load | 317113 | Load | Tran3phPadWye | RANDY D MASON | 580-977-8823 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-26 | 2020 |  | #N/A
J2001.009737 | PD-01262020-00017 | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_429 | 580429 | 2020-01-26 10:33 | 2020-01-26 11:46 | 72.83 | 3 | 2 | 200 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ADA | 2019 WOODLAND DR | CMI_NORMAL | NO | NO | NO | 861113 | 77613 | 11515 | 3414 | 1343 | 0.00023226 | 3.4839e-06 | 66.6667 | 1 | 310 | Load | 17136 | Load | Tran1phOH | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | OK - 2021
J2001.009742 | PD-01262020-00021 | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5224 | 835224 | 2020-01-26 11:05 | 2020-01-26 15:34 | 268.75 | 21 | 15 | 4033.05 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | 12913 River Oaks | CMI_NORMAL | NO | NO | NO | 861113 | 168221 | 148400 | 6517 | 869 | 0.0046835 | 2.4387e-05 | 192.05 | 1 | 310 | Mainline | 360601 | Fuse | FuseRiser | BAD ORDER PRIMARY RES COORD | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | #N/A
J2001.009743 | PD-01262020-00020 | ARKANSAS | POTEAU | 3607:ROLAND ROAD | ROLAND_RD_721 | 360721 | 2020-01-26 11:08 | 2020-01-26 13:37 | 148.88 | 1 | 1 | 136.7833 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 23 | FUSE - PRIMARY | MOFFETT | 1 MI NORTH HWY 64 ON 64D | CMI_NORMAL | NO | NO | NO | 861113 | 82225 | 13488 | 1139 | 1139 | 0.00015884 | 1.1613e-06 | 136.7833 | 1 | 310 | Load | 417200 | Load | Tran1phOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-26 | 2020 |  | #N/A
J2001.009747 | PD-01262020-00019 | METRO EAST | SEMINOLE | 7208:CYPRESS | CYPRESS_821 | 720821 | 2020-01-26 11:13 | 2020-01-26 14:11 | 177.85 | 1 | 1 | 177.85 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | HOLDENVILLE | 6OO S HINCKLEYY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 114385 | 13609 | 2520 | 1089 | 0.00020654 | 1.1613e-06 | 177.85 | 1 | 320 | Customer | 7369 | Load | Tran1phOH | KEVIN M RICH | 405-802-2121 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-26 | 2020 |  | #N/A
J2001.009757 | PD-01262020-00026 | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1223 | 911223 | 2020-01-26 11:55 | 2020-01-26 14:29 | 153.63 | 4 | 5 | 157.6667 | 12 | POOR CONNECTION | 50 | CONNECTOR | FORT SMITH | 3502 PARK AV | CMI_NORMAL | NO | NO | NO | 861113 | 82225 | 61191 | 6599 | 1768 | 0.0001831 | 4.6452e-06 | 39.4167 | 1 | 310 | Secondary | 5454 | Load | Tran1phOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-26 | 2020 |  | Ark - Series 1
J2001.009758 | PD-01262020-00024 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2221 | 832221 | 2020-01-26 12:10 | 2020-01-26 14:10 | 119.98 | 1 | 1 | 119.9833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3225 NW.45 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 9174 | 1658 | 0.00013934 | 1.1613e-06 | 119.9833 | 1 | 310 | Customer | 15169 | Load | Tran1phOH | CAMERON PITTS | 405-537-6633 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-26 | 2020 |  | OK - 2022
J2001.009759 | PD-01262020-00025 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3629 | 833629 | 2020-01-26 12:14 | 2020-01-26 13:11 | 57.47 | 9 | 13 | 499.65 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | THE VILLAGE | 1917 HASLEY DR | CMI_NORMAL | NO | NO | NO | 861113 | 168221 | 148400 | 8788 | 1397 | 0.00058024 | 1.0452e-05 | 55.5167 | 1 | 310 | Load | 8225 | Load | Tran1phOH | CAMERON PITTS | 405-537-6633 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | #N/A
J2001.009760 |  | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9862 | 839862 | 2020-01-26 12:16 | 2020-01-26 12:20 | 4.15 | 1 | 1 | 4.15 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 15501 N PENN | CMI_MOMENTARY | YES | NO | NO | 861113 | 168221 | 148400 | 10660 | 2316 | 4.8193e-06 | 1.1613e-06 | 4.15 | 1 | 310 | Customer | 389322 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | #N/A
J2001.009767 | PD-01262020-00036 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3925 | 833925 | 2020-01-26 12:39 | 2020-01-26 15:47 | 187.87 | 1 | 3 | 177.6833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | WARR ACRES | 6117 NW.57 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 7852 | 2183 | 0.00020634 | 1.1613e-06 | 177.6833 | 1 | 310 | Customer | 12346 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | OK - 2022
J2001.009772 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5121 | 815121 | 2020-01-26 13:28 | 2020-01-26 13:28 | 0 | 1997 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 8101 S PENNSYLVANIA AVE | CMI_MOMENTARY | YES | NO | NO | 861113 | 159135 | 102161 | 13933 | 1997 | 0 | 0.0023191 | 0 | 1 | 0 | Feeder | PENNSYLV_5121 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-26 | 2020 |  | #N/A
J2001.009775 | PD-01262020-00037 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2263 | 852263 | 2020-01-26 13:31 | 2020-01-26 16:07 | 156.32 | 1 | 1 | 156.3167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 15000 LOPP LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 114385 | 71195 | 11633 | 1534 | 0.00018153 | 1.1613e-06 | 156.3167 | 1 | 320 | Load | 37837 | Load | Tran1phOH | CAMERON PITTS | 405-537-6633 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | OK - 2021
J2001.009780 | PD-01262020-00044 | NORTHWEST | ENID | 4240:DEER CREEK | DEER CREEK 46 | 424046 | 2020-01-26 13:50 | 2020-01-26 18:11 | 261.65 | 68 | 7 | 6902 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | NARDIN | NE COR-DEER CR-HWY 11 | CMI_NORMAL | NO | NO | NO | 861113 | 53545 | 37600 | 621 | 145 | 0.0080152 | 7.8968e-05 | 101.5 | 1 | 310 | Mainline | 3666 | Fuse | FuseOH | PATRICK LYONS | 580-395-4171 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-26 | 2020 |  | #N/A
J2001.009781 | PD-01262020-00047 | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_623 | 410623 | 2020-01-26 14:00 | 2020-01-26 17:06 | 186.45 | 1 | 1 | 186.45 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ENID | 715 QUAPAW | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 53545 | 37600 | 6016 | 1546 | 0.00021652 | 1.1613e-06 | 186.45 | 1 | 310 | Customer | 7560 | Load | Tran1phPad | RONALD K GOSE | 580-541-3131 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-26 | 2020 |  | #N/A
J2001.009787 | PD-01262020-00048 | NORTHWEST | ENID | 4119:GLENWOOD | GLENWOOD_1922 | 411922 | 2020-01-26 14:09 | 2020-01-26 17:56 | 226.52 | 2 | 2 | 425.0333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ENID | 113 N.SADDLE RD | CMI_NORMAL | NO | NO | NO | 861113 | 53545 | 37600 | 5415 | 1561 | 0.00049359 | 2.3226e-06 | 212.5167 | 1 | 310 | Secondary | 8240 | Load | Tran1phOH | RONALD K GOSE | 580-541-3131 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | #N/A
J2001.009789 | PD-01262020-00045 | NORTHWEST | ENID | 4151:VANCE AFB | VANCE AFB 22 | 415122 | 2020-01-26 14:12 | 2020-01-26 15:17 | 65.47 | 1 | 1 | 65.4667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ENID | SOUTHGATE+HWY 81-1/2S ON ACCES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 53545 | 37600 | 357 | 356 | 7.6026e-05 | 1.1613e-06 | 65.4667 | 1 | 310 | Customer | 15 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-26 | 2020 |  | #N/A
J2001.009796 | PD-01262020-00050 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5121 | 815121 | 2020-01-26 14:38 | 2020-01-26 16:28 | 110.3 | 1 | 1 | 78.6 | 13 | PREMATURE FAILURE | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | 3100 SW.89 | CMI_NORMAL | NO | NO | NO | 861113 | 159135 | 102161 | 13933 | 1997 | 9.1277e-05 | 1.1613e-06 | 78.6 | 1 | 320 | Load | 76164 | Load | Tran3phPadWye | HOWARD GETCHELL | 530-410-8920 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | #N/A
J2001.009797 | PD-01262020-00051 | NORTHWEST | ENID | 4135:SO 4TH ST | SO_4TH_ST_3524 | 413524 | 2020-01-26 14:40 | 2020-01-26 16:12 | 91.68 | 5 | 5 | 377.0833 | 3 | DAMAGED BY PUBLIC | 31 | CONDUCTOR SERVICE - OH | ENID | 710 W.RUSH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 53545 | 37600 | 3095 | 1612 | 0.0004379 | 5.8064e-06 | 75.4167 | 1 | 310 | Secondary | 5544 | Load | TranOpenDelta | RONALD K GOSE | 580-541-3131 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | #N/A
J2001.009798 |  | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1731 | 831731 | 2020-01-26 14:43 | 2020-01-26 15:00 | 16.75 | 1 | 1 | 16.75 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 12405 INDIAN-CRK BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 6644 | 2017 | 1.9452e-05 | 1.1613e-06 | 16.75 | 1 | 310 | Customer | 31980 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | #N/A
J2001.009803 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4029 | 834029 | 2020-01-26 15:24 | 2020-01-26 15:24 | 0 | 1751 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 10135 ROCKWELL AVE | CMI_MOMENTARY | YES | NO | NO | 861113 | 128816 | 116057 | 10843 | 1146 | 0 | 0.0020334 | 0 | 1 | 0 | Feeder | SILVR LK_4029 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-26 | 2020 |  | #N/A
J2001.009806 | PD-01262020-00055 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4029 | 834029 | 2020-01-26 15:34 | 2020-01-26 16:02 | 27.85 | 1 | 1 | 24.0718 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 11001 N ROCKWELL (FOOD LION) | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 128816 | 116057 | 10843 | 1146 | 2.7954e-05 | 1.1613e-06 | 24.0718 | 1 | 310 | Load | 84778 | Load | Tran3phPadWye | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | #N/A
J2001.009805 | PD-01262020-00054 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2123 | 822123 | 2020-01-26 15:34 | 2020-01-26 17:14 | 99.8 | 1 | 1 | 99.8 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | 3815 NW.15 | CMI_NORMAL | NO | NO | NO | 861113 | 168221 | 148400 | 9252 | 1667 | 0.0001159 | 1.1613e-06 | 99.8 | 1 | 310 | Customer | 3768 | Load | Tran1phOH | CAMERON PITTS | 405-537-6633 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | OK - 2020
J2001.009815 | PD-01262020-00059 | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2924 | 812924 | 2020-01-26 16:09 | 2020-01-26 16:37 | 28.43 | 1 | 1 | 28.4333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 3105 S Madole Bl | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 159135 | 102161 | 6385 | 2129 | 3.3019e-05 | 1.1613e-06 | 28.4333 | 1 | 310 | Customer | 83170 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-26 | 2020 |  | #N/A
J2001.009817 | PD-01262020-00061 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3621 | 853621 | 2020-01-26 16:14 | 2020-01-26 17:47 | 93.2 | 1 | 1 | 91.0667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1726 NE 23rd | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 5927 | 2169 | 0.00010575 | 1.1613e-06 | 91.0667 | 1 | 310 | Customer | 415410 | Load | Tran3phPadWye | CAMERON PITTS | 405-537-6633 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | OK - 2022
J2001.009822 | PD-01262020-00069 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6335 | 816335 | 2020-01-26 16:32 | 2020-01-26 18:15 | 102.55 | 9 | 13 | 912.75 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MOORE | 620 SW.13 | CMI_NORMAL | NO | NO | NO | 861113 | 159135 | 102161 | 11834 | 1212 | 0.00106 | 1.0452e-05 | 101.4167 | 1 | 310 | Load | 19479 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | OK - 2022
J2001.009824 | PD-01262020-00079 | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_622 | 770622 | 2020-01-26 16:46 | 2020-01-26 20:17 | 210.98 | 1 | 1 | 210.9833 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | BRISTOW | 517 E 1ST | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 74040 | 40771 | 3783 | 2010 | 0.00024501 | 1.1613e-06 | 210.9833 | 1 | 310 | Customer | 42747 | Load | Tran1phOH | JOSHUA N MCKINNEY | 918-863-6313 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-26 | 2020 |  | #N/A
J2001.009827 | PD-01262020-00076 | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5824 | 845824 | 2020-01-26 16:58 | 2020-01-26 17:58 | 60.2 | 1 | 1 | 58.3833 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 11123 NE.63 | CMI_NORMAL | NO | NO | NO | 861113 | 114385 | 71195 | 2985 | 861 | 6.78e-05 | 1.1613e-06 | 58.3833 | 1 | 310 | Load | 9505 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Other | N | DISTRIBUTION | 69kV | 2020-01-26 | 2020 |  | #N/A
J2001.009828 | PD-01262020-00080 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_869 | 830869 | 2020-01-26 17:29 | 2020-01-26 19:17 | 108.08 | 1 | 2 | 92.4667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 4213 NW 148TH ST | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 19378 | 2468 | 0.00010738 | 1.1613e-06 | 92.4667 | 1 | 310 | Customer | 79209 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | #N/A
J2001.009837 | PD-01262020-00085 | METRO WEST | WEST | 8158:SARA | SARA_5871 | 815871 | 2020-01-26 18:15 | 2020-01-26 23:36 | 320.18 | 1 | 2 | 82.3 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | Break's West Add Sec 2 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 128816 | 116057 | 18250 | 5398 | 9.5574e-05 | 1.1613e-06 | 82.3 | 1 | 310 | Customer | 258795 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | OK - 2022
J2001.009844 | PD-01262020-00088 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2231 | 852231 | 2020-01-26 19:03 | 2020-01-26 20:45 | 102.25 | 1 | 2 | 95.75 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | CHOCTAW | .5MN SE 29 ES CHOC R | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 114385 | 71195 | 11633 | 1437 | 0.00011119 | 1.1613e-06 | 95.75 | 1 | 310 | Load | 26313 | Load | Tran1phOH | KYLE L GOODIN | 405-426-9802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | OK - 2021
J2001.009845 | PD-01262020-00089 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1931 | 851931 | 2020-01-26 19:12 | 2020-01-26 19:59 | 46.6 | 1 | 1 | 46.6 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SPENCER | 8509 NE.33 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 114385 | 71195 | 12444 | 980 | 5.4116e-05 | 1.1613e-06 | 46.6 | 1 | 310 | Customer | 51508 | Load | Tran1phOH | CAMERON PITTS | 405-537-6633 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | #N/A
J2001.009847 | PD-01262020-00093 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2024 | 822024 | 2020-01-26 19:23 | 2020-01-26 20:33 | 70.1 | 1 | 1 | 70.1 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2819 NW.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 6038 | 1776 | 8.1406e-05 | 1.1613e-06 | 70.1 | 1 | 310 | Customer | 13401 | Load | Tran1phOH | CAMERON PITTS | 405-537-6633 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-26 | 2020 |  | OK - 2020
J2001.009849 | PD-01262020-00095 | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5221 | 835221 | 2020-01-26 19:25 | 2020-01-26 22:40 | 195.05 | 2 | 2 | 341.4 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 4310 RANKIN RD | CMI_NORMAL | NO | NO | NO | 861113 | 168221 | 148400 | 6517 | 1500 | 0.00039646 | 2.3226e-06 | 170.7 | 1 | 310 | Secondary | 63176 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | #N/A
J2001.009850 | PD-01262020-00091 | SOUTHERN | ARDMORE | 5117:MARIETTA | MARIETTA_1721 | 511721 | 2020-01-26 19:25 | 2020-01-26 21:51 | 145.38 | 1 | 1 | 145.3833 | 12 | POOR CONNECTION | 32 | CONDUCTOR SECONDARY - UG | MARIETTA | 503 FRALEY ST - MARIETTA | CMI_NORMAL | NO | NO | NO | 861113 | 77613 | 23588 | 1595 | 638 | 0.00016883 | 1.1613e-06 | 145.3833 | 1 | 320 | Customer | 21129 | Load | Tran1phOH | JOE LOFTIS | 918-884-5349 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-26 | 2020 |  | #N/A
J2001.009853 | PD-01262020-00092 | METRO EAST | SEMINOLE | 7321:LETHA | LETHA_2122 | 732122 | 2020-01-26 19:30 | 2020-01-26 21:12 | 102.08 | 5 | 5 | 297.5 | 22 | WIND | 21 | FUSE - TRANSFORMER | SEMINOLE | 1916 LEWIS AVE | CMI_NORMAL | NO | NO | NO | 861113 | 114385 | 13609 | 1263 | 834 | 0.00034548 | 5.8064e-06 | 59.5 | 1 | 310 | Load | 3462 | Load | Tran1phOH | KEVIN M RICH | 405-802-2121 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-26 | 2020 |  | #N/A
J2001.009852 | PD-01262020-00094 | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1823 | 931823 | 2020-01-26 19:31 | 2020-01-26 20:57 | 86 | 1 | 1 | 147.3333 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | ALMA | SE CORNER CANTERBURY + FAIRFAX | CMI_NORMAL | NO | NO | NO | 861113 | 82225 | 61191 | 2836 | 1228 | 0.0001711 | 1.1613e-06 | 147.3333 | 1 | 310 | Customer | 12784 | Load | Tran1phPad | TRAVIS EARNHART | 479-462-5659 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-26 | 2020 |  | Ark - Series 2
J2001.009863 |  | METRO EAST | EAST | 8542:RENO | RENO_4229 | 854229 | 2020-01-26 21:08 | 2020-01-26 21:25 | 17.65 | 1 | 1 | 17.65 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DEL CITY | 4625 TINKER EX | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 114385 | 71195 | 5212 | 1344 | 2.0497e-05 | 1.1613e-06 | 17.65 | 1 | 310 | Customer | 40589 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | OK - 2022
J2001.009864 |  | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3023 | 743023 | 2020-01-26 21:11 | 2020-01-26 21:51 | 40.17 | 68 | 12 | 1017.1667 | 4 | DETERIORATION | 12 | POLE | BETHEL ACRES | 4MI W ON LAKE RD | CMI_PLANNED | YES | NO | NO | 861113 | 114385 | 22115 | 6647 | 1138 | 0.0011812 | 7.8968e-05 | 14.9583 | 1 | 310 | Mainline | 839 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | OK - 2021
J2001.009869 | PD-01262020-00099 | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-26 21:53 | 2020-01-27 01:14 | 201.05 | 1 | 2 | 198.9 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | MUSTANG | 717 W.FORSTER DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 128816 | 116057 | 18250 | 4429 | 0.00023098 | 1.1613e-06 | 198.9 | 1 | 320 | Customer | 58390 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-26 | 2020 |  | OK - 2022
J2001.009891 |  | ARKANSAS | POTEAU | 3516:TARBY | TARBY_1625 | 351625 | 2020-01-27 02:14 | 2020-01-27 02:42 | 27.77 | 1 | 1 | 27.7667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | POTEAU | 1/4 MI N ON TARBY RD-POTEAU | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 82225 | 13488 | 1676 | 1196 | 3.2245e-05 | 1.1613e-06 | 27.7667 | 1 | 310 | Customer | 1162 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-27 | 2020 |  | #N/A
J2001.009897 | PD-01272020-00010 | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4526 | 824526 | 2020-01-27 04:52 | 2020-01-27 09:11 | 258.52 | 1 | 1 | 258.5167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | * 3/16N NW.10 WS COUNTY LINE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 128816 | 116057 | 3409 | 823 | 0.00030021 | 1.1613e-06 | 258.5167 | 1 | 310 | Customer | 70777 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.009901 | PD-01272020-00011 | METRO EAST | EAST | 8542:RENO | RENO_4231 | 854231 | 2020-01-27 05:44 | 2020-01-27 10:02 | 258.48 | 1 | 3 | 258.4833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DEL CITY | 3901 LAWN DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 114385 | 71195 | 5212 | 958 | 0.00030017 | 1.1613e-06 | 258.4833 | 1 | 320 | Customer | 5746 | Load | Tran1phOH | REX R WILSON | 405-535-4507 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2021
J2001.009907 | PD-01272020-00020 | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5222 | 835222 | 2020-01-27 06:58 | 2020-01-27 09:20 | 142.28 | 1 | 1 | 142.2833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 3117 ROLLING-STONE RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 6517 | 1353 | 0.00016523 | 1.1613e-06 | 142.2833 | 1 | 310 | Customer | 28240 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.009908 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-27 07:04 | 2020-01-27 07:53 | 48.75 | 1 | 0 | 48.7165 | 4 | DETERIORATION | 2 | TRANSFORMER OH | 0 | GOD S RANCH RD - MT.BURG | CMI_PLANNED | YES | NO | NO | 861113 | 82225 | 61191 | 3791 | 2586 | 5.6574e-05 | 1.1613e-06 | 48.7165 | 1 | 0 | Load | 15226 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-27 | 2020 |  | Ark - Series 2
J2001.009915 | PD-01272020-00024 | METRO EAST | SHAWNEE | 7435:MISSION HILL | MISSION HILL 24 | 743524 | 2020-01-27 07:23 | 2020-01-27 14:33 | 429.58 | 1 | 1 | 429.5833 | 3 | DAMAGED BY PUBLIC | 12 | POLE | SHAWNEE | .5S HDSTY ON BEARD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 114385 | 22115 | 948 | 948 | 0.00049887 | 1.1613e-06 | 429.5833 | 1 | 310 | Customer | 14651 | Load | Tran3phPadWye | JAY E COTTMAN | 405-432-7177 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | OK - 2021
J2001.009919 | PD-01272020-00031 | METRO SOUTH | SOUTH | 8719:PLEASANT VLY | PLEASANT_VAL_1924 | 871924 | 2020-01-27 07:38 | 2020-01-27 08:40 | 61.83 | 1 | 1 | 61.8333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | 2801 VENTURE DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 159135 | 56974 | 2108 | 929 | 7.1806e-05 | 1.1613e-06 | 61.8333 | 1 | 310 | Customer | 78360 | Load | Tran3phPadWye | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.009918 | PD-01272020-00029 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4029 | 834029 | 2020-01-27 07:39 | 2020-01-27 09:55 | 135.65 | 1 | 1 | 130.75 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 11413 WARWICK PLACE DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 128816 | 116057 | 10843 | 1146 | 0.00015184 | 1.1613e-06 | 130.75 | 1 | 320 | Customer | 76619 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.009921 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-27 07:56 | 2020-01-27 09:13 | 77.58 | 1 | 1 | 49.1167 | 4 | DETERIORATION | 2 | TRANSFORMER OH | MOUNTAINBURG | RURAL | CMI_PLANNED | YES | NO | NO | 861113 | 82225 | 61191 | 3791 | 2586 | 5.7039e-05 | 1.1613e-06 | 49.1167 | 1 | 308 | Load | 12365 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-27 | 2020 |  | Ark - Series 2
J2001.009923 |  | METRO EAST | SHAWNEE | 7435:MISSION HILL | MISSION HILL 24 | 743524 | 2020-01-27 08:04 | 2020-01-27 14:45 | 400.48 | 13 | 0 | 4848.4583 | 3 | DAMAGED BY PUBLIC | 12 | POLE | SHAWNEE | E FEED INDIAN SANATRM | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 114385 | 22115 | 948 | 948 | 0.0056305 | 1.5097e-05 | 372.9583 | 1 | 0 | Mainline | 5231 | Fuse | FuseOH | Ties | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | OK - 2021
J2001.009924 |  | METRO SOUTH | SOUTH | 8726:NOBLE | NOBLE_2621 | 872621 | 2020-01-27 08:13 | 2020-01-27 08:20 | 6.88 | 1 | 1 | 6.8833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NOBLE | 8TH ST. + HWY 77 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 159135 | 56974 | 2968 | 1447 | 7.9935e-06 | 1.1613e-06 | 6.8833 | 1 | 310 | Customer | 74669 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.009925 |  | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1421 | 911421 | 2020-01-27 08:15 | 2020-01-27 10:25 | 129.78 | 6 | 0 | 778.5977 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | FORT SMITH | 3315 BIRNIE AV | CMI_PLANNED | YES | NO | NO | 861113 | 82225 | 61191 | 4737 | 1747 | 0.00090418 | 6.9677e-06 | 129.7663 | 1 | 0 | Load | 351 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-27 | 2020 |  | Ark - Series 1
J2001.009927 |  | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1421 | 911421 | 2020-01-27 08:18 | 2020-01-27 10:25 | 126.18 | 8 | 7 | 974 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | FORT SMITH | 3210 WIRSING AV,2 POLE W-N.33 | CMI_PLANNED | YES | NO | NO | 861113 | 82225 | 61191 | 4737 | 1747 | 0.0011311 | 9.2903e-06 | 121.75 | 1 | 310 | Load | 3263 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-27 | 2020 |  | Ark - Series 1
J2001.009928 | PD-01272020-00057 | NORTHWEST | ENID | 4220:CLYDE | CLYDE 23 | 422023 | 2020-01-27 08:21 | 2020-01-27 10:00 | 98.73 | 1 | 1 | 98.7333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MANCHESTER | S 1ST + E 6TH MANCHESTER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 53545 | 37600 | 414 | 373 | 0.00011466 | 1.1613e-06 | 98.7333 | 1 | 310 | Customer | 7702 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.009930 | PD-01272020-00055 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7421 | 847421 | 2020-01-27 08:23 | 2020-01-27 09:17 | 53.55 | 1 | 1 | 53.55 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4020 N.LINCOLN BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 6165 | 407 | 6.2187e-05 | 1.1613e-06 | 53.55 | 1 | 310 | Load | 49627 | Load | Tran3phPadWye | REX R WILSON | 405-535-4507 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2022
J2001.009936 | PD-01272020-00066 | METRO EAST | SHAWNEE | 7435:MISSION HILL | MISSION HILL 24 | 743524 | 2020-01-27 08:34 | 2020-01-27 09:35 | 60.7 | 1 | 1 | 60.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SHAWNEE | Father Murphy Complex Phase 3 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 114385 | 22115 | 948 | 948 | 7.049e-05 | 1.1613e-06 | 60.7 | 1 | 310 | Customer | 334260 | Load | Tran1phPad | BRYAN K TATUM | 405-659-0746 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | OK - 2021
J2001.009937 | PD-01272020-00074 | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-01-27 08:41 | 2020-01-27 11:19 | 158.07 | 1 | 1 | 150 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | MUSTANG | 309 W. APPLE BRANCH WAY | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 128816 | 116057 | 18250 | 4429 | 0.00017419 | 1.1613e-06 | 150 | 1 | 310 | Customer | 63880 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2022
J2001.009939 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-27 08:46 | 2020-01-27 09:13 | 27.53 | 7 | 0 | 186.3167 | 4 | DETERIORATION | 2 | TRANSFORMER OH | 0 | ROUTE 2, MTNBURG | CMI_PLANNED | YES | NO | NO | 861113 | 82225 | 61191 | 3791 | 2586 | 0.00021637 | 8.129e-06 | 26.6167 | 1 | 0 | Load | 2586 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-27 | 2020 |  | Ark - Series 2
J2001.009940 | PD-01272020-00086 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_869 | 830869 | 2020-01-27 08:48 | 2020-01-27 09:46 | 58.32 | 1 | 1 | 58.3167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4213 NW 148TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 19378 | 2468 | 6.7722e-05 | 1.1613e-06 | 58.3167 | 1 | 310 | Customer | 79209 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.009942 | PD-01272020-00091 | ARKANSAS | POTEAU | 3514:HEAVENER | HEAVENER 21 | 351421 | 2020-01-27 08:49 | 2020-01-27 10:02 | 73.25 | 1 | 1 | 73.25 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | HEAVENER | 6TH + ADDISON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 82225 | 13488 | 1770 | 463 | 8.5064e-05 | 1.1613e-06 | 73.25 | 1 | 310 | Customer | 5429 | Load | Tran1phOH | TOBY C MEAD | 918-658-5596 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.009941 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-27 08:49 | 2020-01-27 15:05 | 375.05 | 7 | 4 | 1438.15 | 4 | DETERIORATION | 12 | POLE | ARKOMA | POTEAU+CHEROKEE-1BLKN BLOCKER | CMI_PLANNED | YES | NO | NO | 861113 | 82225 | 61191 | 2937 | 875 | 0.0016701 | 8.129e-06 | 205.45 | 1 | 308 | Load | 1719 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-27 | 2020 |  | Ark - Series 2
J2001.009945 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1862 | 941862 | 2020-01-27 08:54 | 2020-01-27 11:26 | 152.88 | 1 | 1 | 118.95 | 4 | DETERIORATION | 12 | POLE | LAMAR | LAMAR AR 72846 | CMI_PLANNED | YES | NO | NO | 861113 | 82225 | 7546 | 730 | 730 | 0.00013814 | 1.1613e-06 | 118.95 | 1 | 308 | Load | 6886 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | Ark - Series 2
J2001.009952 | PD-01272020-00106 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_524 | 510524 | 2020-01-27 09:11 | 2020-01-27 10:52 | 101.17 | 1 | 1 | 101.1667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ARDMORE | LAKE MURRAY GOLF COURSE/LAGOON | CMI_NORMAL | NO | NO | NO | 861113 | 77613 | 23588 | 4775 | 1432 | 0.00011748 | 1.1613e-06 | 101.1667 | 1 | 310 | Customer | 28269 | Load | Tran1phPad | RANDAL G CALLAWAY | 580-220-8449 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | OK - 2021
J2001.009956 | PD-01272020-00102 | METRO WEST | WEST | 8158:SARA | SARA_5864 | 815864 | 2020-01-27 09:16 | 2020-01-27 12:36 | 200.42 | 1 | 1 | 188.9 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | MUSTANG | 329 E MOBILE TE | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 128816 | 116057 | 18250 | 4815 | 0.00021937 | 1.1613e-06 | 188.9 | 1 | 310 | Customer | 248335 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2022
J2001.009958 | PD-01272020-00110 | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_924 | 910924 | 2020-01-27 09:18 | 2020-01-27 10:17 | 59.28 | 1 | 1 | 59.2833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 1701 S.FRESNO 37 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 82225 | 61191 | 5011 | 1724 | 6.8845e-05 | 1.1613e-06 | 59.2833 | 1 | 310 | Customer | 9271 | Load | Tran1phOH | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | Ark - Series 3
J2001.009960 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4022 | 834022 | 2020-01-27 09:20 | 2020-01-27 09:20 | 0.03 | 1371 | 0 | 45.7 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 10135 ROCKWELL AVE | CMI_MOMENTARY | YES | NO | NO | 861113 | 128816 | 116057 | 10843 | 1369 | 5.3071e-05 | 0.0015921 | 0.033333 | 1 | 0 | Feeder | SILVR LK_4022 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.009965 |  | METRO EAST | SEMINOLE | 7505:WEWOKA | WEWOKA 24 | 750524 | 2020-01-27 09:33 | 2020-01-27 09:38 | 4.95 | 1 | 1 | 4.95 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | WEWOKA | 1601 SO MEKESVKEY | CMI_MOMENTARY | YES | NO | NO | 861113 | 114385 | 13609 | 2474 | 1191 | 5.7484e-06 | 1.1613e-06 | 4.95 | 1 | 310 | Customer | 2541 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | OK - 2021
J2001.009967 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-27 09:35 | 2020-01-27 12:55 | 199.58 | 4 | 2 | 789.9333 | 4 | DETERIORATION | 12 | POLE | LAVACA | 2507 BARBARA LANE LAVACA,ARK | CMI_PLANNED | YES | NO | NO | 861113 | 82225 | 61191 | 2735 | 2123 | 0.00091734 | 4.6452e-06 | 197.4833 | 1 | 308 | Load | 2406 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | Ark - Series 2
J2001.009968 | PD-01272020-00121 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1229 | 831229 | 2020-01-27 09:35 | 2020-01-27 10:19 | 43.52 | 1 | 1 | 43.5167 | 27 | TREE:NON PREVENTABLE | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 2020 NW.44 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 7752 | 787 | 5.0535e-05 | 1.1613e-06 | 43.5167 | 1 | 310 | Customer | 12359 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2022
J2001.009970 | PD-01272020-00147 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5134 | 815134 | 2020-01-27 09:41 | 2020-01-27 10:27 | 46.2 | 1 | 1 | 46.2 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1401 SW 89th | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 159135 | 102161 | 13933 | 2467 | 5.3651e-05 | 1.1613e-06 | 46.2 | 1 | 310 | Customer | 334959 | Load | Tran1phPad | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.009972 | PD-01272020-00142 | NORTHEAST | SAPULPA | 7614:KNIPE | KNIPE_1423 | 761423 | 2020-01-27 09:44 | 2020-01-27 11:34 | 109.78 | 1 | 1 | 109.7833 | 4 | DETERIORATION | 50 | CONNECTOR | PERKINS | 120 W.STUMBO | CMI_NORMAL | NO | NO | NO | 861113 | 74040 | 40771 | 1824 | 790 | 0.00012749 | 1.1613e-06 | 109.7833 | 1 | 310 | Customer | 45073 | Load | TranOH3phDelta | BRAD WRIGHT | 918-629-1747 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.009976 |  | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 21 | 570821 | 2020-01-27 09:49 | 2020-01-27 14:13 | 263.88 | 12 | 1 | 116.4888 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | DAVIS | 1003 E.ELLIS ST | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 77613 | 6812 | 1859 | 904 | 0.00013528 | 1.3935e-05 | 9.7074 | 1 | 308 | Load | 15364 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | OK - 2021
J2001.009978 | PD-01272020-00154 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5023 | 865023 | 2020-01-27 10:00 | 2020-01-27 17:28 | 447.72 | 1 | 1 | 441.45 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | MIDWEST CITY | 9200 WONGA DR | CMI_NORMAL | NO | NO | NO | 861113 | 114385 | 71195 | 8630 | 1268 | 0.00051265 | 1.1613e-06 | 441.45 | 1 | 310 | Customer | 67407 | Load | Tran1phOH | JAY E COTTMAN | 405-432-7177 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2022
J2001.009983 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-01-27 10:09 | 2020-01-27 17:26 | 436.72 | 6 | 4 | 2487.5 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | 0 | CMI_PLANNED | YES | NO | NO | 861113 | 159135 | 56974 | 4241 | 1005 | 0.0028887 | 6.9677e-06 | 414.5833 | 1 | 308 | Mainline |  | 0 | 0 | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.009985 |  | SOUTHERN | DURANT | 5504:BUTTERFIELD | BUTTERFIELD_422 | 550422 | 2020-01-27 10:14 | 2020-01-27 10:34 | 20.1 | 1 | 1 | 20.1 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DURANT | 32 BENT TREE PKW | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 77613 | 15492 | 3486 | 562 | 2.3342e-05 | 1.1613e-06 | 20.1 | 1 | 310 | Load | 371783 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.009984 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-27 10:14 | 2020-01-27 15:10 | 296.1 | 2 | 2 | 53.6667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | MOUNTAINBURG | MTNBURG AR | CMI_PLANNED | YES | NO | NO | 861113 | 82225 | 61191 | 3791 | 2586 | 6.2322e-05 | 2.3226e-06 | 26.8333 | 1 | 308 | Load | 8349 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-27 | 2020 |  | Ark - Series 2
J2001.009986 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1226 | 831226 | 2020-01-27 10:16 | 2020-01-27 11:49 | 93.45 | 8 | 0 | 223.4667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 1712 NW.42 | CMI_PLANNED | YES | NO | NO | 861113 | 168221 | 148400 | 7752 | 1747 | 0.00025951 | 9.2903e-06 | 27.9333 | 1 | 0 | Load | 9108 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2021
J2001.009988 | PD-01272020-00178 | METRO EAST | SHAWNEE | 7432:ST GREGORY | ST_GREGORY_3224 | 743224 | 2020-01-27 10:19 | 2020-01-27 11:04 | 45.5 | 1 | 1 | 45.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SHAWNEE | 809 W.39 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 114385 | 22115 | 4093 | 1372 | 5.2839e-05 | 1.1613e-06 | 45.5 | 1 | 310 | Customer | 9036 | Load | Tran1phOH | BRYAN K TATUM | 405-659-0746 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.009990 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-01-27 10:25 | 2020-01-27 10:57 | 32.48 | 1 | 0 | 19.2833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 19837 SOUTH ST | CMI_PLANNED | YES | NO | NO | 861113 | 114385 | 71195 | 11633 | 3535 | 2.2393e-05 | 1.1613e-06 | 19.2833 | 1 | 0 | Load | 71016 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.009992 | PD-01272020-00191 | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5231 | 835231 | 2020-01-27 10:27 | 2020-01-27 12:32 | 125.18 | 1 | 1 | 119.0167 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | THE VILLAGE | 3117 KERRY LN | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 6517 | 638 | 0.00013821 | 1.1613e-06 | 119.0167 | 1 | 310 | Customer | 9212 | Load | Tran1phOH | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.009997 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-01-27 10:37 | 2020-01-27 11:51 | 74.55 | 4 | 3 | 289.9333 | 4 | DETERIORATION | 28 | CROSSARM | BIXBY | 105 N.CABANISS | CMI_PLANNED | YES | NO | NO | 861113 | 74040 | 40771 | 2751 | 1440 | 0.0003367 | 4.6452e-06 | 72.4833 | 1 | 308 | Load | 47767 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | OK - 2021
J2001.010000 | PD-01272020-00203 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3925 | 833925 | 2020-01-27 10:40 | 2020-01-27 11:36 | 55.72 | 1 | 1 | 16.4395 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 5412 WILLOWCLF RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 7852 | 2183 | 1.9091e-05 | 1.1613e-06 | 16.4395 | 1 | 310 | Customer | 47743 | Load | Tran1phPad | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2022
J2001.010004 |  | SOUTHERN | DURANT | 5504:BUTTERFIELD | BUTTERFIELD_422 | 550422 | 2020-01-27 10:49 | 2020-01-27 12:26 | 96.82 | 1 | 0 | 84.9667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | DURANT | 924 RODEO RD | CMI_PLANNED | YES | NO | NO | 861113 | 77613 | 15492 | 3486 | 562 | 9.8671e-05 | 1.1613e-06 | 84.9667 | 1 | 0 | Load | 1022 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010016 |  | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2222 | 882222 | 2020-01-27 11:00 | 2020-01-27 13:04 | 124.62 | 3 | 2 | 48.65 | 4 | DETERIORATION | 2 | TRANSFORMER OH | GUTHRIE | 8100 W. Simmons rd | CMI_PLANNED | YES | NO | NO | 861113 | 168221 | 19821 | 5385 | 1160 | 5.6497e-05 | 3.4839e-06 | 16.2167 | 1 | 308 | Load | 61144 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010015 |  | SOUTHERN | DURANT | 5504:BUTTERFIELD | BUTTERFIELD_422 | 550422 | 2020-01-27 11:00 | 2020-01-27 12:52 | 111.9 | 4 | 4 | 406.3333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | DURANT | NE COR PICKELING PLA (AIRPORT) | CMI_PLANNED | YES | NO | NO | 861113 | 77613 | 15492 | 3486 | 562 | 0.00047187 | 4.6452e-06 | 101.5833 | 1 | 308 | Load | 16588 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010017 | PD-01272020-00241 | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_624 | 410624 | 2020-01-27 11:05 | 2020-01-27 12:05 | 60.3 | 1 | 1 | 60.3 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | ENID | 2126 N VAN BUREN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 53545 | 37600 | 6016 | 1862 | 7.0026e-05 | 1.1613e-06 | 60.3 | 1 | 310 | Customer | 313331 | Load | Tran3phPadWye | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010018 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1023 | 541023 | 2020-01-27 11:06 | 2020-01-27 11:06 | 0 | 843 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MADILL | 12537 HIGHWAY 199 | CMI_MOMENTARY | YES | NO | NO | 861113 | 77613 | 7199 | 2379 | 843 | 0 | 0.00097897 | 0 | 1 | 0 | Feeder | GLASSES_1023 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010019 | PD-01272020-00227 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1229 | 831229 | 2020-01-27 11:07 | 2020-01-27 13:56 | 168.98 | 1 | 2 | 158.9833 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 2020 NW.44 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 7752 | 787 | 0.00018463 | 1.1613e-06 | 158.9833 | 1 | 310 | Customer | 12359 | Load | Tran1phOH | REX R WILSON | 405-535-4507 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2022
J2001.010023 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-01-27 11:15 | 2020-01-27 16:20 | 304.95 | 1 | 1 | 259.1333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 11209 S.WESTMINSTER | CMI_PLANNED | YES | NO | NO | 861113 | 159135 | 56974 | 4241 | 1005 | 0.00030093 | 1.1613e-06 | 259.1333 | 1 | 308 | Load | 31045 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010039 | PD-01272020-00259 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-01-27 11:15 | 2020-01-27 13:28 | 132.95 | 1 | 2 | 127.7667 | 27 | TREE:NON PREVENTABLE | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 2017 NW 15 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 11126 | 2058 | 0.00014837 | 1.1613e-06 | 127.7667 | 1 | 310 | Customer | 3075 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2021
J2001.010025 | PD-01272020-00264 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2222 | 832222 | 2020-01-27 11:16 | 2020-01-27 16:14 | 297.68 | 1 | 1 | 297.6833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1812 NW.39 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 9174 | 1556 | 0.0003457 | 1.1613e-06 | 297.6833 | 1 | 320 | Customer | 69399 | Load | Tran1phPad | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | OK - 2022
J2001.010031 | PD-01272020-00249 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5022 | 865022 | 2020-01-27 11:22 | 2020-01-27 12:44 | 81.68 | 3 | 5 | 211.25 | 12 | POOR CONNECTION | 50 | CONNECTOR | MIDWEST CITY | 616 GENERAL-SENTER | CMI_NORMAL | NO | NO | NO | 861113 | 114385 | 71195 | 8630 | 1662 | 0.00024532 | 3.4839e-06 | 70.4167 | 1 | 310 | Secondary | 45823 | Load | Tran1phOH | ADAM CLARK | 580-310-8924 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2022
J2001.010030 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2231 | 852231 | 2020-01-27 11:28 | 2020-01-27 12:04 | 36.38 | 1 | 1 | 34.7667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | CHOCTAW | 3BN SE29 ES CHOC RD | CMI_PLANNED | YES | NO | NO | 861113 | 114385 | 71195 | 11633 | 1437 | 4.0374e-05 | 1.1613e-06 | 34.7667 | 1 | 308 | Load | 29736 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2021
J2001.010032 |  | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_422 | 510422 | 2020-01-27 11:28 | 2020-01-27 11:28 | 0.03 | 1057 | 0 | 35.2333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 2510 SAM NOBLE PARKWAY | CMI_MOMENTARY | YES | NO | NO | 861113 | 77613 | 23588 | 2317 | 1057 | 4.0916e-05 | 0.0012275 | 0.033333 | 1 | 0 | Feeder | FOUNDATION_422 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010036 | PD-01272020-00287 | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1721 | 911721 | 2020-01-27 11:28 | 2020-01-27 12:33 | 64.68 | 1 | 1 | 17.2167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 0 | 0 | 0 | 0 | 1.9994e-05 | 1.1613e-06 | 17.2167 | 1 | 310 | Customer |  | 0 | 0 | MARK A. SAWYER | 479-462-4457 |  |  |  |  | 06/02/2020 note from burchamc. Reference J2001.010036 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-27 | 2020 |  | #N/A
J2001.010040 | PD-01272020-00252 | ARKANSAS | FORT SMITH | 9512:ADABELL ROAD | ADABELL_ROAD_1221 | 951221 | 2020-01-27 11:31 | 2020-01-27 13:05 | 94.38 | 1 | 1 | 94.3833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | VAN BUREN | 707 VINE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 82225 | 61191 | 3122 | 1095 | 0.00010961 | 1.1613e-06 | 94.3833 | 1 | 310 | Customer | 482 | Load | Tran1phOH | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-27 | 2020 |  | Ark - Series 1
J2001.010042 | PD-01272020-00263 | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_422 | 510422 | 2020-01-27 11:32 | 2020-01-27 13:00 | 88.18 | 3 | 3 | 247.7 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | ARDMORE | 2210 OAKGLEN DR | CMI_NORMAL | NO | NO | NO | 861113 | 77613 | 23588 | 2317 | 1057 | 0.00028765 | 3.4839e-06 | 82.5667 | 1 | 310 | Secondary | 20910 | Load | Tran1phPad | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010044 | PD-01272020-00258 | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_422 | 510422 | 2020-01-27 11:34 | 2020-01-27 13:18 | 103.87 | 3 | 3 | 240.75 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | ARDMORE | OAKGLEN + WHIPPERWILL,500 S,ES | CMI_NORMAL | NO | NO | NO | 861113 | 77613 | 23588 | 2317 | 1057 | 0.00027958 | 3.4839e-06 | 80.25 | 1 | 310 | Load | 27686 | Load | Tran1phPad | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010054 | PD-01272020-00288 | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_629 | 460629 | 2020-01-27 11:42 | 2020-01-27 14:27 | 165.47 | 1 | 2 | 165.4667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | WOODWARD | 917 21ST-WOODWARD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 53545 | 10425 | 5683 | 932 | 0.00019215 | 1.1613e-06 | 165.4667 | 1 | 311 | Customer | 11076 | Load | Tran1phOH | ROY L THRASH | 580-334-5371 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010050 | PD-01272020-00282 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-01-27 11:43 | 2020-01-27 12:24 | 40.92 | 9 | 6 | 357.45 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2345 SW.46 | CMI_NORMAL | NO | NO | NO | 861113 | 159135 | 102161 | 7605 | 2460 | 0.0004151 | 1.0452e-05 | 39.7167 | 1 | 310 | Load | 22996 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010049 | PD-01272020-00286 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9923 | 829923 | 2020-01-27 11:44 | 2020-01-27 12:28 | 44.08 | 1 | 1 | 18.7091 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 820 HUNTER-HILL RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 128816 | 116057 | 9233 | 871 | 2.1727e-05 | 1.1613e-06 | 18.7091 | 1 | 310 | Customer | 22561 | Load | Tran1phOH | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010051 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5123 | 815123 | 2020-01-27 11:46 | 2020-01-27 13:49 | 122.18 | 5 | 3 | 494.1667 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | 7209 S.WINSTON WY | CMI_PLANNED | YES | NO | NO | 861113 | 159135 | 102161 | 13933 | 1323 | 0.00057387 | 5.8064e-06 | 98.8333 | 1 | 308 | Load | 25538 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010058 | PD-01272020-00294 | NORTHWEST | ENID | 4220:CLYDE | CLYDE 23 | 422023 | 2020-01-27 11:55 | 2020-01-27 13:15 | 80.02 | 1 | 1 | 80.0167 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | WAKITA | .5 N-CLYDE | CMI_NORMAL | NO | NO | NO | 861113 | 53545 | 37600 | 414 | 373 | 9.2922e-05 | 1.1613e-06 | 80.0167 | 1 | 310 | Load | 13582 | Load | TranOpenDelta | PATRICK LYONS | 580-395-4171 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010059 |  | ARKANSAS | FORT SMITH | 9126:OAK PARK | OAK_PARK_2623 | 912623 | 2020-01-27 11:56 | 2020-01-27 12:24 | 27.63 | 6 | 3 | 146.7 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | FORT SMITH | 3308 NEIS ST | CMI_PLANNED | YES | NO | NO | 861113 | 82225 | 61191 | 2285 | 1992 | 0.00017036 | 6.9677e-06 | 24.45 | 1 | 308 | Load | 2053 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-27 | 2020 |  | Ark - Series 1
J2001.010065 | PD-01272020-00304 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3222 | 813222 | 2020-01-27 12:01 | 2020-01-27 15:19 | 198.38 | 11 | 14 | 2077.7167 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 1400 SW.60 | CMI_NORMAL | NO | NO | NO | 861113 | 159135 | 102161 | 7605 | 1484 | 0.0024128 | 1.2774e-05 | 188.8833 | 1 | 310 | Load | 39794 | Load | Tran1phOH | COLBY T LLOYD | 405-312-0110 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010062 |  | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-01-27 12:03 | 2020-01-27 12:08 | 5.22 | 1 | 1 | 5.2167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1412 JOHNSTON DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 159135 | 102161 | 7605 | 2460 | 6.0581e-06 | 1.1613e-06 | 5.2167 | 1 | 310 | Customer | 8590 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010068 |  | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_721 | 590721 | 2020-01-27 12:22 | 2020-01-27 12:42 | 19.55 | 1 | 1 | 19.55 | 1 | CANCELLED | 57 | CANCELLED | MANNSVILLE | 110 S. 21ST. ST. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 77613 | 7199 | 2190 | 505 | 2.2703e-05 | 1.1613e-06 | 19.55 | 1 | 310 | Customer | 401216 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2021
J2001.010070 |  | NORTHEAST | SAPULPA | 7605:DRUMRIGHT | DRUMRIGHT_544 | 760544 | 2020-01-27 12:25 | 2020-01-27 13:57 | 91.8 | 1 | 1 | 90.4 | 4 | DETERIORATION | 12 | POLE | JENNINGS | 2BLK S .5BLK PO | CMI_PLANNED | YES | NO | NO | 861113 | 74040 | 40771 | 1694 | 1114 | 0.00010498 | 1.1613e-06 | 90.4 | 1 | 308 | Load | 43150 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010071 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-01-27 12:28 | 2020-01-27 12:34 | 6.45 | 1 | 1 | 6.45 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 16317 SE 74 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 114385 | 71195 | 11633 | 3535 | 7.4903e-06 | 1.1613e-06 | 6.45 | 1 | 310 | Load | 64327 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010079 | PD-01272020-00345 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9923 | 829923 | 2020-01-27 12:51 | 2020-01-27 13:41 | 49.93 | 1 | 1 | 49.9333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1000B S.ROCKWELL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 128816 | 116057 | 9233 | 871 | 5.7987e-05 | 1.1613e-06 | 49.9333 | 1 | 310 | Customer | 16535 | Load | Tran1phOH | GARY D FRANKLIN | 405-637-2002 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010080 | PD-01272020-00352 | METRO EAST | EAST | 8471:NE 30TH ST | NE_30TH_ST_7122 | 847122 | 2020-01-27 12:57 | 2020-01-27 14:47 | 109.97 | 1 | 1 | 109.9667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FOREST PARK | 3012 NORCREST DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 114385 | 71195 | 2401 | 766 | 0.0001277 | 1.1613e-06 | 109.9667 | 1 | 310 | Customer | 9095 | Load | Tran1phOH | REX R WILSON | 405-535-4507 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | OK - 2022
J2001.010081 |  | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_924 | 910924 | 2020-01-27 12:58 | 2020-01-27 13:14 | 15.5 | 1 | 1 | 15.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 1511 S.BOSTON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 82225 | 61191 | 5011 | 1724 | 1.8e-05 | 1.1613e-06 | 15.5 | 1 | 310 | Customer | 11803 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | Ark - Series 3
J2001.010082 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1862 | 941862 | 2020-01-27 13:04 | 2020-01-27 15:22 | 138.2 | 1 | 1 | 106.9667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | LAMAR | LAMAR AR | CMI_PLANNED | YES | NO | NO | 861113 | 82225 | 7546 | 730 | 730 | 0.00012422 | 1.1613e-06 | 106.9667 | 1 | 308 | Load | 11950 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | Ark - Series 2
J2001.010089 |  | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5221 | 835221 | 2020-01-27 13:05 | 2020-01-27 14:38 | 93.58 | 23 | 14 | 1163.8 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | 0 | CMI_PLANNED | YES | NO | NO | 861113 | 168221 | 148400 | 6517 | 1500 | 0.0013515 | 2.671e-05 | 50.6 | 1 | 310 | Mainline | 63136-2 | Switch | SwitchDefault | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010085 |  | METRO SOUTH | SOUTH CENTRAL | 8194:WESTMOORE | WESTMOORE_9429 | 819429 | 2020-01-27 13:10 | 2020-01-27 13:10 | 0.02 | 1133 | 0 | 18.8833 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 12406 S PENNSYLVANIA AVE | CMI_MOMENTARY | YES | NO | NO | 861113 | 159135 | 102161 | 8102 | 1133 | 2.1929e-05 | 0.0013157 | 0.016667 | 1 | 0 | Feeder | WESTMORE_9429 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010088 | PD-01272020-00363 | METRO SOUTH | SOUTH | 8714:LITTLE AXE | LITTLE_AXE_1421 | 871421 | 2020-01-27 13:10 | 2020-01-27 18:54 | 343.6 | 1 | 1 | 312.55 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | NORMAN | 16712 DIAMOND DR. | CMI_NORMAL | NO | NO | NO | 861113 | 159135 | 56974 | 616 | 616 | 0.00036296 | 1.1613e-06 | 312.55 | 1 | 310 | Load | 142291 | Load | Tran1phPad | COLBY T LLOYD | 405-312-0110 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010087 | PD-01272020-00362 | NORTHWEST | ENID | 4353:OTTER | OTTER_5342 | 435342 | 2020-01-27 13:11 | 2020-01-27 16:49 | 218.05 | 1 | 1 | 218.05 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | LUCIEN | 1ME,7 5/8MS-LUCIEN SUB | CMI_NORMAL | NO | NO | NO | 861113 | 53545 | 37600 | 962 | 169 | 0.00025322 | 1.1613e-06 | 218.05 | 1 | 320 | Load | 90078 | Load | 0 | RONALD K GOSE | 580-541-3131 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2022
J2001.010091 | PD-01272020-00366 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-01-27 13:14 | 2020-01-27 13:58 | 43.78 | 1 | 1 | 43.7833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1225 W.HEFNER RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 8788 | 1952 | 5.0845e-05 | 1.1613e-06 | 43.7833 | 1 | 310 | Customer | 35733 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2021
J2001.010100 | PD-01272020-00371 | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1373 | 831373 | 2020-01-27 13:23 | 2020-01-27 18:33 | 309.97 | 1 | 1 | 293.25 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 11301 SARA RD | CMI_NORMAL | NO | NO | NO | 861113 | 128816 | 116057 | 7897 | 4117 | 0.00034055 | 1.1613e-06 | 293.25 | 1 | 310 | Customer | 179047 | Load | Tran1phPad | KAEL GUTHERY | 405-428-1818 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010106 | PD-01272020-00382 | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5424 | 865424 | 2020-01-27 13:29 | 2020-01-27 15:18 | 108.87 | 1 | 2 | 97.8167 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | MOORE | 501 PATTERSON DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 159135 | 102161 | 9808 | 2010 | 0.00011359 | 1.1613e-06 | 97.8167 | 1 | 310 | Customer | 56543 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010118 | PD-01272020-00392 | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9864 | 839864 | 2020-01-27 13:45 | 2020-01-27 14:39 | 53.95 | 1 | 1 | 53.95 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 512 NW 186th ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 10660 | 3298 | 6.2651e-05 | 1.1613e-06 | 53.95 | 1 | 310 | Customer | 402224 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010120 | PD-01272020-00396 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5022 | 865022 | 2020-01-27 13:47 | 2020-01-27 14:53 | 66.37 | 1 | 2 | 63.0333 | 12 | POOR CONNECTION | 50 | CONNECTOR | MIDWEST CITY | 1804 N.KEY BL | CMI_NORMAL | NO | NO | NO | 861113 | 114385 | 71195 | 8630 | 1662 | 7.32e-05 | 1.1613e-06 | 63.0333 | 1 | 310 | Customer | 8384 | Load | Tran1phOH | ADAM CLARK | 580-310-8924 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2022
J2001.010124 |  | NORTHEAST | MUSKOGEE | 3316:WARNER | WARNER_1621 | 331621 | 2020-01-27 13:53 | 2020-01-27 14:06 | 12.72 | 1 | 1 | 12.7167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | WARNER | 2/10 MI.W.HWY 64 ON ZENITH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 74040 | 33269 | 882 | 423 | 1.4768e-05 | 1.1613e-06 | 12.7167 | 1 | 310 | Customer | 17177 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010128 | PD-01272020-00408 | METRO EAST | SEMINOLE | 7321:LETHA | LETHA_2121 | 732121 | 2020-01-27 14:01 | 2020-01-27 14:36 | 35.02 | 1 | 1 | 34.05 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | SEMINOLE | 2MS, .5MW-HWY 270 ON HARVEY | CMI_NORMAL | NO | NO | NO | 861113 | 114385 | 13609 | 1263 | 429 | 3.9542e-05 | 1.1613e-06 | 34.05 | 1 | 310 | Load | 22591 | Load | TranOpenDelta | BRADY A HUFF | 405-519-0701 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | OK - 2021
J2001.010131 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2231 | 852231 | 2020-01-27 14:03 | 2020-01-27 14:37 | 33.25 | 2 | 1 | 35.8667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | CHOCTAW | 14819 SE 15TH | CMI_PLANNED | YES | NO | NO | 861113 | 114385 | 71195 | 11633 | 1437 | 4.1652e-05 | 2.3226e-06 | 17.9333 | 1 | 308 | Load | 20785 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2021
J2001.010132 | PD-01272020-00420 | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_724 | 510724 | 2020-01-27 14:07 | 2020-01-27 14:26 | 18.63 | 1 | 1 | 18.6333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ARDMORE | 602 W.MAIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 77613 | 23588 | 4509 | 1625 | 2.1639e-05 | 1.1613e-06 | 18.6333 | 1 | 320 | Customer | 12878 | Load | TranOpenDelta | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010137 |  | METRO EAST | EAST | 8416:DUNJEE | DUNJEE_1621 | 841621 | 2020-01-27 14:26 | 2020-01-27 14:32 | 5.98 | 1 | 1 | 5.9833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NICOMA PARK | 12402 NE.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 114385 | 71195 | 3542 | 1553 | 6.9484e-06 | 1.1613e-06 | 5.9833 | 1 | 310 | Load | 68640 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010141 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2231 | 852231 | 2020-01-27 14:38 | 2020-01-27 15:22 | 43.67 | 2 | 1 | 58.1833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | CHOCTAW | 15724 SE 15TH | CMI_PLANNED | YES | NO | NO | 861113 | 114385 | 71195 | 11633 | 1437 | 6.7568e-05 | 2.3226e-06 | 29.0917 | 1 | 310 | Load | 55480 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2021
J2001.010148 | PD-01272020-00469 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-01-27 14:42 | 2020-01-27 16:24 | 101.83 | 49 | 15 | 4437.7667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1/2BKSSW46 ES AGNEW | CMI_NORMAL | NO | NO | NO | 861113 | 159135 | 102161 | 7605 | 2460 | 0.0051535 | 5.6903e-05 | 90.5667 | 1 | 310 | Tap | 16459 | Fuse | FuseOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010143 | PD-01272020-00471 | METRO SOUTH | SOUTH | 8726:NOBLE | NOBLE_2623 | 872623 | 2020-01-27 14:45 | 2020-01-27 18:19 | 213.87 | 2 | 2 | 369.3833 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | NOBLE | BLK 3 LOT 3 ROLLING MEADOWS | CMI_NORMAL | NO | NO | NO | 861113 | 159135 | 56974 | 2968 | 1521 | 0.00042896 | 2.3226e-06 | 184.6917 | 1 | 310 | Secondary | 74119 | Load | Tran1phOH | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010145 | PD-01272020-00461 | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_623 | 880623 | 2020-01-27 14:47 | 2020-01-27 15:53 | 66.45 | 1 | 1 | 66.45 | 27 | TREE:NON PREVENTABLE | 31 | CONDUCTOR SERVICE - OH | GUTHRIE | 1611 W.CLEVELAND | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 168221 | 19821 | 5167 | 1416 | 7.7168e-05 | 1.1613e-06 | 66.45 | 1 | 310 | Customer | 43621 | Load | Tran1phOH | KELLEY D WATSON | 405-763-8148 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010144 |  | SOUTHERN | ARDMORE | 5106:HARRIS ST | HARRIS_ST_622 | 510622 | 2020-01-27 14:47 | 2020-01-27 14:47 | 0 | 1108 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 2307 HARRIS | CMI_MOMENTARY | YES | NO | NO | 861113 | 77613 | 23588 | 2069 | 1108 | 0 | 0.0012867 | 0 | 1 | 0 | Feeder | HARRIS_ST_622 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010149 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-01-27 14:50 | 2020-01-27 15:14 | 24.68 | 1 | 1 | 24.6833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 317 NW.24 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 11126 | 2338 | 2.8664e-05 | 1.1613e-06 | 24.6833 | 1 | 310 | Customer | 1390 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2020
J2001.010154 | PD-01272020-00474 | SOUTHERN | ARDMORE | 5106:HARRIS ST | HARRIS_ST_622 | 510622 | 2020-01-27 15:03 | 2020-01-27 16:57 | 114.27 | 1 | 2 | 40.1 | 13 | PREMATURE FAILURE | 36 | CONDUCTOR PRIMARY - UG | ARDMORE | 1627 CITY LAKE RD | CMI_NORMAL | NO | NO | NO | 861113 | 77613 | 23588 | 2069 | 1108 | 4.6568e-05 | 1.1613e-06 | 40.1 | 1 | 310 | Load | 305994 | Load | 0 | MICHAEL D DICKINSON | 580-229-5532 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010161 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-01-27 15:19 | 2020-01-27 15:41 | 22.12 | 1 | 1 | 22.1167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 130 NW.17 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 11126 | 2338 | 2.5684e-05 | 1.1613e-06 | 22.1167 | 1 | 310 | Customer | 289 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2020
J2001.010168 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2525 | 912525 | 2020-01-27 15:33 | 2020-01-27 17:46 | 132.78 | 2 | 1 | 184.05 | 28 | OTHER (DESCRIBE) | 16 | LINE RECLOSER | FORT SMITH | AIRPORT RD | CMI_PLANNED | YES | NO | NO | 861113 | 82225 | 61191 | 2735 | 198 | 0.00021374 | 2.3226e-06 | 92.025 | 1 | 308 | Load | 11024 | Load | TranOpenDelta | Crew | [6 empty] | Other | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | Ark - Series 2
J2001.010169 | PD-01272020-00490 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-01-27 15:36 | 2020-01-27 16:39 | 62.57 | 1 | 1 | 15.2333 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | DEL CITY | 3924 TEAL DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 159135 | 102161 | 7416 | 2238 | 1.769e-05 | 1.1613e-06 | 15.2333 | 1 | 320 | Customer | 7673 | Load | Tran1phOH | KYLE L GOODIN | 405-426-9802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2022
J2001.010171 | PD-01272020-00493 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5138 | 815138 | 2020-01-27 15:40 | 2020-01-27 16:47 | 66.53 | 1 | 1 | 66.5333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1246 SW.74 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 159135 | 102161 | 13933 | 1416 | 7.7264e-05 | 1.1613e-06 | 66.5333 | 1 | 310 | Customer | 33851 | Load | Tran1phPad | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010172 |  | ARKANSAS | FORT SMITH | 9512:ADABELL ROAD | ADABELL_ROAD_1222 | 951222 | 2020-01-27 15:42 | 2020-01-27 15:43 | 0.98 | 6 | 0 | 5.9118 | 1 | CANCELLED | 57 | CANCELLED | 0 | 0 | CMI_MOMENTARY | YES | NO | NO | 861113 | 82225 | 61191 | 3122 | 1088 | 6.8653e-06 | 6.9677e-06 | 0.9853 | 1 | 0 | Mainline | 12884-2 | Switch | SwitchDefault | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-27 | 2020 |  | Ark - Series 1, Ark - Series 2
J2001.010176 |  | NORTHWEST | ENID | 4107:CLEVELAND AVE | CLEVELAND_AVE_722 | 410722 | 2020-01-27 15:47 | 2020-01-27 16:25 | 37.4 | 1 | 1 | 37.4 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ENID | 513.5 S TYLER--ENID | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 53545 | 37600 | 4462 | 1379 | 4.3432e-05 | 1.1613e-06 | 37.4 | 1 | 310 | Customer | 4929 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010175 | PD-01272020-00498 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4123 | 814123 | 2020-01-27 15:48 | 2020-01-27 21:05 | 317.27 | 1 | 1 | 317.2667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6612 S.KELLEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 159135 | 102161 | 5808 | 1323 | 0.00036844 | 1.1613e-06 | 317.2667 | 1 | 310 | Customer | 46969 | Load | TranOpenDelta | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010179 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-27 15:56 | 2020-01-27 18:29 | 153.58 | 2 | 1 | 290.8667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 7510 TERRY ST | CMI_PLANNED | YES | NO | NO | 861113 | 82225 | 61191 | 2735 | 2123 | 0.00033778 | 2.3226e-06 | 145.4333 | 1 | 308 | Load | 202370 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | Ark - Series 2
J2001.010184 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1862 | 941862 | 2020-01-27 16:04 | 2020-01-27 16:39 | 35.58 | 7 | 5 | 240.8 | 4 | DETERIORATION | 47 | ARRESTOR OH | LAMAR | LAMAR AR | CMI_PLANNED | YES | NO | NO | 861113 | 82225 | 7546 | 730 | 730 | 0.00027964 | 8.129e-06 | 34.4 | 1 | 308 | Load | 965 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | Ark - Series 2
J2001.010187 | PD-01272020-00515 | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_521 | 530521 | 2020-01-27 16:08 | 2020-01-27 17:54 | 106.08 | 1 | 1 | 99.8 | 12 | POOR CONNECTION | 50 | CONNECTOR | WILSON | HWY70/DILLARD 3N 1E .5N WS | CMI_NORMAL | NO | NO | NO | 861113 | 77613 | 6798 | 2127 | 1260 | 0.0001159 | 1.1613e-06 | 99.8 | 1 | 320 | Load | 226335 | Load | Tran1phOH | RANDAL G CALLAWAY | 580-220-8449 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | OK - 2020
J2001.010190 | PD-01272020-00551 | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1421 | 911421 | 2020-01-27 16:16 | 2020-01-27 17:19 | 62.95 | 1 | 1 | 62.95 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | FORT SMITH | 2121 N.30 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 82225 | 61191 | 4737 | 1747 | 7.3103e-05 | 1.1613e-06 | 62.95 | 1 | 310 | Customer | 7249 | Load | Tran1phOH | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-27 | 2020 |  | Ark - Series 1
J2001.010199 |  | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1933 | 851933 | 2020-01-27 16:43 | 2020-01-27 17:00 | 16.92 | 1 | 1 | 16.9167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 3520 SHADYBROOK DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 114385 | 71195 | 12444 | 932 | 1.9645e-05 | 1.1613e-06 | 16.9167 | 1 | 310 | Customer | 25273 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2022
J2001.010207 | PD-01272020-00563 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1933 | 851933 | 2020-01-27 17:12 | 2020-01-27 21:01 | 228.75 | 1 | 3 | 187.4667 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | MIDWEST CITY | 3520 SHADYBROOK DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 114385 | 71195 | 12444 | 932 | 0.0002177 | 1.1613e-06 | 187.4667 | 1 | 315 | Customer | 25273 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2022
J2001.010209 |  | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2923 | 812923 | 2020-01-27 17:21 | 2020-01-27 17:28 | 7.45 | 1 | 1 | 7.45 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | ALMONTE APTS-SW.59 + MAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 159135 | 102161 | 6385 | 1636 | 8.6516e-06 | 1.1613e-06 | 7.45 | 1 | 310 | Customer | 71518 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010212 | PD-01272020-00565 | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1421 | 911421 | 2020-01-27 17:39 | 2020-01-27 19:08 | 89.22 | 1 | 2 | 14.3333 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | FORT SMITH | 1920 CHURCHILL RD + MORRIS DR. | CMI_NORMAL | NO | NO | NO | 861113 | 82225 | 61191 | 4737 | 1747 | 1.6645e-05 | 1.1613e-06 | 14.3333 | 1 | 320 | Customer | 3661 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-27 | 2020 |  | Ark - Series 1
J2001.010213 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-01-27 17:42 | 2020-01-27 17:47 | 5.07 | 1 | 1 | 5.0667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 130 NW.17 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168221 | 148400 | 11126 | 2338 | 5.8839e-06 | 1.1613e-06 | 5.0667 | 1 | 310 | Customer | 289 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2020
J2001.010216 |  | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1924 | 851924 | 2020-01-27 17:53 | 2020-01-27 17:58 | 5.1 | 1 | 1 | 5.1 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | NE 12 + DOUGLAS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 114385 | 71195 | 12444 | 1608 | 5.9226e-06 | 1.1613e-06 | 5.1 | 1 | 310 | Customer | 72681 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010219 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_824 | 870824 | 2020-01-27 18:02 | 2020-01-27 18:12 | 10.1 | 1 | 1 | 10.1 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 918.5 S.LAHOMA AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 159134 | 56974 | 6776 | 1462 | 1.1729e-05 | 1.1613e-06 | 10.1 | 1 | 310 | Customer | 33206 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010220 | PD-01272020-00566 | METRO EAST | EAST | 8417:ROUND BARN | ROUND_BARN_1723 | 841723 | 2020-01-27 18:04 | 2020-01-27 19:58 | 114.43 | 1 | 2 | 105.1833 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 11420 N.WESTMINSTER | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 114373 | 71193 | 1007 | 1007 | 0.00012215 | 1.1613e-06 | 105.1833 | 1 | 320 | Customer | 55609 | Load | Tran1phOH | BRADLEY SUDBECK | 405-999-6850 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010223 |  | ARKANSAS | POTEAU | 3509:PANAMA | PANAMA 21 | 350921 | 2020-01-27 18:13 | 2020-01-27 18:13 | 0 | 315 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | 0 | 24068 OK-31 | CMI_MOMENTARY | YES | NO | NO | 861113 | 82219 | 13487 | 1388 | 819 | 0 | 0.00036581 | 0 | 1 | 0 | Mainline | 401900 | Recloser | Rec3phElectronic | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010225 | PD-01272020-00567 | ARKANSAS | POTEAU | 3607:ROLAND ROAD | ROLAND_RD_721 | 360721 | 2020-01-27 18:25 | 2020-01-27 19:45 | 79.53 | 1 | 1 | 79.5333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ROLAND | WEST END OF ROLAND VILLAGE APT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 82219 | 13487 | 1139 | 1139 | 9.2361e-05 | 1.1613e-06 | 79.5333 | 1 | 310 | Customer | 16917 | Load | Tran1phPad | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010227 | PD-01272020-00568 | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6223 | 866223 | 2020-01-27 18:43 | 2020-01-28 01:15 | 392.38 | 30 | 17 | 11616.5 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | .3MS SE44 .4ME ANDRSON | CMI_NORMAL | NO | NO | NO | 861113 | 114373 | 71193 | 7210 | 2235 | 0.01349 | 3.4839e-05 | 387.2167 | 1 | 310 | Mainline | 14681 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010229 |  | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6223 | 866223 | 2020-01-27 18:43 | 2020-01-28 01:32 | 409.07 | 20 | 12 | 7771 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | .3MS SE44 .4ME ANDRSON | CMI_NORMAL | NO | NO | NO | 861113 | 114373 | 71193 | 7210 | 2235 | 0.0090244 | 2.3226e-05 | 388.55 | 1 | 310 | Mainline | 14681 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010233 | PD-01272020-00571 | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_721 | 590721 | 2020-01-27 18:50 | 2020-01-27 19:52 | 62.43 | 1 | 1 | 62.4333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MANNSVILLE | 110 S. 21ST. ST. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 77612 | 7199 | 2190 | 505 | 7.2503e-05 | 1.1613e-06 | 62.4333 | 1 | 310 | Customer | 401216 | Load | Tran1phPad | ANDREW CHAVERS | 580-504-0524 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2021
J2001.010253 |  | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2923 | 812923 | 2020-01-27 19:04 | 2020-01-27 19:25 | 20.12 | 1 | 1 | 20.1167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 5901 S.MAY ALMONTE APTS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 159134 | 102160 | 6385 | 1636 | 2.3361e-05 | 1.1613e-06 | 20.1167 | 1 | 310 | Customer | 71509 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010263 |  | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1933 | 851933 | 2020-01-27 19:52 | 2020-01-27 21:03 | 70.73 | 3 | 3 | 81.75 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | MIDWEST CITY | 3520 SHADYBROOK DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861113 | 114373 | 71193 | 12444 | 932 | 9.4935e-05 | 3.4839e-06 | 27.25 | 1 | 310 | Load | 25273 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2022
J2001.010262 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4022 | 834022 | 2020-01-27 19:54 | 2020-01-27 20:02 | 7.6 | 1 | 1 | 7.6 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6062B - W BRITTON RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 128814 | 116056 | 10843 | 1369 | 8.8258e-06 | 1.1613e-06 | 7.6 | 1 | 310 | Customer | 70657 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | #N/A
J2001.010264 | PD-01272020-00574 | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2923 | 812923 | 2020-01-27 20:01 | 2020-01-27 22:00 | 118.65 | 1 | 1 | 118.65 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 5901 S.MAY ALMONTE APTS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 159134 | 102160 | 6385 | 1636 | 0.00013779 | 1.1613e-06 | 118.65 | 1 | 310 | Customer | 71509 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010265 |  | METRO WEST | WEST | 8335:BETHANY | BETHANY_3529 | 833529 | 2020-01-27 20:07 | 2020-01-27 20:19 | 12 | 1 | 1 | 12 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | NW.42 + MERIDIAN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 128814 | 116056 | 7870 | 2017 | 1.3935e-05 | 1.1613e-06 | 12 | 1 | 310 | Customer | 75561 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010266 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-01-27 20:12 | 2020-01-27 20:24 | 12.3 | 1 | 1 | 12.3 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1305 N.MERIDIAN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861113 | 168218 | 148397 | 9250 | 1943 | 1.4284e-05 | 1.1613e-06 | 12.3 | 1 | 310 | Customer | 38494 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2021
J2001.010268 | PD-01272020-00582 | METRO EAST | SEMINOLE | 7508:EMAHAKA | EMAHAKA 21 | 750821 | 2020-01-27 20:38 | 2020-01-27 23:30 | 172.47 | 1 | 1 | 114.9333 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | HOLDENVILLE | 5S 2E 1/4N WEWOKA | CMI_NORMAL | NO | NO | NO | 861113 | 114373 | 13608 | 253 | 253 | 0.00013347 | 1.1613e-06 | 114.9333 | 1 | 310 | Customer | 6686 | Load | Tran3phWye | KEVIN M RICH | 405-802-2121 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010269 | PD-01272020-00583 | NORTHEAST | SAPULPA | 3213:BOWDEN | BOWDEN_1329 | 321329 | 2020-01-27 20:46 | 2020-01-27 22:00 | 74.23 | 1 | 1 | 71.3333 | 5 | ELECTRICAL TRACKING | 20 | FUSE BARREL | SAPULPA | WEST END OF ANDREW | CMI_NORMAL | NO | NO | NO | 861113 | 74040 | 40772 | 3373 | 1517 | 8.2839e-05 | 1.1613e-06 | 71.3333 | 1 | 310 | Customer | 46733 | Load | Tran1phOH | JOSHUA N MCKINNEY | 918-863-6313 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2020
J2001.010273 | PD-01272020-00587 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4823 | 824823 | 2020-01-27 20:54 | 2020-01-27 22:54 | 119.83 | 1 | 2 | 23.2 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 3221 SW.24 | CMI_NORMAL | NO | NO | NO | 861113 | 168218 | 148397 | 4195 | 1796 | 2.6942e-05 | 1.1613e-06 | 23.2 | 1 | 310 | Customer | 21896 | Load | Tran1phOH | THOMAS E COLE | 405-623-9338 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2021
J2001.010274 |  | ARKANSAS | POTEAU | 3607:ROLAND ROAD | ROLAND_RD_721 | 360721 | 2020-01-27 21:07 | 2020-01-27 21:11 | 3.85 | 1 | 1 | 3.85 | 1 | CANCELLED | 57 | CANCELLED | ROLAND | WEST END OF ROLAND VILLAGE APT | CMI_MOMENTARY | YES | NO | NO | 861113 | 82219 | 13487 | 1139 | 1139 | 4.471e-06 | 1.1613e-06 | 3.85 | 1 | 310 | Customer | 16917 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-27 | 2020 |  | #N/A
J2001.010284 | PD-01272020-00593 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4821 | 824821 | 2020-01-27 22:37 | 2020-01-28 00:05 | 88.1 | 1 | 1 | 88.1 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 2109 W Sheridan | CMI_NORMAL | NO | NO | NO | 861113 | 168218 | 148397 | 4195 | 242 | 0.00010231 | 1.1613e-06 | 88.1 | 1 | 311 | Load | 350751 | Load | Tran3phWye | DARREN L STOCKTON | 918-777-1697 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-27 | 2020 |  | OK - 2022
J2001.010545 | PD-01282020-00084 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-01-28 03:43 | 2020-01-28 07:41 | 238.12 | 2 | 1 | 476.2333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 4901 S INDIAN MERIDIAN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 114373 | 71193 | 11632 | 3534 | 0.00055297 | 2.3223e-06 | 238.1167 | 1 | 310 | Secondary | 77868 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010546 | PD-01282020-00085 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-01-28 03:43 | 2020-01-28 10:40 | 416.65 | 1 | 1 | 416.65 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 5600 Montford Way | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 114373 | 71193 | 11632 | 3534 | 0.00048379 | 1.1611e-06 | 416.65 | 1 | 310 | Customer | 375108 | Load | Tran1phPad | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010547 | PD-01282020-00097 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-01-28 03:43 | 2020-01-28 11:11 | 447.65 | 1 | 1 | 447.65 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1/2 S HOLZMAN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 114373 | 71193 | 11632 | 3534 | 0.00051978 | 1.1611e-06 | 447.65 | 1 | 308 | Customer | 77716 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010430 | PD-01282020-00006 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-01-28 03:43 | 2020-01-28 07:41 | 238.12 | 459 | 151 | 109295.55 | 5 | ELECTRICAL TRACKING | 47 | ARRESTOR OH | CHOCTAW | TRIPLE XXX RD & SE 29TH | CMI_NORMAL | NO | NO | NO | 861225 | 114373 | 71193 | 11632 | 3534 | 0.12691 | 0.00053296 | 238.1167 | 1 | 310 | Mainline | 19978 | Switch | SwitchOH | JAY E COTTMAN | 405-432-7177 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010337 |  | ARKANSAS | POTEAU | 3607:ROLAND ROAD | ROLAND_RD_721 | 360721 | 2020-01-28 03:55 | 2020-01-28 05:06 | 71.17 | 1 | 1 | 71.1667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ROLAND | WEST END OF ROLAND VILLAGE APT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 82219 | 13487 | 1139 | 1139 | 8.2634e-05 | 1.1611e-06 | 71.1667 | 1 | 310 | Customer | 16917 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | #N/A
J2001.010472 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-01-28 04:45 | 2020-01-28 06:12 | 87.3 | 117 | 44 | 9137.54 | 25 | LIGHTNING | 47 | ARRESTOR OH | CHOCTAW | S. Triple X Rd. and SE 15th St. | CMI_NORMAL | NO | NO | NO | 861225 | 114373 | 71193 | 11632 | 3534 | 0.01061 | 0.00013585 | 78.0986 | 1 | 310 | Mainline | 304031 | Recloser | Rec3phHydralic | [7 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010466 | PD-01282020-00013 | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3422 | 843422 | 2020-01-28 05:34 | 2020-01-28 08:11 | 157.33 | 1 | 1 | 127.4833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 6601 N.EASTERN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 168218 | 148397 | 1224 | 726 | 0.00014803 | 1.1611e-06 | 127.4833 | 1 | 310 | Customer | 3710 | Load | TranOHDeltaSplitBank | REX R WILSON | 405-535-4507 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | #N/A
J2001.010477 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-01-28 05:42 | 2020-01-28 08:05 | 142.55 | 1 | 2 | 119.3667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 0 | 0 | 0 | 0 | 0.0001386 | 1.1611e-06 | 119.3667 | 1 | 310 | Customer |  | 0 | 0 | [6 empty] | 06/02/2020 note from burchamc. Reference J2001.010477 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Manually completed blank Job Region, Job Area, etc. OMS Notes for Job. This is non connected call. | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010471 | PD-01282020-00017 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2031 | 862031 | 2020-01-28 05:56 | 2020-01-28 08:29 | 153.17 | 1 | 1 | 112.1672 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 845 SE.29 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 159134 | 102160 | 4749 | 1442 | 0.00013024 | 1.1611e-06 | 112.1672 | 1 | 320 | Load | 90520 | Load | 0 | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2021
J2001.010478 |  | METRO WEST | EL RENO | 8908:ROMAN NOSE | ROMAN_NOSE_852 | 890852 | 2020-01-28 06:01 | 2020-01-28 06:01 | 0 | 256 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | WATONGA | 6006 ST HWY 3 | CMI_MOMENTARY | YES | NO | NO | 861225 | 128814 | 12758 | 525 | 256 | 0 | 0.00029725 | 0 | 1 | 0 | Feeder | ROMAN_NOSE_852 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010481 | PD-01282020-00018 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2222 | 852222 | 2020-01-28 06:08 | 2020-01-28 08:32 | 143.57 | 1 | 1 | 93.05 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | HARRAH | 724 N. PEEBLY RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 114373 | 71193 | 11632 | 2214 | 0.00010804 | 1.1611e-06 | 93.05 | 1 | 310 | Load | 326827 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010482 | PD-01282020-00016 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2031 | 862031 | 2020-01-28 06:09 | 2020-01-28 08:16 | 127.35 | 1 | 1 | 92.5 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1216 SE.18 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 159134 | 102160 | 4749 | 1442 | 0.00010741 | 1.1611e-06 | 92.5 | 1 | 310 | Customer | 22107 | Load | Tran1phOH | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2021
J2001.010483 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2135 | 822135 | 2020-01-28 06:10 | 2020-01-28 06:19 | 8.42 | 426 | 26 | 1881.25 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 4431 NW 10TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 168218 | 148397 | 9250 | 426 | 0.0021844 | 0.00049464 | 4.4161 | 1 | 310 | Feeder | MERIDIAN_2135 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-28 | 2020 |  | OK - 2022
J2001.010492 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2135 | 822135 | 2020-01-28 06:15 | 2020-01-28 12:08 | 353.05 | 5 | 5 | 1188.8333 | 22 | WIND | 28 | CROSSARM | OKLAHOMA CITY | 3845 NW.10 | CMI_NORMAL | NO | NO | NO | 861225 | 168218 | 148397 | 9250 | 426 | 0.0013804 | 5.8057e-06 | 237.7667 | 1 | 310 | Secondary | 4259 | Load | TranOpenDelta | Crew | [6 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2022
J2001.010486 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-01-28 06:17 | 2020-01-28 08:06 | 108.95 | 1 | 1 | 84.2167 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 0 | 0 | 0 | 0 | 9.7787e-05 | 1.1611e-06 | 84.2167 | 1 | 310 | Customer |  | 0 | 0 | [6 empty] | 06/02/2020 note from burchamc. Reference J2001.010486 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Manually completed blank Job Region, Job Area, etc. OMS Notes for Job. This is non connected call. | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010489 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2135 | 822135 | 2020-01-28 06:18 | 2020-01-28 07:43 | 84.67 | 1 | 1 | 84.6667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 3913 NW.PARK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 168218 | 148397 | 9250 | 426 | 9.831e-05 | 1.1611e-06 | 84.6667 | 1 | 310 | Customer | 28221 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2022
J2001.010488 | PD-01282020-00021 | METRO WEST | EL RENO | 8908:ROMAN NOSE | ROMAN_NOSE_852 | 890852 | 2020-01-28 06:20 | 2020-01-28 09:05 | 165.2 | 1 | 2 | 96.1833 | 5 | ELECTRICAL TRACKING | 47 | ARRESTOR OH | LOYAL | OMEGA RURAL | CMI_NORMAL | NO | NO | NO | 861225 | 128814 | 12758 | 525 | 256 | 0.00011168 | 1.1611e-06 | 96.1833 | 1 | 310 | Customer | 30368 | Load | Tran1phOH | MICHAEL T MAHEN | 405-210-6029 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010493 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2135 | 822135 | 2020-01-28 06:23 | 2020-01-28 07:25 | 62.37 | 1 | 1 | 62.3667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 3625 SW.13 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 168218 | 148397 | 9250 | 426 | 7.2416e-05 | 1.1611e-06 | 62.3667 | 1 | 310 | Customer | 8919 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2022
J2001.010494 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6329 | 816329 | 2020-01-28 06:27 | 2020-01-28 06:27 | 0.03 | 1744 | 0 | 58.1333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 241 SW 134TH ST | CMI_MOMENTARY | YES | NO | NO | 861225 | 159134 | 102160 | 11834 | 1709 | 6.7501e-05 | 0.002025 | 0.033333 | 1 | 0 | Feeder | SOUTHGAT_6329 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010498 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2135 | 822135 | 2020-01-28 06:29 | 2020-01-28 07:24 | 55.62 | 1 | 1 | 55.6167 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 4009 NW.PARK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 168218 | 148397 | 9250 | 426 | 6.4579e-05 | 1.1611e-06 | 55.6167 | 1 | 310 | Customer | 4012 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2022
J2001.010500 | PD-01282020-00019 | METRO EAST | CHANDLER | 7119:WARWICK | WARWICK_1941 | 711941 | 2020-01-28 06:33 | 2020-01-28 11:16 | 283.32 | 1 | 1 | 283.3167 | 25 | LIGHTNING | 12 | POLE | WELLSTON | 1.5MS-HW 66 ON SUNFLWR | CMI_NORMAL | NO | NO | NO | 861225 | 114373 | 7465 | 2419 | 1462 | 0.00032897 | 1.1611e-06 | 283.3167 | 1 | 310 | Tap | 5529 | Fuse | FuseOH | JAY E COTTMAN | 405-432-7177 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2021
J2001.010508 | PD-01282020-00031 | METRO WEST | WEST | 8321:PIEDMONT | PIEDMONT_2169 | 832169 | 2020-01-28 07:05 | 2020-01-28 08:58 | 113.42 | 1 | 1 | 112.0667 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | PIEDMONT | Lot 12, block 1 of Autumn Chase/Hawks Landing at Town Central | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861225 | 128814 | 116056 | 6294 | 1656 | 0.00013012 | 1.1611e-06 | 112.0667 | 1 | 320 | Customer | 376404 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010514 | PD-01282020-00032 | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_423 | 710423 | 2020-01-28 07:06 | 2020-01-28 14:13 | 426.8 | 12 | 4 | 5148.8 | 25 | LIGHTNING | 12 | POLE | CHANDLER | ON HWY66 4MI E CHANDLR | CMI_NORMAL | NO | NO | NO | 861225 | 114373 | 7465 | 2822 | 976 | 0.0059785 | 1.3934e-05 | 429.0667 | 1 | 310 | Mainline | 1284 | Fuse | FuseOH | SHAWN HILL | 405-308-1695 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010518 | PD-01282020-00039 | METRO NORTH | NORTH | 8493:KELLEY AVE | KELLEY_AVENUE_9331 | 849331 | 2020-01-28 07:40 | 2020-01-28 09:45 | 125.35 | 2 | 3 | 245.5667 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 7400 N BROADWAY EXT | CMI_NORMAL | NO | NO | NO | 861225 | 168218 | 148397 | 1481 | 1059 | 0.00028514 | 2.3223e-06 | 122.7833 | 1 | 310 | Load | 65431 | Load | Tran3phWye | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010529 | PD-01282020-00052 | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3821 | 913821 | 2020-01-28 08:05 | 2020-01-28 09:36 | 91.43 | 1 | 1 | 91.4333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 319 S.9 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 82219 | 61186 | 2936 | 209 | 0.00010617 | 1.1611e-06 | 91.4333 | 1 | 320 | Customer | 7244 | Load | TranOH3phDelta | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-28 | 2020 |  | Ark - Series 2
J2001.010528 | PD-01282020-00049 | METRO WEST | EL RENO | 8908:ROMAN NOSE | ROMAN_NOSE_852 | 890852 | 2020-01-28 08:05 | 2020-01-28 09:14 | 69.37 | 1 | 1 | 37.8167 | 5 | ELECTRICAL TRACKING | 47 | ARRESTOR OH | LOYAL | 13 ME WATONGA | CMI_NORMAL | NO | NO | NO | 861225 | 128814 | 12758 | 525 | 256 | 4.391e-05 | 1.1611e-06 | 37.8167 | 1 | 310 | Load | 34318 | Load | TranOH3phDelta | MICHAEL T MAHEN | 405-210-6029 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010531 | PD-01282020-00055 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1924 | 851924 | 2020-01-28 08:06 | 2020-01-28 09:49 | 102.83 | 1 | 1 | 102.8333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | NE 12 + DOUGLAS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 114373 | 71193 | 12444 | 1608 | 0.0001194 | 1.1611e-06 | 102.8333 | 1 | 310 | Customer | 72681 | Load | Tran1phPad | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010532 | PD-01282020-00057 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_871 | 830871 | 2020-01-28 08:07 | 2020-01-28 10:40 | 152.98 | 1 | 1 | 145.8833 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 2329 NW 195TH ST | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861225 | 168218 | 148397 | 19378 | 4241 | 0.00016939 | 1.1611e-06 | 145.8833 | 1 | 320 | Customer | 302523 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2021
J2001.010539 | PD-01282020-00064 | METRO EAST | SHAWNEE | 7409:MCLOUD | MCLOUD_922 | 740922 | 2020-01-28 08:12 | 2020-01-28 15:23 | 431.35 | 22 | 8 | 2285.8 | 25 | LIGHTNING | 12 | POLE | MCLOUD | MCLOUD | CMI_NORMAL | NO | NO | NO | 861225 | 114373 | 22107 | 2032 | 1210 | 0.0026541 | 2.5545e-05 | 103.9 | 1 | 310 | Tap | 149255 | Fuse | FuseOH | JEREMIAH D WALKER | 405-974-0464 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | OK - 2021
J2001.010540 | PD-01282020-00063 | METRO WEST | WEST | 8158:SARA | SARA_5862 | 815862 | 2020-01-28 08:19 | 2020-01-28 13:33 | 314.38 | 1 | 1 | 314.3833 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | Olde Rockwell Estates | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861225 | 128814 | 116056 | 18250 | 3608 | 0.00036504 | 1.1611e-06 | 314.3833 | 1 | 310 | Customer | 262718 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2022
J2001.010550 | PD-01282020-00086 | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1721 | 861721 | 2020-01-28 08:40 | 2020-01-28 11:28 | 167.62 | 1 | 1 | 126.5771 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 4601 ROYAL OAK DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 114373 | 71193 | 6949 | 1505 | 0.00014697 | 1.1611e-06 | 126.5771 | 1 | 310 | Customer | 62439 | Load | Tran1phPad | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | #N/A
J2001.010549 | PD-01282020-00107 | METRO EAST | SEMINOLE | 7505:WEWOKA | WEWOKA 24 | 750524 | 2020-01-28 08:42 | 2020-01-28 09:54 | 71.85 | 1 | 1 | 69.2667 | 25 | LIGHTNING | 20 | FUSE BARREL | WEWOKA | DIXIE CAMP ROAD | CMI_NORMAL | NO | NO | NO | 861225 | 114373 | 13608 | 2474 | 1191 | 8.0428e-05 | 1.1611e-06 | 69.2667 | 1 | 310 | Load | 289 | Load | Tran1phOH | DELBERT HISAW | 405-683-1721 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | OK - 2021
J2001.010551 |  | METRO WEST | EL RENO | 8908:ROMAN NOSE | ROMAN_NOSE_852 | 890852 | 2020-01-28 08:42 | 2020-01-28 08:42 | 0 | 254 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | WATONGA | 6006 ST HWY 3 | CMI_MOMENTARY | YES | NO | NO | 861225 | 128814 | 12758 | 525 | 256 | 0 | 0.00029493 | 0 | 1 | 0 | Feeder | ROMAN_NOSE_852 | Recloser | 0 | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010559 | PD-01282020-00126 | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_622 | 770622 | 2020-01-28 08:52 | 2020-01-28 10:13 | 81.23 | 1 | 2 | 77.05 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 21 | FUSE - TRANSFORMER | BRISTOW | 3 MN BRISTOW | CMI_NORMAL | NO | NO | NO | 861225 | 74040 | 40772 | 3783 | 2010 | 8.9466e-05 | 1.1611e-06 | 77.05 | 1 | 310 | Load | 40806 | Load | Tran1phOH | GREGORY R HOOVER | 918-261-6803 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | #N/A
J2001.010555 | PD-01282020-00105 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-01-28 08:56 | 2020-01-28 10:28 | 92.22 | 6 | 7 | 482.1 | 3 | DAMAGED BY PUBLIC | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 2333 SW 49 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 159134 | 102160 | 7605 | 2460 | 0.00055978 | 6.9668e-06 | 80.35 | 1 | 310 | Load | 18700 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | #N/A
J2001.010557 | PD-01282020-00108 | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2122 | 892122 | 2020-01-28 09:02 | 2020-01-28 09:41 | 39.17 | 1 | 1 | 39.1667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | EL RENO | 3705 S. Choctaw | CMI_NORMAL | NO | NO | NO | 861225 | 128814 | 12758 | 3190 | 883 | 4.5478e-05 | 1.1611e-06 | 39.1667 | 1 | 320 | Load | 252928 | Load | Tran3phWye | JOSH BLACK | 405-403-9382 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010560 |  | METRO SOUTH | SOUTH | 8726:NOBLE | NOBLE_2621 | 872621 | 2020-01-28 09:07 | 2020-01-28 09:14 | 6.38 | 1 | 1 | 6.3833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NOBLE | 8TH ST. + HWY 77 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 159134 | 56974 | 2968 | 1447 | 7.4119e-06 | 1.1611e-06 | 6.3833 | 1 | 310 | Customer | 74669 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010566 | PD-01282020-00135 | NORTHEAST | SAPULPA | 3214:LONE STAR | LONE_STAR_1422 | 321422 | 2020-01-28 09:18 | 2020-01-28 10:12 | 54.37 | 1 | 1 | 54.3667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SAPULPA | 1/4S 151ST ON 97-W AV 100 W | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 74040 | 40772 | 2658 | 1098 | 6.3127e-05 | 1.1611e-06 | 54.3667 | 1 | 310 | Load | 46283 | Load | Tran1phOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2020
J2001.010575 | PD-01282020-00148 | METRO WEST | WEST | 8158:SARA | SARA_5862 | 815862 | 2020-01-28 09:45 | 2020-01-28 11:17 | 91.73 | 1 | 1 | 91.7333 | 11 | OVERLOAD | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | Tpk.1/4E of 4915 S.Morgan Rd. | CMI_NORMAL | NO | NO | NO | 861225 | 128814 | 116056 | 18250 | 3608 | 0.00010651 | 1.1611e-06 | 91.7333 | 1 | 310 | Load | 419158 | Load | Tran1phOH | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2022
J2001.010576 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3821 | 913821 | 2020-01-28 09:46 | 2020-01-28 09:46 | 0 | 209 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | FT SMITH | 1904 SOUTH 7TH ST | CMI_MOMENTARY | YES | NO | NO | 861225 | 82219 | 61186 | 2936 | 209 | 0 | 0.00024268 | 0 | 1 | 0 | Feeder | ARKOMA_3821 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-01-28 | 2020 |  | Ark - Series 2
J2001.010580 | PD-01282020-00169 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6024 | 836024 | 2020-01-28 09:51 | 2020-01-28 11:57 | 126.18 | 7 | 5 | 874.1833 | 4 | DETERIORATION | 20 | FUSE BARREL | OKLAHOMA CITY | MORGAN/ NW 63 | CMI_NORMAL | NO | NO | NO | 861225 | 128814 | 116056 | 5505 | 1342 | 0.001015 | 8.128e-06 | 124.8833 | 1 | 310 | Mainline | 13807 | Fuse | FuseOH | STEVEN GILES | 405-227-2802 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | OK - 2022
J2001.010582 | PD-01282020-00189 | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_649 | 890649 | 2020-01-28 10:02 | 2020-01-28 11:19 | 77 | 1 | 1 | 77 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | WATONGA | 3MI S 11/2M E OF SOUTHARD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 128814 | 12758 | 1364 | 276 | 8.9408e-05 | 1.1611e-06 | 77 | 1 | 320 | Load | 183009 | Load | Tran1phOH | MICHAEL T MAHEN | 405-210-6029 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010589 | PD-01282020-00205 | METRO NORTH | NORTH | 8493:KELLEY AVE | KELLEY_AVENUE_9331 | 849331 | 2020-01-28 10:21 | 2020-01-28 14:53 | 272.48 | 1 | 2 | 272.4833 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 7400 N BROADWAY EXT | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861225 | 168218 | 148397 | 1481 | 1059 | 0.00031639 | 1.1611e-06 | 272.4833 | 1 | 320 | Customer | 65431 | Load | Tran3phWye | CORY J HUFFMAN | 870-668-0377 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010588 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3821 | 913821 | 2020-01-28 10:21 | 2020-01-28 10:38 | 17.23 | 1 | 1 | 17.2333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 319 S.9 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 82219 | 61186 | 2936 | 209 | 2.001e-05 | 1.1611e-06 | 17.2333 | 1 | 320 | Customer | 7244 | Load | TranOH3phDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-28 | 2020 |  | Ark - Series 2
J2001.010591 | PD-01282020-00224 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1522 | 811522 | 2020-01-28 10:26 | 2020-01-28 10:55 | 28.97 | 1 | 1 | 13.9288 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2511 SW.27 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 159134 | 102160 | 6062 | 1942 | 1.6173e-05 | 1.1611e-06 | 13.9288 | 1 | 310 | Customer | 33105 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | OK - 2022
J2001.010593 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-01-28 10:33 | 2020-01-28 12:11 | 98.5 | 16 | 2 | 1540.8 | 4 | DETERIORATION | 13 | PIN | OKLAHOMA CITY | SE 127 ES ANDERSON | CMI_PLANNED | YES | NO | NO | 861225 | 159134 | 56974 | 4240 | 1005 | 0.0017891 | 1.8578e-05 | 96.3 | 1 | 310 | Mainline | 9177 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010597 | PD-01282020-00229 | NORTHWEST | ENID | 4107:CLEVELAND AVE | CLEVELAND_AVE_721 | 410721 | 2020-01-28 10:38 | 2020-01-28 11:05 | 26.5 | 1 | 1 | 26.5 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ENID | 418 S HARDING--ENID | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 53540 | 37596 | 4462 | 856 | 3.077e-05 | 1.1611e-06 | 26.5 | 1 | 320 | Customer | 5565 | Load | Tran1phOH | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | #N/A
J2001.010598 | PD-01282020-00230 | METRO EAST | EAST | 8471:NE 30TH ST | NE_30TH_ST_7122 | 847122 | 2020-01-28 10:40 | 2020-01-28 12:09 | 89.38 | 1 | 1 | 89.3833 | 14 | SEALED OUT/OPEN | 27 | CUTOUT | OKLAHOMA CITY | 1/2 MN NE 36TH, WS SOONER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 114373 | 71193 | 2401 | 766 | 0.00010379 | 1.1611e-06 | 89.3833 | 1 | 320 | Load | 77377 | Load | Tran3phWye | REX R WILSON | 405-535-4507 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | OK - 2022
J2001.010600 | PD-01282020-00232 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1221 | 831221 | 2020-01-28 10:41 | 2020-01-28 11:10 | 29.47 | 1 | 1 | 17.0553 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 5904 N.PENN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 168218 | 148397 | 7752 | 995 | 1.9804e-05 | 1.1611e-06 | 17.0553 | 1 | 310 | Customer | 35253 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2022
J2001.010601 |  | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1421 | 911421 | 2020-01-28 10:42 | 2020-01-28 13:17 | 154.7 | 1 | 1 | 154.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 2121 N.30 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 82219 | 61186 | 4737 | 1747 | 0.00017963 | 1.1611e-06 | 154.7 | 1 | 310 | Customer | 7249 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-28 | 2020 |  | Ark - Series 1
J2001.010599 | PD-01282020-00231 | METRO EAST | EAST | 8471:NE 30TH ST | NE_30TH_ST_7122 | 847122 | 2020-01-28 10:42 | 2020-01-28 13:37 | 174.98 | 1 | 1 | 174.9833 | 14 | SEALED OUT/OPEN | 27 | CUTOUT | OKLAHOMA CITY | 5BNNE50-2BE SOONER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 114373 | 71193 | 2401 | 766 | 0.00020318 | 1.1611e-06 | 174.9833 | 1 | 320 | Load | 55798 | Load | Tran3phWye | REX R WILSON | 405-535-4507 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | OK - 2022
J2001.010603 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-01-28 10:55 | 2020-01-28 12:12 | 76.65 | 2 | 2 | 147.6833 | 4 | DETERIORATION | 13 | PIN | OKLAHOMA CITY | 11823 SE.128 | CMI_PLANNED | YES | NO | NO | 861225 | 159134 | 56974 | 4240 | 1005 | 0.00017148 | 2.3223e-06 | 73.8417 | 1 | 310 | Secondary | 48063 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010604 |  | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_924 | 910924 | 2020-01-28 10:55 | 2020-01-28 11:05 | 9.4 | 1 | 1 | 9.4 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 1624 S.FRESNO | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 82219 | 61186 | 5010 | 1724 | 1.0915e-05 | 1.1611e-06 | 9.4 | 1 | 310 | Customer | 14753 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | Ark - Series 3
J2001.010605 | PD-01282020-00265 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3627 | 833627 | 2020-01-28 11:05 | 2020-01-28 12:00 | 55.38 | 1 | 1 | 55.3833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1928 HERITAGE-PK PERSIMMON SQR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 168218 | 148397 | 8788 | 1494 | 6.4308e-05 | 1.1611e-06 | 55.3833 | 1 | 310 | Customer | 69162 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010607 | PD-01282020-00260 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2022 | 822022 | 2020-01-28 11:06 | 2020-01-28 11:57 | 50.85 | 1 | 1 | 28.0507 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 2350 NW.PARK | CMI_NORMAL | NO | NO | NO | 861225 | 168218 | 148397 | 6038 | 2121 | 3.2571e-05 | 1.1611e-06 | 28.0507 | 1 | 310 | Customer | 27455 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | OK - 2020
J2001.010608 | PD-01282020-00273 | ARKANSAS | POTEAU | 3509:PANAMA | PANAMA 21 | 350921 | 2020-01-28 11:17 | 2020-01-28 12:18 | 60.73 | 1 | 1 | 59.4667 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 23 | FUSE - PRIMARY | PANAMA | PANAMA, SOUTHEAST SIDE | CMI_NORMAL | NO | NO | NO | 861225 | 82219 | 13487 | 1388 | 819 | 6.9049e-05 | 1.1611e-06 | 59.4667 | 1 | 310 | Customer | 2216 | Load | Tran1phOH | JOHN MEEH | 918-413-0959 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | #N/A
J2001.010615 | PD-01282020-00287 | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5222 | 835222 | 2020-01-28 11:34 | 2020-01-28 12:46 | 72.25 | 1 | 1 | 72.25 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 13518 HOLLOW ROCK RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 168218 | 148397 | 6517 | 1353 | 8.3892e-05 | 1.1611e-06 | 72.25 | 1 | 310 | Customer | 59681 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010617 | PD-01282020-00286 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9921 | 829921 | 2020-01-28 11:41 | 2020-01-28 13:59 | 137.53 | 3 | 5 | 304.1 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 6710 NW.11 | CMI_NORMAL | NO | NO | NO | 861225 | 128814 | 116056 | 9233 | 1636 | 0.0003531 | 3.4834e-06 | 101.3667 | 1 | 310 | Load | 1282 | Load | Tran1phOH | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010618 | PD-01282020-00283 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-01-28 11:42 | 2020-01-28 13:20 | 97.52 | 1 | 1 | 97.5167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | HARRAH | LOT 27, BLK 1 WAGON TRAIL BLVD. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 114373 | 71193 | 11632 | 3534 | 0.00011323 | 1.1611e-06 | 97.5167 | 1 | 310 | Customer | 233638 | Load | Tran1phPad | STEVEN CASKEY | 405-777-8855 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010620 |  | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5431 | 865431 | 2020-01-28 12:04 | 2020-01-28 12:10 | 5.92 | 1 | 1 | 5.9167 | 1 | CANCELLED | 57 | CANCELLED | MOORE | NE 12 AND EASTERN AVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 159134 | 102160 | 9808 | 1377 | 6.8701e-06 | 1.1611e-06 | 5.9167 | 1 | 310 | Customer | 78188 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010621 | PD-01282020-00290 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3024 | 743024 | 2020-01-28 12:12 | 2020-01-28 12:43 | 31.42 | 1 | 1 | 31.4167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SHAWNEE | 109 E MAIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 114373 | 22107 | 6646 | 1640 | 3.6479e-05 | 1.1611e-06 | 31.4167 | 1 | 320 | Customer | 2203 | Load | Tran3phWye | BRYAN K TATUM | 405-659-0746 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010624 |  | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1931 | 851931 | 2020-01-28 12:26 | 2020-01-28 12:35 | 9.15 | 1 | 1 | 9.15 | 1 | CANCELLED | 57 | CANCELLED | SPENCER | 3424 N.SPENCER RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 114373 | 71193 | 12444 | 980 | 1.0624e-05 | 1.1611e-06 | 9.15 | 1 | 310 | Customer | 19808 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010626 | PD-01282020-00309 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6963 | 846963 | 2020-01-28 12:36 | 2020-01-28 14:23 | 106.58 | 1 | 1 | 106.5833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1/4E-BDWY EXT.5SS-SUMMIT RIDGE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 168218 | 148397 | 7724 | 1172 | 0.00012376 | 1.1611e-06 | 106.5833 | 1 | 310 | Customer | 69926 | Load | Tran1phPad | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010628 | PD-01282020-00312 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2135 | 822135 | 2020-01-28 12:41 | 2020-01-28 13:48 | 67.38 | 1 | 1 | 12.2671 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 1105 N SHAWNEE | CMI_NORMAL | NO | NO | NO | 861225 | 168218 | 148397 | 9250 | 426 | 1.4244e-05 | 1.1611e-06 | 12.2671 | 1 | 310 | Customer | 27822 | Load | TranOpenDelta | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2022
J2001.010631 |  | ARKANSAS | POTEAU | 3607:ROLAND ROAD | ROLAND_RD_721 | 360721 | 2020-01-28 12:52 | 2020-01-28 13:09 | 17.15 | 2 | 1 | 21.0667 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | SHADY GROVE | .5ME RLND RD HW64 | CMI_PLANNED | YES | NO | NO | 861225 | 82219 | 13487 | 1139 | 1139 | 2.4461e-05 | 2.3223e-06 | 10.5333 | 1 | 310 | Load | 6209 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | #N/A
J2001.010632 |  | NORTHWEST | WOODWARD | 4608:WOODWARD DISTR | WOODWARD_DIST_846 | 460846 | 2020-01-28 13:14 | 2020-01-28 13:14 | 0.27 | 653 | 0 | 174.1333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | WOODWARD | 204079 E COUNTY RD 44 | CMI_MOMENTARY | YES | NO | NO | 861225 | 53540 | 10424 | 1217 | 653 | 0.00020219 | 0.00075822 | 0.26667 | 1 | 0 | Feeder | WOODWD DIS_846 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-28 | 2020 |  | OK - 2020
J2001.010634 | PD-01282020-00322 | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3821 | 913821 | 2020-01-28 13:15 | 2020-01-28 15:10 | 114.68 | 1 | 2 | 114.6833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 319 S.9 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 82219 | 61186 | 2936 | 209 | 0.00013316 | 1.1611e-06 | 114.6833 | 1 | 320 | Customer | 7244 | Load | TranOH3phDelta | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-28 | 2020 |  | Ark - Series 2
J2001.010635 | PD-01282020-00332 | SOUTHERN | ARDMORE | 5117:MARIETTA | MARIETTA_1722 | 511722 | 2020-01-28 13:16 | 2020-01-28 14:03 | 47.27 | 3 | 2 | 136.85 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MARIETTA | CEMETARY RD | CMI_NORMAL | NO | NO | NO | 861225 | 77612 | 23588 | 1595 | 956 | 0.0001589 | 3.4834e-06 | 45.6167 | 1 | 310 | Load | 7322 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | #N/A
J2001.010636 | PD-01282020-00326 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9921 | 829921 | 2020-01-28 13:19 | 2020-01-28 14:18 | 58.88 | 1 | 1 | 7.2101 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | BETHANY | 6504 NW.22 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 128814 | 116056 | 9233 | 1636 | 8.372e-06 | 1.1611e-06 | 7.2101 | 1 | 310 | Customer | 23401 | Load | Tran1phOH | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010637 | PD-01282020-00327 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3022 | 743022 | 2020-01-28 13:20 | 2020-01-28 14:23 | 62.77 | 1 | 1 | 57.9667 | 12 | POOR CONNECTION | 50 | CONNECTOR | SHAWNEE | 521 N.CHAPMAN | CMI_NORMAL | NO | NO | NO | 861225 | 114373 | 22107 | 6646 | 2166 | 6.7307e-05 | 1.1611e-06 | 57.9667 | 1 | 320 | Customer | 2195 | Load | Tran1phOH | BRYAN K TATUM | 405-659-0746 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2020
J2001.010639 | PD-01282020-00353 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2135 | 822135 | 2020-01-28 13:29 | 2020-01-28 14:07 | 37.97 | 1 | 1 | 27.11 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3845 NW.10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 168218 | 148397 | 9250 | 426 | 3.1478e-05 | 1.1611e-06 | 27.11 | 1 | 310 | Customer | 4259 | Load | TranOpenDelta | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2022
J2001.010643 |  | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1222 | 911222 | 2020-01-28 13:38 | 2020-01-28 13:47 | 9.42 | 1 | 1 | 9.4167 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 811 S.18 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 82219 | 61186 | 6599 | 1289 | 1.0934e-05 | 1.1611e-06 | 9.4167 | 1 | 320 | Customer | 661 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | Ark - Series 1
J2001.010644 | PD-01282020-00357 | NORTHEAST | SAPULPA | 3218:BEGGS | BEGGS_1829 | 321829 | 2020-01-28 13:51 | 2020-01-28 14:54 | 62.52 | 1 | 1 | 59.75 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 21 | FUSE - TRANSFORMER | BEGGS | 1/4N OF 251ST ON HWY 75A WS | CMI_NORMAL | NO | NO | NO | 861225 | 74040 | 40772 | 1837 | 899 | 6.9378e-05 | 1.1611e-06 | 59.75 | 1 | 310 | Load | 20822 | Load | Tran1phOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2020
J2001.010646 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1022 | 541022 | 2020-01-28 14:01 | 2020-01-28 14:01 | 0 | 873 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MADILL | 12537 HIGHWAY 199 | CMI_MOMENTARY | YES | NO | NO | 861225 | 77612 | 7199 | 2379 | 873 | 0 | 0.0010137 | 0 | 1 | 0 | Feeder | GLASSES_1022 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010648 | PD-01282020-00369 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9929 | 829929 | 2020-01-28 14:03 | 2020-01-28 16:20 | 137.48 | 1 | 2 | 127.7 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 1200 N.OVERHOLSER | CMI_NORMAL | NO | NO | NO | 861225 | 128814 | 116056 | 9233 | 2208 | 0.00014828 | 1.1611e-06 | 127.7 | 1 | 320 | Customer | 15020 | Load | TranOpenDelta | STEVEN GILES | 405-227-2802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010652 | PD-01282020-00376 | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1022 | 541022 | 2020-01-28 14:08 | 2020-01-28 15:55 | 107.18 | 1 | 1 | 107.1833 | 4 | DETERIORATION | 18 | INSULATOR | MADILL | WS US70 @ SMILEY RD 600'' W FR ROADWAY | CMI_NORMAL | NO | NO | NO | 861225 | 77612 | 7199 | 2379 | 873 | 0.00012445 | 1.1611e-06 | 107.1833 | 1 | 320 | Load | 310148 | Load | Tran3phPadWye | MICHAEL D DICKINSON | 580-229-5532 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010655 | PD-01282020-00388 | ARKANSAS | POTEAU | 3506:CAVANAL MTN | CAVANAL MTN 21 | 350621 | 2020-01-28 14:14 | 2020-01-28 14:57 | 42.82 | 3 | 6 | 125.3 | 13 | PREMATURE FAILURE | 20 | FUSE BARREL | POTEAU | 1001 BROADWAY | CMI_NORMAL | NO | NO | NO | 861225 | 82219 | 13487 | 2052 | 707 | 0.00014549 | 3.4834e-06 | 41.7667 | 1 | 310 | Load | 10438 | Load | TranOpenDelta | TOBY C MEAD | 918-658-5596 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | #N/A
J2001.010659 | PD-01282020-00393 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1929 | 851929 | 2020-01-28 14:23 | 2020-01-28 15:09 | 46.1 | 3 | 4 | 135.05 | 4 | DETERIORATION | 20 | FUSE BARREL | MIDWEST CITY | 109 E.MEADOW LN | CMI_NORMAL | NO | NO | NO | 861225 | 114373 | 71193 | 12444 | 828 | 0.00015681 | 3.4834e-06 | 45.0167 | 1 | 310 | Load | 37556 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2022
J2001.010656 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9921 | 829921 | 2020-01-28 14:28 | 2020-01-28 15:04 | 35.85 | 1 | 1 | 35.85 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BETHANY | 6504 NW.22 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 128814 | 116056 | 9233 | 1636 | 4.1627e-05 | 1.1611e-06 | 35.85 | 1 | 310 | Customer | 23401 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010658 | PD-01282020-00407 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7021 | 817021 | 2020-01-28 14:28 | 2020-01-28 16:29 | 120.63 | 119 | 111 | 13381.55 | 4 | DETERIORATION | 17 | JUMPER | OKLAHOMA CITY | N/SW.62 + WALKER | CMI_NORMAL | NO | NO | NO | 861225 | 159134 | 102160 | 9937 | 1789 | 0.015538 | 0.00013818 | 112.45 | 1 | 310 | Mainline | 17597 | Fuse | FuseOH | CARL BILYEU | 405-820-9246 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010660 | PD-01282020-00395 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6961 | 846961 | 2020-01-28 14:37 | 2020-01-28 16:55 | 137.83 | 1387 | 765 | 119924.5 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | 401 NE 122ND ST | CMI_NORMAL | NO | NO | NO | 861225 | 168218 | 148397 | 7724 | 1388 | 0.13925 | 0.0016105 | 86.4632 | 1 | 310 | Feeder | MEMORIAL_6961 | Recloser | SubRecloser | SHAWN HILL | 405-308-1695 | [5 empty] | Equipment | N | SUBSTATION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010706 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6961 | 846961 | 2020-01-28 14:37 | 2020-01-28 14:55 | 18.1 | 1 | 0 | 18.1 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | 700 E.MEMORIAL | CMI_NORMAL | NO | NO | NO | 861225 | 168218 | 148397 | 7724 | 1388 | 2.1017e-05 | 1.1611e-06 | 18.1 | 1 | 0 | Customer | 85194 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010663 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_866 | 830866 | 2020-01-28 14:37 | 2020-01-28 15:19 | 42.22 | 7 | 13 | 228.6 | 22 | WIND | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | 1/2BS-NW.148 + LONGFORD WAY | CMI_NORMAL | NO | NO | NO | 861225 | 168218 | 148397 | 19378 | 4305 | 0.00026544 | 8.128e-06 | 32.6571 | 1 | 310 | Customer | 85398 | Load | Tran1phPad | Crew | [6 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010661 | PD-01282020-00406 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7024 | 817024 | 2020-01-28 14:40 | 2020-01-28 16:37 | 116.82 | 1 | 1 | 100.5833 | 12 | POOR CONNECTION | 17 | JUMPER | OKLAHOMA CITY | SW,62ND/ROBINSON | CMI_NORMAL | NO | NO | NO | 861225 | 159134 | 102160 | 9937 | 1751 | 0.00011679 | 1.1611e-06 | 100.5833 | 1 | 310 | Customer | 36080 | Load | Tran1phPad | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010665 | PD-01282020-00396 | METRO WEST | EL RENO | 8910:OKARCHE | OKARCHE_1021 | 891021 | 2020-01-28 14:43 | 2020-01-28 15:35 | 52.1 | 1 | 1 | 52.1 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKARCHE | 611 MEMORIAL DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 128814 | 12758 | 727 | 727 | 6.0495e-05 | 1.1611e-06 | 52.1 | 1 | 310 | Customer | 63714 | Load | Tran1phPad | MICHAEL T MAHEN | 405-210-6029 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | #N/A
J2001.010667 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6128 | 836128 | 2020-01-28 14:47 | 2020-01-28 15:08 | 20.97 | 1 | 1 | 20.9667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 408 NW 40TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 168218 | 148397 | 11126 | 959 | 2.4345e-05 | 1.1611e-06 | 20.9667 | 1 | 310 | Customer | 12329 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2021
J2001.010670 |  | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2731 | 872731 | 2020-01-28 14:52 | 2020-01-28 15:00 | 8.17 | 1 | 1 | 8.1667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 1001 N.BERRY RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 159134 | 56974 | 6464 | 1351 | 9.4826e-06 | 1.1611e-06 | 8.1667 | 1 | 310 | Customer | 44640 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010685 | PD-01282020-00417 | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6223 | 866223 | 2020-01-28 15:05 | 2020-01-28 17:16 | 130.75 | 1 | 1 | 116.0833 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | MIDWEST CITY | 1912 DEERWOOD TRAIL/WINDSONG | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861225 | 114373 | 71193 | 7210 | 2235 | 0.00013479 | 1.1611e-06 | 116.0833 | 1 | 310 | Customer | 82610 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010693 | PD-01282020-00430 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3024 | 743024 | 2020-01-28 15:18 | 2020-01-28 16:03 | 44.92 | 1 | 1 | 44.9167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SHAWNEE | 109 E MAIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 114373 | 22107 | 6646 | 1640 | 5.2154e-05 | 1.1611e-06 | 44.9167 | 1 | 310 | Customer | 2203 | Load | Tran3phWye | BRYAN K TATUM | 405-659-0746 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010694 |  | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4121 | 814121 | 2020-01-28 15:22 | 2020-01-28 15:33 | 10.65 | 1 | 1 | 10.65 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1020 SW.38 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 159134 | 102160 | 5808 | 1201 | 1.2366e-05 | 1.1611e-06 | 10.65 | 1 | 310 | Customer | 56048 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | #N/A
J2001.010698 | PD-01282020-00446 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1225 | 831225 | 2020-01-28 15:33 | 2020-01-28 16:44 | 70.87 | 1 | 1 | 70.8667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 3114 NW.50 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 168218 | 148397 | 7752 | 886 | 8.2286e-05 | 1.1611e-06 | 70.8667 | 1 | 320 | Customer | 1738 | Load | Tran1phOH | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2022
J2001.010699 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5922 | 835922 | 2020-01-28 15:34 | 2020-01-28 15:40 | 6.58 | 1 | 1 | 6.5833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | YUKON | 400 S.RANCHWOOD BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 128814 | 116056 | 6428 | 1638 | 7.6442e-06 | 1.1611e-06 | 6.5833 | 1 | 310 | Customer | 38784 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | #N/A
J2001.010700 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1022 | 541022 | 2020-01-28 15:36 | 2020-01-28 15:55 | 18.72 | 1 | 1 | 16.2667 | 4 | DETERIORATION | 18 | INSULATOR | MADILL | TALIAFERRO ACRES | CMI_NORMAL | NO | NO | NO | 861225 | 77612 | 7199 | 2379 | 873 | 1.8888e-05 | 1.1611e-06 | 16.2667 | 1 | 310 | Customer | 5605 | Load | Tran1phOH | MICHAEL D DICKINSON | 580-229-5532 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010703 | PD-01282020-00454 | METRO EAST | SEMINOLE | 7312:JUMPER CREEK | JUMPER_CREEK_1227 | 731227 | 2020-01-28 15:42 | 2020-01-28 18:05 | 142.7 | 1 | 1 | 27.8138 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | KONAWA | SE corner Stonebrook addition | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861225 | 114373 | 13608 | 1217 | 886 | 3.2296e-05 | 1.1611e-06 | 27.8138 | 1 | 320 | Customer | 331947 | Load | Tran1phOH | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | OK - 2021
J2001.010714 | PD-01282020-00472 | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5422 | 865422 | 2020-01-28 16:16 | 2020-01-28 17:21 | 64.88 | 1 | 1 | 64.8833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MOORE | 100 SE 19TH ST. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 159134 | 102160 | 9808 | 1158 | 7.5338e-05 | 1.1611e-06 | 64.8833 | 1 | 310 | Load | 383510 | Load | Tran3phWye | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010720 | PD-01282020-00479 | SOUTHERN | HEALDTON | 5306:COUNTY LINE | COUNTY LINE 21 | 530621 | 2020-01-28 16:33 | 2020-01-28 21:17 | 284.38 | 1 | 1 | 281.9833 | 5 | ELECTRICAL TRACKING | 27 | CUTOUT | RATLIFF CITY | CONTINENTAL RD/KNOB HILL RD .1W .2S .1W | CMI_NORMAL | NO | NO | NO | 861225 | 77612 | 6798 | 756 | 342 | 0.00032742 | 1.1611e-06 | 281.9833 | 1 | 310 | Load | 371128 | Load | Tran1phOH | MICHAEL D DICKINSON | 580-229-5532 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | #N/A
J2001.010719 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_866 | 830866 | 2020-01-28 16:33 | 2020-01-28 17:03 | 30.02 | 1 | 1 | 21.75 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | 1/2BS-NW.148 + LONGFORD WAY | CMI_NORMAL | NO | NO | NO | 861225 | 168218 | 148397 | 19378 | 4305 | 2.5255e-05 | 1.1611e-06 | 21.75 | 1 | 310 | Customer | 85398 | Load | Tran1phPad | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010725 | PD-01282020-00487 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1928 | 851928 | 2020-01-28 17:04 | 2020-01-28 18:32 | 87.67 | 1 | 1 | 87.6667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 9618 SE.6 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 114373 | 71193 | 12444 | 2018 | 0.00010179 | 1.1611e-06 | 87.6667 | 1 | 310 | Customer | 22392 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010724 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6961 | 846961 | 2020-01-28 17:04 | 2020-01-28 17:09 | 4.07 | 1 | 1 | 4.0667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | L3,B1-OAKMOND ADDN | CMI_MOMENTARY | YES | NO | NO | 861225 | 168218 | 148397 | 7724 | 1388 | 4.722e-06 | 1.1611e-06 | 4.0667 | 1 | 310 | Customer | 85946 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010726 | PD-01282020-00490 | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6224 | 866224 | 2020-01-28 17:08 | 2020-01-28 18:48 | 99.88 | 1 | 1 | 64.8 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 504 E.BELLEVIEW | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 114373 | 71193 | 7210 | 1781 | 7.5242e-05 | 1.1611e-06 | 64.8 | 1 | 310 | Customer | 8651 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010727 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6961 | 846961 | 2020-01-28 17:09 | 2020-01-28 17:12 | 3.5 | 1 | 1 | 3.5 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | LEE + 140,BLK 5 LOT N | CMI_MOMENTARY | YES | NO | NO | 861225 | 168218 | 148397 | 7724 | 1388 | 4.064e-06 | 1.1611e-06 | 3.5 | 1 | 310 | Customer | 69402 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010728 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6961 | 846961 | 2020-01-28 17:10 | 2020-01-28 17:14 | 3.48 | 1 | 1 | 3.4833 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 14204 GLEN OAKS PL | CMI_MOMENTARY | YES | NO | NO | 861225 | 168218 | 148397 | 7724 | 1388 | 4.0446e-06 | 1.1611e-06 | 3.4833 | 1 | 310 | Customer | 89751 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010730 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7021 | 817021 | 2020-01-28 17:18 | 2020-01-28 17:25 | 7.53 | 1 | 1 | 7.5333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7235 S.WALKER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 159134 | 102160 | 9937 | 1789 | 8.7472e-06 | 1.1611e-06 | 7.5333 | 1 | 310 | Customer | 46598 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010731 | PD-01282020-00492 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6024 | 836024 | 2020-01-28 17:19 | 2020-01-28 18:40 | 81.03 | 1 | 1 | 69.1667 | 12 | POOR CONNECTION | 50 | CONNECTOR | BETHANY | 8313 NW.37 | CMI_NORMAL | NO | NO | NO | 861225 | 128814 | 116056 | 5505 | 1342 | 8.0312e-05 | 1.1611e-06 | 69.1667 | 1 | 310 | Customer | 23641 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | OK - 2022
J2001.010734 | PD-01282020-00496 | SOUTHERN | DURANT | 5505:DURANT | DURANT 23 | 550523 | 2020-01-28 17:45 | 2020-01-28 18:47 | 61.63 | 1 | 1 | 61.6333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DURANT | 420 NE 5TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 77612 | 15491 | 1319 | 147 | 7.1565e-05 | 1.1611e-06 | 61.6333 | 1 | 310 | Customer | 7930 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010735 | PD-01282020-00493 | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5222 | 835222 | 2020-01-28 17:48 | 2020-01-28 19:15 | 86.6 | 1 | 1 | 86.6 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 3525 QUAIL CREEK RD | CMI_NORMAL | NO | NO | NO | 861225 | 168218 | 148397 | 6517 | 1353 | 0.00010055 | 1.1611e-06 | 86.6 | 1 | 320 | Customer | 23550 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010737 | PD-01282020-00495 | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_521 | 320521 | 2020-01-28 17:54 | 2020-01-28 20:00 | 125.92 | 1 | 1 | 125.9167 | 5 | ELECTRICAL TRACKING | 2 | TRANSFORMER OH | SAPULPA | 708 N.HICKORY | CMI_NORMAL | NO | NO | NO | 861225 | 74040 | 40772 | 3849 | 1610 | 0.00014621 | 1.1611e-06 | 125.9167 | 1 | 310 | Customer | 42679 | Load | Tran1phOH | JOSHUA N MCKINNEY | 918-863-6313 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | OK - 2022
J2001.010740 | PD-01282020-00498 | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_429 | 580429 | 2020-01-28 18:05 | 2020-01-28 20:42 | 157.17 | 21 | 12 | 3143 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | ADA | CC/18TH .25N ES | CMI_NORMAL | NO | NO | NO | 861225 | 77621 | 11516 | 3414 | 1343 | 0.0036495 | 2.4384e-05 | 149.6667 | 1 | 310 | Tap | 5874 | Fuse | FuseOH | CAMERON BRADY | 580-307-7052 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2021
J2001.010739 |  | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_429 | 580429 | 2020-01-28 18:06 | 2020-01-28 21:06 | 180.32 | 1 | 1 | 148.7167 | 29 | TREES : GROW IN | 37 | CONDUCTOR PRIMARY - OH | ADA | 400 S.CNTRY-CLB RD | CMI_NORMAL | NO | NO | NO | 861225 | 77621 | 11516 | 3414 | 1343 | 0.00017268 | 1.1611e-06 | 148.7167 | 1 | 310 | Customer | 16794 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2021
J2001.010745 |  | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_429 | 580429 | 2020-01-28 18:18 | 2020-01-28 21:06 | 168.02 | 2 | 2 | 273.5 | 29 | TREES : GROW IN | 37 | CONDUCTOR PRIMARY - OH | ADA | 2222 EAST 18TH | CMI_NORMAL | NO | NO | NO | 861225 | 77621 | 11516 | 3414 | 1343 | 0.00031757 | 2.3223e-06 | 136.75 | 1 | 310 | Secondary | 27438 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2021
J2001.010749 |  | ARKANSAS | POTEAU | 3607:ROLAND ROAD | ROLAND_RD_721 | 360721 | 2020-01-28 18:38 | 2020-01-28 18:48 | 9.42 | 1 | 1 | 9.4167 | 1 | CANCELLED | 57 | CANCELLED | ROLAND | WEST END OF ROLAND VILLAGE APT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 82241 | 13491 | 1139 | 1139 | 1.0934e-05 | 1.1611e-06 | 9.4167 | 1 | 310 | Customer | 16917 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | #N/A
J2001.010750 | PD-01282020-00500 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5134 | 815134 | 2020-01-28 18:40 | 2020-01-28 20:53 | 133.27 | 1 | 1 | 114.65 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 1008 SW.99 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861225 | 159155 | 102173 | 13938 | 2469 | 0.00013312 | 1.1611e-06 | 114.65 | 1 | 310 | Customer | 48890 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010751 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_863 | 830863 | 2020-01-28 18:51 | 2020-01-28 19:01 | 9.9 | 1 | 1 | 9.9 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | .5MW OF PENN + NW.142 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 168236 | 148411 | 19380 | 1673 | 1.1495e-05 | 1.1611e-06 | 9.9 | 1 | 310 | Customer | 69766 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010760 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_724 | 870724 | 2020-01-28 19:23 | 2020-01-28 19:29 | 5.93 | 1 | 1 | 5.9333 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 811 BILOXI DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 159155 | 56982 | 11834 | 2409 | 6.8894e-06 | 1.1611e-06 | 5.9333 | 1 | 310 | Customer | 46834 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010766 | PD-01282020-00505 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3724 | 833724 | 2020-01-28 19:29 | 2020-01-28 21:18 | 109.38 | 3 | 5 | 318.05 | 4 | DETERIORATION | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 6914 N CLASSEN BL | CMI_NORMAL | NO | NO | NO | 861225 | 168236 | 148411 | 5767 | 302 | 0.0003693 | 3.4834e-06 | 106.0167 | 1 | 310 | Secondary | 85031 | Load | TranOpenDelta | TONY J ILG | 405-714-7441 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010769 | PD-01282020-00506 | SOUTHERN | PAULS VALLEY | 5619:RUSH CREEK | RUSH_CREEK_1922 | 561922 | 2020-01-28 19:45 | 2020-01-28 21:05 | 80 | 1 | 1 | 52.0833 | 4 | DETERIORATION | 20 | FUSE BARREL | PAULS VALLEY | RT 2 BOX 88 | CMI_NORMAL | NO | NO | NO | 861225 | 77621 | 6209 | 2073 | 1193 | 6.0476e-05 | 1.1611e-06 | 52.0833 | 1 | 310 | Load | 5427 | Load | Tran1phOH | GARRID H BROWN | 405-207-3948 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | OK - 2021
J2001.010776 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-01-28 20:41 | 2020-01-28 21:02 | 20.45 | 1 | 1 | 20.45 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1326 NW.97 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 168236 | 148411 | 8788 | 1952 | 2.3745e-05 | 1.1611e-06 | 20.45 | 1 | 310 | Customer | 11651 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2021
J2001.010778 | PD-01282020-00515 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1231 | 831231 | 2020-01-28 20:43 | 2020-01-28 21:40 | 57.45 | 1 | 1 | 57.45 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NICHOLS HILLS | 6405 avondale dr | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 168236 | 148411 | 7752 | 467 | 6.6707e-05 | 1.1611e-06 | 57.45 | 1 | 310 | Customer | 383595 | Load | Tran3phPadWye | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | OK - 2022
J2001.010794 |  | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_861 | 550861 | 2020-01-28 22:44 | 2020-01-28 22:51 | 7.6 | 1 | 1 | 7.6 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DURANT | 203 HILLCREST HEIGHTS DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861225 | 77621 | 15496 | 1103 | 481 | 8.8246e-06 | 1.1611e-06 | 7.6 | 1 | 310 | Load | 305573 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010796 | PD-01282020-00518 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2627 | 862627 | 2020-01-28 22:56 | 2020-01-29 00:51 | 115.33 | 1 | 1 | 115.3333 | 13 | PREMATURE FAILURE | 15 | METER - SECONDARY | OKLAHOMA CITY | 5104 BROOKDALE DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861225 | 159155 | 102173 | 7417 | 2001 | 0.00013392 | 1.1611e-06 | 115.3333 | 1 | 320 | Customer | 39065 | Load | Tran1phPad | DARREN L STOCKTON | 918-777-1697 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-28 | 2020 |  | #N/A
J2001.010799 | PD-01282020-00519 | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_921 | 910921 | 2020-01-28 23:00 | 2020-01-29 03:29 | 268.12 | 206 | 101 | 51548.0667 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | FORT SMITH | COUNTRY CLUB AND HILAND | CMI_NORMAL | NO | NO | NO | 861225 | 82241 | 61204 | 5011 | 1427 | 0.059854 | 0.00023919 | 250.2333 | 1 | 310 | Mainline | 5042 | Fuse | FuseOH | LANCE M BECKER | 479-883-5087 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-28 | 2020 |  | Ark - Series 3
J2001.010822 | PD-01292020-00011 | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_621 | 880621 | 2020-01-29 01:49 | 2020-01-29 06:33 | 283.77 | 27 | 22 | 7497 | 5 | ELECTRICAL TRACKING | 39 | BUSHING | GUTHRIE | 3/4MN of Seward Road on | CMI_NORMAL | NO | NO | NO | 861225 | 168236 | 19825 | 5170 | 1878 | 0.008705 | 3.1351e-05 | 277.6667 | 1 | 310 | Mainline | 333612 | Fuse | FuseRiser | DERICK WINSETT | 405-650-6102 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010836 |  | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_621 | 880621 | 2020-01-29 06:02 | 2020-01-29 06:39 | 37.57 | 3 | 4 | 76 | 13 | PREMATURE FAILURE | 39 | BUSHING | GUTHRIE | Lot-39, Paddock Circle | CMI_PLANNED | YES | NO | NO | 861343 | 168236 | 19825 | 5170 | 1878 | 8.8234e-05 | 3.4829e-06 | 25.3333 | 1 | 310 | Load | 334053 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010842 |  | SOUTHERN | SULPHUR | 5712:JOLLYVILLE | JOLLYVILLE_1262 | 571262 | 2020-01-29 06:39 | 2020-01-29 06:39 | 0 | 110 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | DAVIS | E 1750 RD AND N 3310 RD | CMI_MOMENTARY | YES | NO | NO | 861343 | 77621 | 6812 | 372 | 110 | 0 | 0.00012771 | 0 | 1 | 0 | Feeder | JOLLYVIL_1262 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010844 | PD-01292020-00019 | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1371 | 831371 | 2020-01-29 06:40 | 2020-01-29 08:50 | 130.05 | 1 | 3 | 122.6 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | YUKON | 420 Frisco Ridge Rd | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861343 | 128835 | 116069 | 7900 | 3781 | 0.00014234 | 1.161e-06 | 122.6 | 1 | 310 | Customer | 376444 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010853 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2525 | 912525 | 2020-01-29 07:42 | 2020-01-29 08:18 | 35.8 | 1 | 1 | 23.05 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 5023 OLD-GREENWOOD | CMI_PLANNED | YES | NO | NO | 861343 | 82241 | 61204 | 2735 | 198 | 2.6761e-05 | 1.161e-06 | 23.05 | 1 | 308 | Load | 17236 | Load | Tran3phWye | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | Ark - Series 2
J2001.010859 | PD-01292020-00029 | METRO WEST | WEST | 8222:CZECH HALL | CZECH_HALL_2221 | 822221 | 2020-01-29 08:03 | 2020-01-29 09:57 | 113.68 | 1 | 2 | 103.75 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 108 HICKORY HILL ST | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861343 | 128835 | 116069 | 8607 | 1892 | 0.00012045 | 1.161e-06 | 103.75 | 1 | 310 | Customer | 58659 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010856 |  | NORTHEAST | MUSKOGEE | 3313:ILLINOIS RIVER | ILLINOIS_RIVER_1321 | 331321 | 2020-01-29 08:04 | 2020-01-29 13:29 | 325.22 | 1 | 0 | 319.2667 | 4 | DETERIORATION | 28 | CROSSARM | WEBBERS FALLS | HWY64 & ARK RVR BRDG | CMI_PLANNED | YES | NO | NO | 861343 | 74054 | 33273 | 791 | 791 | 0.00037066 | 1.161e-06 | 319.2667 | 1 | 0 | Tap | 19527 | Fuse | FuseRiser | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | OK - 2020
J2001.010857 | PD-01292020-00036 | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_622 | 770622 | 2020-01-29 08:05 | 2020-01-29 09:10 | 65.17 | 1 | 1 | 68.2856 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | BRISTOW | 4N 2E BRISTOW | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 74054 | 40781 | 3783 | 2010 | 7.9278e-05 | 1.161e-06 | 68.2856 | 1 | 310 | Customer | 48317 | Load | Tran1phOH | GREGORY R HOOVER | 918-261-6803 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | #N/A
J2001.010860 |  | ARKANSAS | POTEAU | 3607:ROLAND ROAD | ROLAND_RD_721 | 360721 | 2020-01-29 08:06 | 2020-01-29 08:24 | 17.53 | 1 | 1 | 17.5333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ROLAND | WEST END OF ROLAND VILLAGE APT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 82241 | 13491 | 1139 | 1139 | 2.0356e-05 | 1.161e-06 | 17.5333 | 1 | 310 | Customer | 16917 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | #N/A
J2001.010862 | PD-01292020-00034 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3722 | 833722 | 2020-01-29 08:14 | 2020-01-29 15:07 | 413.13 | 1 | 1 | 391.0333 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | NICHOLS HILLS | 6721 AVONDALE DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861343 | 168236 | 148411 | 5767 | 1111 | 0.00045398 | 1.161e-06 | 391.0333 | 1 | 310 | Customer | 8962 | Load | TranOpenDelta | KAEL GUTHERY | 405-428-1818 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | OK - 2022
J2001.010865 | PD-01292020-00045 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3925 | 833925 | 2020-01-29 08:20 | 2020-01-29 09:34 | 74.48 | 1 | 1 | 74.4833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | WARR ACRES | 6117 NW.57 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 168236 | 148411 | 7852 | 2183 | 8.6473e-05 | 1.161e-06 | 74.4833 | 1 | 310 | Customer | 12346 | Load | Tran1phOH | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | OK - 2022
J2001.011009 | PD-01292020-00046 | METRO EAST | SHAWNEE | 7433:ROCK CREEK | ROCK_CREEK_3322 | 743322 | 2020-01-29 08:24 | 2020-01-29 15:51 | 447.38 | 33 | 3 | 13561.35 | 4 | DETERIORATION | 8 | SPLICE - UG | SHAWNEE | 1810 N.HARRISON | CMI_PLANNED | YES | NO | NO | 861343 | 114393 | 22111 | 1802 | 1034 | 0.015744 | 3.8312e-05 | 410.95 | 1 | 310 | Load | 12620 | Load | Tran1phPad | JEREMIAH D WALKER | 405-974-0464 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010868 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-01-29 08:29 | 2020-01-29 12:51 | 262.1 | 2 | 2 | 499.9167 | 4 | DETERIORATION | 12 | POLE | POCOLA | STANDFIELD RD | CMI_PLANNED | YES | NO | NO | 861343 | 82241 | 61204 | 1457 | 1239 | 0.00058039 | 2.322e-06 | 249.9583 | 1 | 308 | Load | 13925 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | Ark - Series 2
J2001.010869 | PD-01292020-00051 | METRO EAST | CHANDLER | 7119:WARWICK | WARWICK_1941 | 711941 | 2020-01-29 08:30 | 2020-01-29 09:51 | 81.27 | 1 | 2 | 70.5 | 12 | POOR CONNECTION | 50 | CONNECTOR | WELLSTON | BOX 56 | CMI_NORMAL | NO | NO | NO | 861343 | 114393 | 7467 | 2420 | 1463 | 8.1849e-05 | 1.161e-06 | 70.5 | 1 | 320 | Customer | 3931 | Load | Tran1phOH | SCOTT C PERRY | 405-258-6044 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | OK - 2021
J2001.010876 | PD-01292020-00056 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3628 | 833628 | 2020-01-29 08:36 | 2020-01-29 09:12 | 35.68 | 1 | 1 | 35.6833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 11500 N.MAY AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 168236 | 148411 | 8788 | 1312 | 4.1428e-05 | 1.161e-06 | 35.6833 | 1 | 310 | Customer | 69117 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010874 | PD-01292020-00057 | METRO WEST | WEST | 8323:RICHARDS | RICHARDS_2323 | 832323 | 2020-01-29 08:36 | 2020-01-29 09:10 | 33.62 | 1 | 1 | 7.4447 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 10608 N. COUNCIL - WS BLDG. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 128835 | 116069 | 5020 | 1671 | 8.6431e-06 | 1.161e-06 | 7.4447 | 1 | 310 | Customer | 73431 | Load | Tran1phPad | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010875 | PD-01292020-00059 | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6224 | 866224 | 2020-01-29 08:37 | 2020-01-29 09:13 | 36.02 | 1 | 1 | 36.0167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 1116 lynn fry blvd | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 114393 | 71203 | 7212 | 1781 | 4.1815e-05 | 1.161e-06 | 36.0167 | 1 | 310 | Customer | 72053 | Load | Tran1phPad | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010879 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-01-29 08:41 | 2020-01-29 14:00 | 319.35 | 10 | 9 | 3070.1667 | 4 | DETERIORATION | 12 | POLE | BIXBY | 119 E NEEDLES | CMI_PLANNED | YES | NO | NO | 861343 | 74054 | 40781 | 2752 | 1440 | 0.0035644 | 1.161e-05 | 307.0167 | 1 | 310 | Load | 40102 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | OK - 2021
J2001.010880 |  | NORTHEAST | SAPULPA | 3216:BEELINE | BEELINE_1628 | 321628 | 2020-01-29 08:47 | 2020-01-29 14:52 | 365.35 | 1 | 1 | 42.7833 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | GLENPOOL | 13910 SO ELWOOD | CMI_PLANNED | YES | NO | NO | 861343 | 74054 | 40781 | 5565 | 1445 | 4.967e-05 | 1.161e-06 | 42.7833 | 1 | 308 | Load | 46602 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010884 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-01-29 08:56 | 2020-01-29 13:10 | 254 | 3 | 1 | 762 | 4 | DETERIORATION | 2 | TRANSFORMER OH | NORMAN | 1351 E. Indian Hills | CMI_PLANNED | YES | NO | NO | 861343 | 159155 | 56982 | 4239 | 3070 | 0.00088466 | 3.4829e-06 | 254 | 1 | 308 | Load | 258999 | Load | Tran3phWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010885 |  | SOUTHERN | DURANT | 5505:DURANT | DURANT 22 | 550522 | 2020-01-29 09:02 | 2020-01-29 13:06 | 244.03 | 10 | 9 | 1963.1667 | 4 | DETERIORATION | 12 | POLE | DURANT | 1/2 BLOCK E OF 18TH ON SMITH | CMI_PLANNED | YES | NO | NO | 861343 | 77621 | 15496 | 1319 | 799 | 0.0022792 | 1.161e-05 | 196.3167 | 1 | 310 | Load | 15863 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010889 |  | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-01-29 09:05 | 2020-01-29 09:15 | 10.12 | 1 | 1 | 10.1167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2808 SW.41 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 159155 | 102173 | 7607 | 2461 | 1.1745e-05 | 1.161e-06 | 10.1167 | 1 | 310 | Customer | 38040 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | #N/A
J2001.010890 | PD-01292020-00085 | METRO EAST | SHAWNEE | 7407:REMINGTON | REMINGTON 22 | 740722 | 2020-01-29 09:08 | 2020-01-29 10:13 | 65.23 | 1 | 1 | 65.2333 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | SHAWNEE | 1810 N.HARRISON | CMI_NORMAL | NO | NO | NO | 861343 | 114393 | 22111 | 3667 | 1645 | 7.5734e-05 | 1.161e-06 | 65.2333 | 1 | 310 | Customer | 12619 | Load | Tran1phPad | BRYAN K TATUM | 405-659-0746 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | #N/A
J2001.010891 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-01-29 09:10 | 2020-01-29 10:27 | 77.03 | 12 | 10 | 844.8 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | CHARLESTON | VINE + N. 6 ST | CMI_PLANNED | YES | NO | NO | 861343 | 82241 | 61204 | 960 | 490 | 0.00098079 | 1.3932e-05 | 70.4 | 1 | 308 | Mainline | 1500 | Fuse | FuseRiser | [7 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-01-29 | 2020 |  | Ark - Series 2
J2001.010893 | PD-01292020-00106 | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1222 | 911222 | 2020-01-29 09:10 | 2020-01-29 10:07 | 56.57 | 1 | 1 | 56.5667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 820 S.17 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 82241 | 61204 | 6599 | 1288 | 6.5673e-05 | 1.161e-06 | 56.5667 | 1 | 310 | Customer | 13702 | Load | Tran1phPad | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | Ark - Series 1
J2001.010894 |  | NORTHWEST | ENID | 4240:DEER CREEK | DEER CREEK 48 | 424048 | 2020-01-29 09:13 | 2020-01-29 12:42 | 209.3 | 1 | 1 | 204.7 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | LAMONT | 2W,2.5S-LAMONT | CMI_PLANNED | YES | NO | NO | 861343 | 53549 | 37601 | 621 | 476 | 0.00023765 | 1.161e-06 | 204.7 | 1 | 308 | Tap | 2927 | Fuse | FuseOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | #N/A
J2001.010898 | PD-01292020-00096 | METRO NORTH | NORTH | 8209:CLASSEN | CLASSEN_961 | 820961 | 2020-01-29 09:16 | 2020-01-29 10:17 | 61.38 | 1 | 1 | 54.55 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 1212 NW.3 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861343 | 168236 | 148411 | 3885 | 868 | 6.3331e-05 | 1.161e-06 | 54.55 | 1 | 310 | Customer | 22290 | Load | TranOpenDelta | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010900 |  | SOUTHERN | SULPHUR | 5712:JOLLYVILLE | JOLLYVILLE_1262 | 571262 | 2020-01-29 09:24 | 2020-01-29 09:24 | 0.03 | 110 | 0 | 3.6667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | DAVIS | E 1750 RD AND N 3310 RD | CMI_MOMENTARY | YES | NO | NO | 861343 | 77621 | 6812 | 372 | 110 | 4.2569e-06 | 0.00012771 | 0.033333 | 1 | 0 | Feeder | JOLLYVIL_1262 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010904 | PD-01292020-00111 | METRO SOUTH | SOUTH CENTRAL | 8194:WESTMOORE | WESTMOORE_9429 | 819429 | 2020-01-29 09:31 | 2020-01-29 11:42 | 131.47 | 1 | 1 | 128.6833 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | SW 119th & Meridian Av | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861343 | 159155 | 102173 | 8103 | 1133 | 0.0001494 | 1.161e-06 | 128.6833 | 1 | 320 | Customer | 371041 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010908 | PD-01292020-00115 | METRO EAST | EAST | 8685:TINKER FIELD 4 | TINKER_4_8526 | 868526 | 2020-01-29 09:38 | 2020-01-29 09:43 | 5.23 | 1 | 1 | 5.2333 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | South of Bldg 11 - North of 5th Av | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 114393 | 71203 | 184 | 14 | 6.0758e-06 | 1.161e-06 | 5.2333 | 1 | 310 | Load | 344555 | Load | Tran3phPadWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010911 | PD-01292020-00150 | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1721 | 911721 | 2020-01-29 09:40 | 2020-01-29 10:58 | 78.45 | 2 | 3 | 152.3333 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | FORT SMITH | 9109 S.ZERO | CMI_NORMAL | NO | NO | NO | 861343 | 82241 | 61204 | 4241 | 209 | 0.00017686 | 2.322e-06 | 76.1667 | 1 | 310 | Load | 18533 | Load | Tran1phOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-01-29 | 2020 |  | #N/A
J2001.010912 | PD-01292020-00118 | METRO EAST | EAST | 8687:TINKER FIELD 5 | TINKER_5_8737 | 868737 | 2020-01-29 09:49 | 2020-01-29 11:06 | 77.32 | 33 | 13 | 2551.45 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | S DOUGLAS BLVD + SE 49TH ST | CMI_NORMAL | NO | NO | NO | 861343 | 114393 | 71203 | 130 | 0 | 0.0029622 | 3.8312e-05 | 77.3167 | 1 | 310 | Feeder | TINKER5_8721ML | Breaker | SubRecloser | [7 empty] | Equipment | N | SUBSTATION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010923 | PD-01292020-00137 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7021 | 817021 | 2020-01-29 09:59 | 2020-01-29 10:20 | 21.27 | 1 | 1 | 6.2115 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7235 S.WALKER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 159155 | 102173 | 9937 | 1789 | 7.2114e-06 | 1.161e-06 | 6.2115 | 1 | 310 | Customer | 46598 | Load | Tran1phPad | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010932 |  | METRO WEST | WEST | 8335:BETHANY | BETHANY_3526 | 833526 | 2020-01-29 10:16 | 2020-01-29 10:54 | 37.13 | 1 | 2 | 26.1833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | WARR ACRES | 6035 NW.50 | CMI_PLANNED | YES | NO | NO | 861343 | 128835 | 116069 | 7871 | 2061 | 3.0398e-05 | 1.161e-06 | 26.1833 | 1 | 310 | Load | 38128 | Load | TranOpenDelta | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | #N/A
J2001.010928 | PD-01292020-00155 | METRO SOUTH | SOUTH | 8726:NOBLE | NOBLE_2621 | 872621 | 2020-01-29 10:21 | 2020-01-29 12:04 | 102.55 | 1 | 2 | 99.9 | 4 | DETERIORATION | 50 | CONNECTOR | NOBLE | 506 N.7 | CMI_NORMAL | NO | NO | NO | 861343 | 159155 | 56982 | 2969 | 1448 | 0.00011598 | 1.161e-06 | 99.9 | 1 | 310 | Customer | 46117 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010929 | PD-01292020-00151 | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4529 | 824529 | 2020-01-29 10:22 | 2020-01-29 13:48 | 206 | 1 | 1 | 11.2263 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 8621 SW.2 | CMI_NORMAL | NO | NO | NO | 861343 | 128835 | 116069 | 3409 | 256 | 1.3033e-05 | 1.161e-06 | 11.2263 | 1 | 320 | Customer | 65427 | Load | TranOpenDelta | GARY D FRANKLIN | 405-637-2002 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010930 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-29 10:24 | 2020-01-29 12:02 | 98.57 | 1 | 1 | 88.3667 | 4 | DETERIORATION | 12 | POLE | LAVACA | RIVER ROAD SOF BARB.LN | CMI_PLANNED | YES | NO | NO | 861343 | 82241 | 61204 | 2735 | 2123 | 0.00010259 | 1.161e-06 | 88.3667 | 1 | 308 | Tap | 6995 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | Ark - Series 2
J2001.010933 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-29 10:28 | 2020-01-29 12:15 | 107.32 | 33 | 2 | 3204.3 | 4 | DETERIORATION | 23 | FUSE - PRIMARY | ALMA | W 71 + N OF HWY 282 | CMI_PLANNED | YES | NO | NO | 861343 | 82241 | 61204 | 3791 | 2586 | 0.0037201 | 3.8312e-05 | 97.1 | 1 | 310 | Mainline | 6942 | Fuse | FuseRiser | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-29 | 2020 |  | Ark - Series 2
J2001.010934 |  | METRO SOUTH | SOUTH | 8726:NOBLE | NOBLE_2621 | 872621 | 2020-01-29 10:28 | 2020-01-29 10:59 | 31.07 | 11 | 0 | 341.9069 | 4 | DETERIORATION | 12 | POLE | NOBLE | FRONT,CHESTNUT | CMI_PLANNED | YES | NO | NO | 861343 | 159155 | 56982 | 2969 | 1448 | 0.00039695 | 1.2771e-05 | 31.0825 | 1 | 0 | Mainline | 12270 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010938 | PD-01292020-00161 | METRO WEST | WEST | 8158:SARA | SARA_5871 | 815871 | 2020-01-29 10:31 | 2020-01-29 10:57 | 25.95 | 1 | 1 | 25.95 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | Mustang Drive & Mustang Rd Mustang Creek Apts | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 128835 | 116069 | 18252 | 5398 | 3.0127e-05 | 1.161e-06 | 25.95 | 1 | 310 | Customer | 238499 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | OK - 2022
J2001.010941 | PD-01292020-00167 | ARKANSAS | POTEAU | 3607:ROLAND ROAD | ROLAND_RD_721 | 360721 | 2020-01-29 10:40 | 2020-01-29 12:01 | 80.67 | 1 | 1 | 80.6667 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | ROLAND | WEST END OF ROLAND VILLAGE APT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 82241 | 13491 | 1139 | 1139 | 9.3652e-05 | 1.161e-06 | 80.6667 | 1 | 310 | Customer | 16917 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | #N/A
J2001.010946 | PD-01292020-00187 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-29 10:43 | 2020-01-29 11:33 | 49.53 | 44 | 20 | 1956.5333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ALMA | 71 @ HL 2/18 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 82241 | 61204 | 3791 | 2586 | 0.0022715 | 5.1083e-05 | 44.4667 | 1 | 310 | Tap | 4384 | Fuse | FuseOH | KRIS L HALMES | 479-430-9447 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-29 | 2020 |  | Ark - Series 2
J2001.010945 |  | METRO SOUTH | SOUTH | 8726:NOBLE | NOBLE_2621 | 872621 | 2020-01-29 10:49 | 2020-01-29 12:39 | 110.37 | 91 | 61 | 8259.7667 | 4 | DETERIORATION | 12 | POLE | NOBLE | 2ND,CHESTNUT | CMI_PLANNED | YES | NO | NO | 861343 | 159155 | 56982 | 2969 | 1448 | 0.0095894 | 0.00010565 | 90.7667 | 1 | 310 | Mainline | 22000 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010944 | PD-01292020-00176 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5123 | 815123 | 2020-01-29 10:50 | 2020-01-29 11:22 | 31.98 | 1 | 1 | 7.5971 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 8101 S.WESTERN BLDG 8 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 159155 | 102173 | 13938 | 1323 | 8.8201e-06 | 1.161e-06 | 7.5971 | 1 | 310 | Customer | 74606 | Load | Tran3phWye | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010956 | PD-01292020-00193 | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1731 | 831731 | 2020-01-29 11:17 | 2020-01-29 11:48 | 30.68 | 1 | 1 | 30.6833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2600 TEALWOOD DR BLDG 2 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 168236 | 148411 | 6646 | 2017 | 3.5623e-05 | 1.161e-06 | 30.6833 | 1 | 310 | Customer | 69469 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011008 |  | NORTHEAST | MUSKOGEE | 3109:HONOR HEIGHTS | HONOR_HEIGHTS_921 | 310921 | 2020-01-29 11:26 | 2020-01-29 13:50 | 143.97 | 12 | 8 | 1303.2 | 1 | CANCELLED | 57 | CANCELLED | MUSKOGEE | kershaw circle,east lane | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 74054 | 33273 | 1178 | 1156 | 0.001513 | 1.3932e-05 | 108.6 | 1 | 310 | Mainline | 222787 | Fuse | FuseOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | OK - 2020
J2001.010961 |  | NORTHEAST | MUSKOGEE | 3109:HONOR HEIGHTS | HONOR_HEIGHTS_921 | 310921 | 2020-01-29 11:26 | 2020-01-29 13:50 | 143.97 | 13 | 9 | 1373.45 | 4 | DETERIORATION | 12 | POLE | MUSKOGEE | 0 | CMI_PLANNED | YES | NO | NO | 861343 | 74054 | 33273 | 1178 | 1156 | 0.0015945 | 1.5093e-05 | 105.65 | 1 | 310 | Mainline |  | 0 | 0 | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | OK - 2020
J2001.010963 | PD-01292020-00205 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7021 | 817021 | 2020-01-29 11:34 | 2020-01-29 11:59 | 25.38 | 1 | 1 | 25.3833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7235 S.WALKER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 159155 | 102173 | 9937 | 1789 | 2.9469e-05 | 1.161e-06 | 25.3833 | 1 | 310 | Customer | 46598 | Load | Tran1phPad | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010964 | PD-01292020-00207 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4124 | 814124 | 2020-01-29 11:34 | 2020-01-29 12:16 | 41.85 | 1 | 1 | 27.5134 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 4221 S HARVEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 159155 | 102173 | 5808 | 2013 | 3.1942e-05 | 1.161e-06 | 27.5134 | 1 | 310 | Customer | 33280 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | #N/A
J2001.010968 |  | NORTHEAST | MUSKOGEE | 3109:HONOR HEIGHTS | HONOR_HEIGHTS_921 | 310921 | 2020-01-29 11:47 | 2020-01-29 12:33 | 45.48 | 1 | 1 | 45.4833 | 1 | CANCELLED | 57 | CANCELLED | MUSKOGEE | 5028 W.OKMULGEE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 74054 | 33273 | 1178 | 1156 | 5.2805e-05 | 1.161e-06 | 45.4833 | 1 | 310 | Customer | 5019 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | OK - 2020
J2001.010973 |  | METRO SOUTH | SOUTH | 8709:LITTLE R LAKE | LITTLE_RIVER_L_921 | 870921 | 2020-01-29 11:51 | 2020-01-29 13:05 | 73.55 | 1 | 0 | 61.9167 | 4 | DETERIORATION | 2 | TRANSFORMER OH | NORMAN | 3120 ISIM RD | CMI_PLANNED | YES | NO | NO | 861343 | 159155 | 56982 | 673 | 673 | 7.1884e-05 | 1.161e-06 | 61.9167 | 1 | 0 | Load | 56648 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | #N/A
J2001.010976 |  | METRO SOUTH | SOUTH | 8726:NOBLE | NOBLE_2621 | 872621 | 2020-01-29 11:57 | 2020-01-29 13:25 | 88.22 | 1 | 1 | 22.2667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NOBLE | 3BN 1E OF BANK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 159155 | 56982 | 2969 | 1448 | 2.5851e-05 | 1.161e-06 | 22.2667 | 1 | 310 | Customer | 31562 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010986 | PD-01292020-00234 | METRO NORTH | NORTH | 8209:CLASSEN | CLASSEN_923 | 820923 | 2020-01-29 12:01 | 2020-01-29 12:39 | 38.15 | 9 | 8 | 244.2 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1608 NW.11 | CMI_NORMAL | NO | NO | NO | 861343 | 168236 | 148411 | 3885 | 1148 | 0.00028351 | 1.0449e-05 | 27.1333 | 1 | 310 | Load | 27314 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010979 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-29 12:03 | 2020-01-29 14:51 | 168.4 | 5 | 3 | 424.0833 | 4 | DETERIORATION | 12 | POLE | ARKOMA | 430 CHOCTAW | CMI_PLANNED | YES | NO | NO | 861343 | 82241 | 61204 | 2938 | 876 | 0.00049235 | 5.8049e-06 | 84.8167 | 1 | 308 | Load | 4831 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-29 | 2020 |  | Ark - Series 2
J2001.010981 | PD-01292020-00308 | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-01-29 12:07 | 2020-01-29 16:04 | 237.48 | 2 | 3 | 460.2833 | 23 | CUSTOMER EQUIPMENT | 27 | CUTOUT | BIXBY | 318 N MONTGOMERY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 74054 | 40781 | 2752 | 1440 | 0.00053438 | 2.322e-06 | 230.1417 | 1 | 310 | Secondary | 42455 | Load | TranOpenDelta | JOSHUA N MCKINNEY | 918-863-6313 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | OK - 2021
J2001.010984 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-01-29 12:14 | 2020-01-29 14:00 | 106.62 | 12 | 11 | 1173 | 4 | DETERIORATION | 12 | POLE | BIXBY | 221 E NEEDLES | CMI_PLANNED | YES | NO | NO | 861343 | 74054 | 40781 | 2752 | 1440 | 0.0013618 | 1.3932e-05 | 97.75 | 1 | 310 | Load | 43621 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | OK - 2021
J2001.010985 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-01-29 12:15 | 2020-01-29 13:22 | 66.92 | 3 | 2 | 189.95 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | 0 | CMI_PLANNED | YES | NO | NO | 861343 | 159155 | 56982 | 4239 | 1005 | 0.00022053 | 3.4829e-06 | 63.3167 | 1 | 308 | Mainline |  | 0 | 0 | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.010991 | PD-01292020-00263 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-29 12:25 | 2020-01-29 13:48 | 82.73 | 1 | 1 | 56.3167 | 12 | POOR CONNECTION | 50 | CONNECTOR | MOUNTAINBURG | 7022 MOTE RD | CMI_NORMAL | NO | NO | NO | 861343 | 82241 | 61204 | 3791 | 2586 | 6.5382e-05 | 1.161e-06 | 56.3167 | 1 | 310 | Load | 15856 | Load | Tran1phOH | KRIS L HALMES | 479-430-9447 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-29 | 2020 |  | Ark - Series 2
J2001.011001 |  | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-01-29 12:40 | 2020-01-29 12:58 | 18.7 | 1 | 1 | 18.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2808 SW.41 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 159155 | 102173 | 7607 | 2461 | 2.171e-05 | 1.161e-06 | 18.7 | 1 | 310 | Customer | 38040 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | #N/A
J2001.011002 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-29 12:42 | 2020-01-29 14:44 | 121.67 | 1 | 2 | 58.7759 | 4 | DETERIORATION | 2 | TRANSFORMER OH | ALMA | 8278 Hwy 282 | CMI_PLANNED | YES | NO | NO | 861343 | 82241 | 61204 | 3791 | 2586 | 6.8237e-05 | 1.161e-06 | 58.7759 | 1 | 310 | Load | 406043 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-29 | 2020 |  | Ark - Series 2
J2001.011004 | PD-01292020-00250 | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5629 | 865629 | 2020-01-29 12:43 | 2020-01-29 14:36 | 112.53 | 1 | 1 | 91.2 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 5920 S.STEVE AV | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861343 | 159155 | 102173 | 2755 | 734 | 0.00010588 | 1.161e-06 | 91.2 | 1 | 320 | Customer | 36111 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011007 | PD-01292020-00255 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1928 | 851928 | 2020-01-29 12:44 | 2020-01-29 14:32 | 107.57 | 1 | 1 | 107.5667 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | MIDWEST CITY | 3421 PARKWOOD LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 114393 | 71203 | 12446 | 2018 | 0.00012488 | 1.161e-06 | 107.5667 | 1 | 310 | Customer | 13144 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011011 |  | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6523 | 836523 | 2020-01-29 12:57 | 2020-01-29 13:24 | 26.8 | 1 | 1 | 21.2333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 3/8ME-ROCKWELL,1/2MN-63RD | CMI_PLANNED | YES | NO | NO | 861343 | 128835 | 116069 | 7422 | 2257 | 2.4651e-05 | 1.161e-06 | 21.2333 | 1 | 308 | Load | 42929 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | OK - 2022
J2001.011012 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3829 | 913829 | 2020-01-29 13:00 | 2020-01-29 14:06 | 65.88 | 16 | 15 | 892.2667 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | FORT SMITH | S.-DODSON AV. W.-S.17 | CMI_PLANNED | YES | NO | NO | 861343 | 82241 | 61204 | 2938 | 1186 | 0.0010359 | 1.8576e-05 | 55.7667 | 1 | 308 | Mainline | 3391 | Fuse | FuseRiser | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-29 | 2020 |  | Ark - Series 2
J2001.011015 | PD-01292020-00269 | METRO WEST | WEST | 8158:SARA | SARA_5871 | 815871 | 2020-01-29 13:12 | 2020-01-29 13:51 | 39.42 | 1 | 1 | 18.2154 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 11013 SW 39TH CT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 128835 | 116069 | 18252 | 5398 | 2.1148e-05 | 1.161e-06 | 18.2154 | 1 | 310 | Customer | 301114 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | OK - 2022
J2001.011019 | PD-01292020-00283 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2123 | 822123 | 2020-01-29 13:24 | 2020-01-29 14:04 | 40.43 | 1 | 1 | 19.1037 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1133 N.META | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 168236 | 148411 | 9250 | 1667 | 2.2179e-05 | 1.161e-06 | 19.1037 | 1 | 320 | Customer | 6196 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | OK - 2020
J2001.011024 | PD-01292020-00297 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1924 | 851924 | 2020-01-29 13:33 | 2020-01-29 15:08 | 94.88 | 1 | 1 | 94.8833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 9100 JENNIFER PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 114393 | 71203 | 12446 | 1608 | 0.00011016 | 1.161e-06 | 94.8833 | 1 | 310 | Customer | 24517 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011023 |  | NORTHEAST | SAPULPA | 3210:HICKORY HILL | HICKORY_HILL_1024 | 321024 | 2020-01-29 13:34 | 2020-01-29 15:09 | 95.87 | 8 | 7 | 231.8667 | 4 | DETERIORATION | 27 | CUTOUT | SAPULPA | 1002 E.COURTNEY | CMI_PLANNED | YES | NO | NO | 861343 | 74054 | 40781 | 2684 | 1247 | 0.00026919 | 9.2878e-06 | 28.9833 | 1 | 308 | Load | 47085 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | OK - 2022
J2001.011031 |  | NORTHEAST | SAPULPA | 3210:HICKORY HILL | HICKORY_HILL_1024 | 321024 | 2020-01-29 13:39 | 2020-01-29 14:48 | 68.73 | 7 | 6 | 164.85 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SAPULPA | 1014 E.COURTNEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 74054 | 40781 | 2684 | 1247 | 0.00019139 | 8.1268e-06 | 23.55 | 1 | 310 | Load | 47087 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | OK - 2022
J2001.011029 |  | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1935 | 851935 | 2020-01-29 13:45 | 2020-01-29 14:02 | 17.18 | 1 | 1 | 17.1833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 1412A N.MIDWEST BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 114393 | 71203 | 12446 | 2158 | 1.9949e-05 | 1.161e-06 | 17.1833 | 1 | 310 | Customer | 37623 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011030 | PD-01292020-00307 | METRO EAST | CHANDLER | 7119:WARWICK | WARWICK_1942 | 711942 | 2020-01-29 13:48 | 2020-01-29 16:46 | 178.48 | 1 | 1 | 179.2274 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | TRYON | DAIRY FREEZE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 114393 | 7467 | 2420 | 957 | 0.00020808 | 1.161e-06 | 179.2274 | 1 | 310 | Customer | 10386 | Load | Tran1phOH | GREGORY R HOOVER | 918-261-6803 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | OK - 2022
J2001.011032 | PD-01292020-00301 | METRO WEST | WEST | 8359:YUKON | YUKON_5921 | 835921 | 2020-01-29 13:49 | 2020-01-29 14:22 | 32.68 | 1 | 1 | 6.9159 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | YUKON | 55 RANCHWOOD BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 128835 | 116069 | 6429 | 1819 | 8.0293e-06 | 1.161e-06 | 6.9159 | 1 | 310 | Customer | 47687 | Load | Tran1phPad | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | #N/A
J2001.011033 | PD-01292020-00331 | NORTHEAST | SAPULPA | 7606:CUSHING TAP | CUSHING_TAP_649 | 760649 | 2020-01-29 13:52 | 2020-01-29 18:06 | 254.45 | 1 | 1 | 258.9057 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | CUSHING | 19604 E 56 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 74054 | 40781 | 148 | 96 | 0.00030058 | 1.161e-06 | 258.9057 | 1 | 310 | Load | 14175 | Load | Tran1phOH | GREGORY R HOOVER | 918-261-6803 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | OK - 2021
J2001.011037 |  | NORTHEAST | SAPULPA | 3214:LONE STAR | LONE_STAR_1422 | 321422 | 2020-01-29 14:06 | 2020-01-29 15:30 | 84.62 | 3 | 2 | 187.85 | 4 | DETERIORATION | 2 | TRANSFORMER OH | SAPULPA | 3/8MS 151ST ON 97-W AV S SP W | CMI_PLANNED | YES | NO | NO | 861343 | 74054 | 40781 | 2658 | 1098 | 0.00021809 | 3.4829e-06 | 62.6167 | 1 | 308 | Load | 47625 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | OK - 2020
J2001.011041 |  | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_521 | 320521 | 2020-01-29 14:24 | 2020-01-29 15:53 | 88.3 | 6 | 4 | 141.8 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | SAPULPA | 708 N.HICKORY | CMI_NORMAL | NO | NO | NO | 861343 | 74054 | 40781 | 3850 | 1610 | 0.00016463 | 6.9659e-06 | 23.6333 | 1 | 308 | Load | 42679 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | OK - 2022
J2001.011043 |  | SOUTHERN | HEALDTON | 5122:DILLARD | DILLARD_2222 | 512222 | 2020-01-29 14:32 | 2020-01-29 15:10 | 37.63 | 4 | 1 | 103.3333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | WILSON | 417 W.IDABELL | CMI_PLANNED | YES | NO | NO | 861343 | 77621 | 6798 | 1189 | 698 | 0.00011997 | 4.6439e-06 | 25.8333 | 1 | 308 | Load | 7620 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011053 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_724 | 870724 | 2020-01-29 14:59 | 2020-01-29 16:12 | 72.23 | 1 | 1 | 72.2333 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 1500 E.LINDSEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 159155 | 56982 | 11834 | 2409 | 8.3861e-05 | 1.161e-06 | 72.2333 | 1 | 310 | Customer | 74216 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011057 |  | NORTHEAST | MUSKOGEE | 3109:HONOR HEIGHTS | HONOR_HEIGHTS_921 | 310921 | 2020-01-29 15:14 | 2020-01-29 16:57 | 102.27 | 7 | 4 | 285.7167 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | MUSKOGEE | 5217 KERSHAW CI | CMI_PLANNED | YES | NO | NO | 861343 | 74054 | 33273 | 1178 | 1156 | 0.00033171 | 8.1268e-06 | 40.8167 | 1 | 308 | Load | 4309 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | OK - 2020
J2001.011061 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7429 | 847429 | 2020-01-29 15:23 | 2020-01-29 15:36 | 13.53 | 1 | 1 | 13.5333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2309 E.MADISON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 168236 | 148411 | 6168 | 681 | 1.5712e-05 | 1.161e-06 | 13.5333 | 1 | 310 | Customer | 6347 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | OK - 2022
J2001.011063 |  | METRO WEST | WEST | 8323:RICHARDS | RICHARDS_2323 | 832323 | 2020-01-29 15:26 | 2020-01-29 15:38 | 11.15 | 1 | 1 | 11.15 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 10608 N. COUNCIL - WS BLDG. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 128835 | 116069 | 5020 | 1671 | 1.2945e-05 | 1.161e-06 | 11.15 | 1 | 310 | Customer | 73431 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011065 | PD-01292020-00371 | METRO NORTH | NORTH | 8209:CLASSEN | CLASSEN_921 | 820921 | 2020-01-29 15:29 | 2020-01-29 16:36 | 67.05 | 1 | 1 | 35.6255 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1130 NW 12TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 168236 | 148411 | 3885 | 452 | 4.136e-05 | 1.161e-06 | 35.6255 | 1 | 310 | Customer | 503 | Load | Tran1phOH | REX R WILSON | 405-535-4507 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011064 |  | METRO NORTH | GUTHRIE | 8813:FITZGERALD CR | FITZGERALD_CR_1341 | 881341 | 2020-01-29 15:30 | 2020-01-29 15:51 | 21.12 | 1 | 1 | 21.1167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | COYLE | COYLE OK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 168236 | 19825 | 1045 | 237 | 2.4516e-05 | 1.161e-06 | 21.1167 | 1 | 310 | Customer | 40869 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011071 |  | METRO WEST | WEST | 8342:BRADEN PARK | BRADEN_PARK_4223 | 834223 | 2020-01-29 15:41 | 2020-01-29 15:45 | 3.98 | 1 | 1 | 3.9833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1/2MN NW.122 + MAC ARTHUR | CMI_MOMENTARY | YES | NO | NO | 861343 | 128835 | 116069 | 3401 | 1783 | 4.6246e-06 | 1.161e-06 | 3.9833 | 1 | 310 | Customer | 70871 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | OK - 2022
J2001.011072 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7021 | 817021 | 2020-01-29 15:47 | 2020-01-29 16:10 | 23.17 | 1 | 1 | 23.1667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 121F SW.74 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 159155 | 102173 | 9937 | 1789 | 2.6896e-05 | 1.161e-06 | 23.1667 | 1 | 310 | Customer | 36319 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011077 |  | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5222 | 835222 | 2020-01-29 16:07 | 2020-01-29 16:11 | 4.17 | 1 | 1 | 4.1667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 13518 HOLLOW ROCK RD | CMI_MOMENTARY | YES | NO | NO | 861343 | 168236 | 148411 | 6517 | 1353 | 4.8374e-06 | 1.161e-06 | 4.1667 | 1 | 310 | Customer | 59681 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011079 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-29 16:12 | 2020-01-29 16:36 | 23.72 | 31 | 0 | 734.0195 | 4 | DETERIORATION | 28 | CROSSARM | FORT SMITH | 4th and Custer | CMI_PLANNED | YES | NO | NO | 861343 | 82241 | 61204 | 2735 | 2123 | 0.00085218 | 3.599e-05 | 23.678 | 1 | 0 | Mainline | 100987 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | Ark - Series 2
J2001.011100 | PD-01292020-00422 | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5231 | 835231 | 2020-01-29 17:08 | 2020-01-29 20:42 | 213.53 | 1 | 1 | 202.9667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 11009 MAGNOLIA PK | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861343 | 168236 | 148411 | 6517 | 638 | 0.00023564 | 1.161e-06 | 202.9667 | 1 | 310 | Customer | 27852 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011105 |  | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1823 | 931823 | 2020-01-29 17:15 | 2020-01-29 18:10 | 55.03 | 4 | 2 | 151.6 | 12 | POOR CONNECTION | 1 | TRANSFORMER UG | ALMA | DAVENWOOD LOT 5 | CMI_NORMAL | NO | NO | NO | 861343 | 82241 | 61204 | 2848 | 1240 | 0.000176 | 4.6439e-06 | 37.9 | 1 | 308 | Load | 13299 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | Ark - Series 2
J2001.011110 | PD-01292020-00424 | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-01-29 17:30 | 2020-01-30 00:14 | 403.88 | 1 | 2 | 400.4833 | 3 | DAMAGED BY PUBLIC | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 11805 BLUEBERRY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 159155 | 56982 | 4239 | 1005 | 0.00046495 | 1.161e-06 | 400.4833 | 1 | 310 | Customer | 56145 | Load | Tran1phPad | CARL BILYEU | 405-820-9246 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011118 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2126 | 822126 | 2020-01-29 18:21 | 2020-01-29 18:43 | 22.5 | 1 | 1 | 22.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4224 NW.10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 168246 | 148422 | 9250 | 676 | 2.6122e-05 | 1.161e-06 | 22.5 | 1 | 310 | Customer | 48591 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011123 | PD-01292020-00430 | SOUTHERN | MADILL | 5408:CANEY CREEK | CANEY_CREEK_831 | 540831 | 2020-01-29 18:22 | 2020-01-29 19:52 | 90.25 | 12 | 9 | 880.6 | 5 | ELECTRICAL TRACKING | 47 | ARRESTOR OH | KINGSTON | NE COR MAIN + 7TH | CMI_NORMAL | NO | NO | NO | 861343 | 77628 | 7199 | 1052 | 628 | 0.0010224 | 1.3932e-05 | 73.3833 | 1 | 310 | Mainline | 4882 | Fuse | FuseOH | ANDREW CHAVERS | 580-504-0524 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011128 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2126 | 822126 | 2020-01-29 18:47 | 2020-01-29 18:52 | 5.3 | 1 | 1 | 5.3 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4224 NW.10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 168246 | 148422 | 9250 | 676 | 6.1532e-06 | 1.161e-06 | 5.3 | 1 | 310 | Customer | 48591 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011132 | PD-01292020-00436 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1226 | 831226 | 2020-01-29 18:51 | 2020-01-29 19:49 | 58.35 | 1 | 1 | 58.35 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1141 NW.46 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 168246 | 148422 | 7753 | 1748 | 6.7743e-05 | 1.161e-06 | 58.35 | 1 | 310 | Customer | 13983 | Load | Tran1phOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | OK - 2021
J2001.011131 |  | SOUTHERN | MADILL | 5408:CANEY CREEK | CANEY_CREEK_831 | 540831 | 2020-01-29 18:51 | 2020-01-29 19:51 | 60.15 | 1 | 1 | 60.15 | 4 | DETERIORATION | 47 | ARRESTOR OH | KINGSTON | 300 N WILLIS | CMI_NORMAL | NO | NO | NO | 861343 | 77628 | 7199 | 1052 | 628 | 6.9833e-05 | 1.161e-06 | 60.15 | 1 | 320 | Customer | 4170 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011133 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-01-29 18:53 | 2020-01-29 18:59 | 6.67 | 1 | 1 | 6.6667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BIXBY | PECAN PARK BETWEEN L37+38 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 74060 | 40784 | 2752 | 1440 | 7.7399e-06 | 1.161e-06 | 6.6667 | 1 | 310 | Customer | 43105 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | OK - 2021
J2001.011135 | PD-01292020-00437 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2126 | 822126 | 2020-01-29 19:08 | 2020-01-29 20:43 | 95.42 | 1 | 1 | 95.4167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4224 NW.10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 168246 | 148422 | 9250 | 676 | 0.00011078 | 1.161e-06 | 95.4167 | 1 | 310 | Customer | 48591 | Load | Tran1phPad | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011136 | PD-01292020-00438 | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1823 | 931823 | 2020-01-29 19:08 | 2020-01-29 20:45 | 96.83 | 1 | 1 | 95.6667 | 5 | ELECTRICAL TRACKING | 20 | FUSE BARREL | ALMA | 1708 HWY 71 NORTH | CMI_NORMAL | NO | NO | NO | 861343 | 82257 | 61217 | 2848 | 1240 | 0.00011107 | 1.161e-06 | 95.6667 | 1 | 310 | Load | 5841 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | Ark - Series 2
J2001.011141 | PD-01292020-00439 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3731 | 833731 | 2020-01-29 19:44 | 2020-01-29 21:50 | 126.1 | 1 | 2 | 122.6167 | 12 | POOR CONNECTION | 50 | CONNECTOR | THE VILLAGE | 1933 SHEFFIELD RD | CMI_NORMAL | NO | NO | NO | 861343 | 168246 | 148422 | 5766 | 1903 | 0.00014236 | 1.161e-06 | 122.6167 | 1 | 320 | Customer | 23050 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | OK - 2020
J2001.011144 | PD-01292020-00440 | METRO SOUTH | SOUTH | 8728:CHERRY CREEK | CHERRY_CREEK_2829 | 872829 | 2020-01-29 20:03 | 2020-01-29 22:10 | 126.98 | 1 | 1 | 104.0167 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | NORMAN | 4109 QUAIL DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861343 | 159190 | 57006 | 7106 | 1149 | 0.00012076 | 1.161e-06 | 104.0167 | 1 | 310 | Customer | 64287 | Load | Tran1phPad | CHAD W GLEAVE | 405-250-7464 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011151 | PD-01292020-00448 | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_622 | 770622 | 2020-01-29 20:44 | 2020-01-30 00:24 | 220.05 | 8 | 9 | 1600.9333 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | BRISTOW | 1118 S OAK, BRISTOW | CMI_NORMAL | NO | NO | NO | 861343 | 74060 | 40784 | 3783 | 2010 | 0.0018586 | 9.2878e-06 | 200.1167 | 1 | 310 | Load | 14877 | Load | Tran1phPad | CONTRACTOR 5 DAVID ELLIOT INC | 918-639-5055 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | #N/A
J2001.011160 | PD-01292020-00452 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-01-29 21:50 | 2020-01-29 23:14 | 84.08 | 1 | 1 | 74.4 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 212 NW.28 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861343 | 168246 | 148422 | 11127 | 2338 | 8.6377e-05 | 1.161e-06 | 74.4 | 1 | 320 | Customer | 2362 | Load | Tran1phOH | DARREN L STOCKTON | 918-777-1697 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | OK - 2020
J2001.011162 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5923 | 835923 | 2020-01-29 22:03 | 2020-01-29 22:03 | 0 | 1149 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | YUKON | 4323 N CZECH HALL RD | CMI_MOMENTARY | YES | NO | NO | 861343 | 128844 | 116073 | 6427 | 1150 | 0 | 0.001334 | 0 | 1 | 0 | Feeder | YUKON_5923 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-29 | 2020 |  | #N/A
J2001.011164 | PD-01292020-00454 | NORTHEAST | SAPULPA | 3216:BEELINE | BEELINE_1628 | 321628 | 2020-01-29 22:19 | 2020-01-30 02:17 | 238.4 | 1 | 1 | 228.7667 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | GLENPOOL | 13888 S.NYSSA PL | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861343 | 74060 | 40784 | 5565 | 1445 | 0.00026559 | 1.161e-06 | 228.7667 | 1 | 310 | Customer | 42195 | Load | Tran1phPad | CONTRACTOR 5 DAVID ELLIOT INC | 918-639-5055 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011168 | PD-01292020-00457 | SOUTHERN | MADILL | 5408:CANEY CREEK | CANEY_CREEK_831 | 540831 | 2020-01-29 22:45 | 2020-01-30 00:59 | 134.78 | 1 | 1 | 134.7833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | KINGSTON | % PO BOX 165 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861343 | 77628 | 7199 | 1052 | 628 | 0.00015648 | 1.161e-06 | 134.7833 | 1 | 310 | Customer | 12239 | Load | Tran1phOH | ANDREW CHAVERS | 580-504-0524 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011171 | PD-01292020-00455 | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-01-29 22:57 | 2020-01-30 04:11 | 313.95 | 1 | 1 | 307.7333 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | EL RENO | ROUTE 3 | CMI_NORMAL | NO | NO | NO | 861343 | 128844 | 12771 | 6954 | 1827 | 0.00035727 | 1.161e-06 | 307.7333 | 1 | 310 | Customer | 41323 | Load | Tran1phOH | KAEL GUTHERY | 405-428-1818 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-29 | 2020 |  | #N/A
J2001.011177 | PD-01302020-00001 | METRO WEST | WEST | 8359:YUKON | YUKON_5922 | 835922 | 2020-01-29 23:52 | 2020-01-30 04:17 | 265.15 | 1 | 1 | 137.6167 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | YUKON | 400 S.RANCHWOOD BL | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861343 | 128844 | 116073 | 6427 | 1638 | 0.00015977 | 1.161e-06 | 137.6167 | 1 | 310 | Customer | 38786 | Load | Tran1phPad | CARL BILYEU | 405-820-9246 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-29 | 2020 |  | #N/A
J2001.011196 | PD-01302020-00013 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1422 | 311422 | 2020-01-30 05:17 | 2020-01-30 10:02 | 285.28 | 1 | 1 | 254.75 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | MUSKOGEE | 2240 W.SHAWNEE | CMI_NORMAL | NO | NO | NO | 861407 | 74060 | 33276 | 4569 | 1171 | 0.00029574 | 1.1609e-06 | 254.75 | 1 | 320 | Load | 533 | Load | Tran3phPadWye | STEVE K HIGHFILL | 918-869-2785 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | OK - 2020
J2001.011198 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2525 | 912525 | 2020-01-30 05:46 | 2020-01-30 07:37 | 110.97 | 3 | 3 | 328.2 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | OLD GREENWOOD ST AND S SAVANNAH ST | CMI_PLANNED | YES | NO | NO | 861407 | 82257 | 61217 | 2738 | 198 | 0.000381 | 3.4827e-06 | 109.4 | 1 | 308 | Load | 8380 | Load | TranOpenDelta | Contractor | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | Ark - Series 2
J2001.011201 | PD-01302020-00017 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6524 | 836524 | 2020-01-30 06:14 | 2020-01-30 08:25 | 130.95 | 1 | 2 | 78.3262 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1/2MW MERIDIAN NS NW.HWY. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 128844 | 116073 | 7423 | 1651 | 9.0928e-05 | 1.1609e-06 | 78.3262 | 1 | 310 | Load | 76463 | Load | Tran3phPadWye | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011209 | PD-01302020-00024 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-01-30 07:20 | 2020-01-30 08:55 | 94.9 | 1 | 1 | 79.5833 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 2008 N.ANN-ARBOR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861407 | 168246 | 148422 | 9250 | 1943 | 9.2388e-05 | 1.1609e-06 | 79.5833 | 1 | 320 | Customer | 2984 | Load | Tran1phOH | BROC ROBINSON | 405-312-1688 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | OK - 2021
J2001.011214 |  | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_621 | 550621 | 2020-01-30 07:52 | 2020-01-30 10:21 | 148.43 | 6 | 5 | 795.15 | 4 | DETERIORATION | 1 | TRANSFORMER UG | DURANT | 206 MEADOW LARK LN | CMI_PLANNED | YES | NO | NO | 861407 | 77628 | 15497 | 6739 | 901 | 0.00092308 | 6.9653e-06 | 132.525 | 1 | 308 | Load | 20019 | Load | Tran1phPad | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011215 | PD-01302020-00030 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3925 | 833925 | 2020-01-30 08:03 | 2020-01-30 09:46 | 102.55 | 1 | 1 | 102.55 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | WARR ACRES | 6117 NW.57 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861407 | 168246 | 148422 | 7852 | 2183 | 0.00011905 | 1.1609e-06 | 102.55 | 1 | 310 | Customer | 12346 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | OK - 2022
J2001.011222 | PD-01302020-00050 | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_647 | 890647 | 2020-01-30 08:24 | 2020-01-30 10:48 | 143.73 | 1 | 1 | 143.7333 | 22 | WIND | 17 | JUMPER | CANTON | 3E 1.5S .5E CANTON | CMI_NORMAL | NO | NO | NO | 861407 | 128844 | 12771 | 1365 | 1070 | 0.00016686 | 1.1609e-06 | 143.7333 | 1 | 310 | Load | 47791 | Load | Tran3phWye | MICHAEL T MAHEN | 405-210-6029 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011224 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-01-30 08:35 | 2020-01-30 14:03 | 328.62 | 1 | 1 | 321.1833 | 4 | DETERIORATION | 12 | POLE | CLARKSVILLE | 3M W-LAMAR SCHOOL | CMI_PLANNED | YES | NO | NO | 861407 | 82257 | 7546 | 730 | 0 | 0.00037286 | 1.1609e-06 | 321.1833 | 1 | 308 | Load | 17821 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | #N/A
J2001.011226 | PD-01302020-00059 | SOUTHERN | SULPHUR | 5705:SULPHUR | SULPHUR_531 | 570531 | 2020-01-30 08:37 | 2020-01-30 11:03 | 146.78 | 1 | 2 | 133.75 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | SULPHUR | N OF CITY | CMI_NORMAL | NO | NO | NO | 861407 | 77628 | 6814 | 3633 | 602 | 0.00015527 | 1.1609e-06 | 133.75 | 1 | 310 | Load | 17838 | Load | Tran1phOH | JOE LOFTIS | 918-884-5349 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011227 | PD-01302020-00061 | ARKANSAS | POTEAU | 3507:HOWE | HOWE_722 | 350722 | 2020-01-30 08:41 | 2020-01-30 09:45 | 64.22 | 1 | 1 | 64.2167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | HOWE | HOWE OK 74940 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 82257 | 13494 | 509 | 434 | 7.4549e-05 | 1.1609e-06 | 64.2167 | 1 | 320 | Customer | 7439 | Load | Tran1phOH | TOBY C MEAD | 918-658-5596 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | OK - 2020
J2001.011231 | PD-01302020-00064 | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2224 | 882224 | 2020-01-30 08:47 | 2020-01-30 14:28 | 341.12 | 1 | 1 | 316.4667 | 3 | DAMAGED BY PUBLIC | 15 | METER - SECONDARY | GUTHRIE | 91/4MS 1ME HY 77 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 168246 | 19824 | 5385 | 1850 | 0.00036738 | 1.1609e-06 | 316.4667 | 1 | 310 | Load | 43956 | Load | Tran1phOH | KELLEY D WATSON | 405-763-8148 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011235 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-30 08:48 | 2020-01-30 11:46 | 178.68 | 5 | 4 | 699.9167 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | ALLEY BTWN ELLIS ST. & TERRY AVE. | CMI_PLANNED | YES | NO | NO | 861407 | 82257 | 61217 | 2738 | 2126 | 0.00081253 | 5.8045e-06 | 139.9833 | 1 | 308 | Load | 202380 | Load | Tran3phWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | Ark - Series 2
J2001.011230 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-01-30 08:48 | 2020-01-30 08:54 | 6.7 | 1 | 1 | 6.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | HARRAH | 17000 LYTAL LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 114402 | 71204 | 11636 | 3534 | 7.778e-06 | 1.1609e-06 | 6.7 | 1 | 310 | Customer | 57917 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011233 | PD-01302020-00070 | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1724 | 831724 | 2020-01-30 08:55 | 2020-01-30 09:52 | 56.78 | 1 | 1 | 56.7833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 12831 STRATFORD DR BLDG 10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 168246 | 148422 | 6646 | 2777 | 6.5919e-05 | 1.1609e-06 | 56.7833 | 1 | 310 | Customer | 75449 | Load | Tran1phPad | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011232 |  | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1935 | 851935 | 2020-01-30 08:56 | 2020-01-30 13:38 | 282.33 | 8 | 7 | 2167.2 | 4 | DETERIORATION | 1 | TRANSFORMER UG | MIDWEST CITY | 1459 N.MIDWEST BL | CMI_PLANNED | YES | NO | NO | 861407 | 114402 | 71204 | 12446 | 2158 | 0.0025159 | 9.2871e-06 | 270.9 | 1 | 308 | Load | 51528 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011234 |  | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1935 | 851935 | 2020-01-30 08:57 | 2020-01-30 13:38 | 281.1 | 16 | 11 | 4311.4667 | 4 | DETERIORATION | 1 | TRANSFORMER UG | MIDWEST CITY | 1457 N.MIDWEST BL | CMI_PLANNED | YES | NO | NO | 861407 | 114402 | 71204 | 12446 | 2158 | 0.0050051 | 1.8574e-05 | 269.4667 | 1 | 308 | Load | 51527 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011245 |  | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1722 | 831722 | 2020-01-30 09:09 | 2020-01-30 09:45 | 35.67 | 1 | 1 | 29.5167 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 11415 N.WESTERN | CMI_NORMAL | NO | NO | NO | 861407 | 168246 | 148422 | 6646 | 1203 | 3.4266e-05 | 1.1609e-06 | 29.5167 | 1 | 308 | Customer | 4947 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011240 |  | ARKANSAS | FORT SMITH | 9104:J STREET | J_STREET_422 | 910422 | 2020-01-30 09:09 | 2020-01-30 12:36 | 206.92 | 1 | 1 | 206.9167 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | FORT SMITH | 707 N.7 | CMI_NORMAL | NO | NO | NO | 861407 | 82257 | 61217 | 1999 | 511 | 0.00024021 | 1.1609e-06 | 206.9167 | 1 | 310 | Customer | 6871 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-30 | 2020 |  | Ark - Series 2
J2001.011246 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-30 09:27 | 2020-01-30 12:58 | 210.72 | 1 | 1 | 190.1167 | 4 | DETERIORATION | 12 | POLE | LAVACA | 6 POLE N-HWY 22 ON 96,S-LAVACA | CMI_PLANNED | YES | NO | NO | 861407 | 82257 | 61217 | 2738 | 2126 | 0.0002207 | 1.1609e-06 | 190.1167 | 1 | 308 | Load | 3662 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | Ark - Series 2
J2001.011247 |  | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_647 | 890647 | 2020-01-30 09:28 | 2020-01-30 10:24 | 56.78 | 5 | 4 | 127.8333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | CANTON | 62909 N 2494 Rd | CMI_PLANNED | YES | NO | NO | 861407 | 128844 | 12771 | 1365 | 1070 | 0.0001484 | 5.8045e-06 | 25.5667 | 1 | 308 | Load | 34424 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011249 | PD-01302020-00117 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-01-30 09:31 | 2020-01-30 10:49 | 78.12 | 1 | 1 | 78.1167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4748 NW 23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 168246 | 148422 | 9250 | 1943 | 9.0685e-05 | 1.1609e-06 | 78.1167 | 1 | 310 | Customer | 35030 | Load | Tran1phPad | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | OK - 2021
J2001.011254 | PD-01302020-00107 | METRO SOUTH | SOUTH | 5606:WALNUT CREEK | WALNUT_CREEK_621 | 560621 | 2020-01-30 09:35 | 2020-01-30 11:05 | 90.33 | 1 | 1 | 90.3333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | WAYNE | 1W 1/4S BELLS CR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 159190 | 57006 | 1107 | 1107 | 0.00010487 | 1.1609e-06 | 90.3333 | 1 | 321 | Customer | 14692 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011262 | PD-01302020-00128 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2225 | 832225 | 2020-01-30 09:52 | 2020-01-30 10:48 | 55.65 | 2 | 2 | 104.9167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2208 NW.32 | CMI_NORMAL | NO | NO | NO | 861407 | 168246 | 148422 | 9175 | 2039 | 0.0001218 | 2.3218e-06 | 52.4583 | 1 | 310 | Secondary | 13701 | Load | Tran1phOH | REX R WILSON | 405-535-4507 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | OK - 2021
J2001.011263 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-30 09:57 | 2020-01-30 14:56 | 298.97 | 6 | 3 | 1585.95 | 4 | DETERIORATION | 12 | POLE | ARKOMA | 424 OKLAHOMA | CMI_PLANNED | YES | NO | NO | 861407 | 82257 | 61217 | 2938 | 876 | 0.0018411 | 6.9653e-06 | 264.325 | 1 | 308 | Load | 5355 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-30 | 2020 |  | Ark - Series 2
J2001.011267 | PD-01302020-00143 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2029 | 862029 | 2020-01-30 10:00 | 2020-01-30 10:36 | 35.62 | 1 | 1 | 11.7258 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 500 SE 29TH ST | CMI_NORMAL | NO | NO | NO | 861407 | 159190 | 102184 | 4752 | 984 | 1.3612e-05 | 1.1609e-06 | 11.7258 | 1 | 310 | Load | 83834 | Load | TranOpenDelta | ETHAN MORRIS | 918-510-5170 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011268 | PD-01302020-00138 | METRO NORTH | GUTHRIE | 8813:FITZGERALD CR | FITZGERALD_CR_1341 | 881341 | 2020-01-30 10:05 | 2020-01-30 22:17 | 732.2 | 1 | 1 | 732.2 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | COYLE | N/MAIN/E IOWA-COYLE | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861407 | 168246 | 19824 | 1045 | 237 | 0.00085 | 1.1609e-06 | 732.2 | 1 | 320 | Customer | 43521 | Load | Tran1phOH | SCOTT C PERRY | 405-258-6044 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011272 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-30 10:14 | 2020-01-30 11:16 | 62.42 | 6 | 3 | 222 | 4 | DETERIORATION | 2 | TRANSFORMER OH | MOUNTAINBURG | HWY 71 AT WILLOW, MTBURG | CMI_PLANNED | YES | NO | NO | 861407 | 82257 | 61217 | 3790 | 2586 | 0.00025772 | 6.9653e-06 | 37 | 1 | 308 | Load | 8098 | Load | TranOHDeltaSplitBank | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-30 | 2020 |  | Ark - Series 2
J2001.011280 | PD-01302020-00160 | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-01-30 10:32 | 2020-01-30 15:49 | 317.28 | 1 | 1 | 305.2667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 11000 SE. 95TH ST. | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861407 | 159190 | 57006 | 4239 | 1005 | 0.00035438 | 1.1609e-06 | 305.2667 | 1 | 310 | Load | 18130 | Load | Tran1phOH | CHAD W GLEAVE | 405-250-7464 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011284 | PD-01302020-00165 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1524 | 811524 | 2020-01-30 10:39 | 2020-01-30 11:06 | 27.15 | 1 | 1 | 6.7608 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1616 SW.32 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 159190 | 102184 | 6065 | 2072 | 7.8486e-06 | 1.1609e-06 | 6.7608 | 1 | 320 | Customer | 22152 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | OK - 2022
J2001.011283 |  | METRO SOUTH | SOUTH CENTRAL | 8194:WESTMOORE | WESTMOORE_9424 | 819424 | 2020-01-30 10:39 | 2020-01-30 10:39 | 0 | 1645 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 12406 S PENNSYLVANIA AVE | CMI_MOMENTARY | YES | NO | NO | 861407 | 159190 | 102184 | 8105 | 1645 | 0 | 0.0019097 | 0 | 1 | 0 | Feeder | WESTMORE_9424 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011292 | PD-01302020-00179 | METRO SOUTH | SOUTH CENTRAL | 8194:WESTMOORE | WESTMOORE_9424 | 819424 | 2020-01-30 10:44 | 2020-01-30 12:32 | 108.4 | 15 | 7 | 1480 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | OKLAHOMA CITY | 3201 SW 130TH PL | CMI_NORMAL | NO | NO | NO | 861407 | 159190 | 102184 | 8105 | 1645 | 0.0017181 | 1.7413e-05 | 98.6667 | 1 | 310 | Mainline | 107764 | Fuse | FuseRiser | ETHAN MORRIS | 918-510-5170 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011290 | PD-01302020-00178 | METRO NORTH | GUTHRIE | 8813:FITZGERALD CR | FITZGERALD_CR_1342 | 881342 | 2020-01-30 10:47 | 2020-01-30 12:24 | 96.7 | 1 | 1 | 96.7 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | LANGSTON | 5BE LANG UNIV ON WA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 168246 | 19824 | 1045 | 808 | 0.00011226 | 1.1609e-06 | 96.7 | 1 | 310 | Customer | 32182 | Load | Tran1phOH | KELLEY D WATSON | 405-763-8148 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011301 | PD-01302020-00190 | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_631 | 460631 | 2020-01-30 11:02 | 2020-01-30 12:03 | 61.33 | 1 | 2 | 40.55 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 21 | FUSE - TRANSFORMER | WOODWARD | .5BW-MARTN RD,OILPATCH RD | CMI_NORMAL | NO | NO | NO | 861407 | 53552 | 10428 | 5685 | 1170 | 4.7074e-05 | 1.1609e-06 | 40.55 | 1 | 310 | Load | 13086 | Load | TranOpenDelta | ROY L THRASH | 580-334-5371 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | #N/A
J2001.011299 | PD-01302020-00185 | METRO EAST | SHAWNEE | 7410:MAUD TAP | MAUD_TAP_1021 | 741021 | 2020-01-30 11:02 | 2020-01-30 14:07 | 184.5 | 1 | 1 | 184.5 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ST. LOUIS | SW,SE,NW, SEC 13-7-4 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 114402 | 22118 | 1020 | 763 | 0.00021418 | 1.1609e-06 | 184.5 | 1 | 320 | Load | 18107 | Load | TranOpenDelta | BRYAN K TATUM | 405-659-0746 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011300 | PD-01302020-00186 | METRO EAST | SHAWNEE | 7410:MAUD TAP | MAUD_TAP_1021 | 741021 | 2020-01-30 11:03 | 2020-01-30 12:45 | 102.43 | 1 | 2 | 102.4333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MAUD | MAUD OK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 114402 | 22118 | 1020 | 763 | 0.00011891 | 1.1609e-06 | 102.4333 | 1 | 310 | Customer | 4536 | Load | Tran1phOH | BRYAN K TATUM | 405-659-0746 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011306 | PD-01302020-00196 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2229 | 852229 | 2020-01-30 11:03 | 2020-01-30 12:59 | 116.02 | 5 | 6 | 463.6667 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | HARRAH | 18735 NE.23 | CMI_NORMAL | NO | NO | NO | 861407 | 114402 | 71204 | 11636 | 1392 | 0.00053827 | 5.8045e-06 | 92.7333 | 1 | 310 | Load | 61353 | Load | Tran1phOH | STEVEN CASKEY | 405-777-8855 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011304 | PD-01302020-00256 | ARKANSAS | OZARK | 9224:BRANCH | BRANCH_2463 | 922463 | 2020-01-30 11:17 | 2020-01-30 13:12 | 114.88 | 1 | 1 | 114.8833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | CAULKSVILLE | 525 SHAVER RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 82257 | 7546 | 1796 | 822 | 0.00013337 | 1.1609e-06 | 114.8833 | 1 | 310 | Load | 217579 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-30 | 2020 |  | Ark - Series 3
J2001.011305 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-30 11:18 | 2020-01-30 11:43 | 24.92 | 1 | 0 | 24.8873 | 4 | DETERIORATION | 27 | CUTOUT | 0 | 3/4M E-HWY 71 + HWY282 | CMI_PLANNED | YES | NO | NO | 861407 | 82257 | 61217 | 3790 | 2586 | 2.8891e-05 | 1.1609e-06 | 24.8873 | 1 | 0 | Tap | 5334 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-30 | 2020 |  | Ark - Series 2
J2001.011308 |  | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_521 | 320521 | 2020-01-30 11:22 | 2020-01-30 14:23 | 180.38 | 3 | 4 | 62.55 | 3 | DAMAGED BY PUBLIC | 36 | CONDUCTOR PRIMARY - UG | SAPULPA | 221 N.MOUNDS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 74060 | 40784 | 3850 | 1610 | 7.2614e-05 | 3.4827e-06 | 20.85 | 1 | 310 | Secondary | 41139 | Load | Tran1phPad | Ties | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | OK - 2022
J2001.011310 |  | SOUTHERN | MADILL | 5409:LITTLE CITY | LITTLE CITY 21 | 540921 | 2020-01-30 11:25 | 2020-01-30 14:47 | 202.32 | 1 | 1 | 196.9 | 4 | DETERIORATION | 12 | POLE | MADILL | 1W 1.5 S 1W LITTLE CITY | CMI_PLANNED | YES | NO | NO | 861407 | 77628 | 7199 | 609 | 590 | 0.00022858 | 1.1609e-06 | 196.9 | 1 | 308 | Load | 19879 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011312 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-01-30 11:28 | 2020-01-30 14:08 | 160.28 | 9 | 10 | 633.9 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | BIXBY | 126 E NEEDLES | CMI_PLANNED | YES | NO | NO | 861407 | 74060 | 40784 | 2752 | 1440 | 0.00073589 | 1.0448e-05 | 70.4333 | 1 | 310 | Load | 40990 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | OK - 2021
J2001.011313 | PD-01302020-00209 | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_521 | 320521 | 2020-01-30 11:28 | 2020-01-30 12:10 | 42.28 | 1 | 1 | 42.2833 | 3 | DAMAGED BY PUBLIC | 36 | CONDUCTOR PRIMARY - UG | SAPULPA | 215 W.JOHNSON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 74060 | 40784 | 3850 | 1610 | 4.9086e-05 | 1.1609e-06 | 42.2833 | 1 | 311 | Customer | 41162 | Load | Tran1phPad | DAVID SEXTON | 918-978-1499 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | OK - 2022
J2001.011317 | PD-01302020-00219 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7022 | 817022 | 2020-01-30 11:39 | 2020-01-30 12:26 | 47.07 | 1 | 1 | 8.81 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MOORE | 2500 NOTTINGHAM WY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 159190 | 102184 | 9937 | 2104 | 1.0227e-05 | 1.1609e-06 | 8.81 | 1 | 310 | Customer | 20664 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011319 |  | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1623 | 581623 | 2020-01-30 11:44 | 2020-01-30 17:53 | 369.4 | 14 | 2 | 3772.7667 | 29 | TREES : GROW IN | 2 | TRANSFORMER OH | ADA | 610 S.CHERRY | CMI_PLANNED | YES | NO | NO | 861407 | 77628 | 11516 | 3461 | 1653 | 0.0043798 | 1.6252e-05 | 269.4833 | 1 | 308 | Load | 3126 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011322 | PD-01302020-00238 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3221 | 813221 | 2020-01-30 11:51 | 2020-01-30 13:00 | 69.43 | 1 | 2 | 34.7149 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1108 SW.47 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 159190 | 102184 | 7607 | 2076 | 4.03e-05 | 1.1609e-06 | 34.7149 | 1 | 320 | Customer | 8317 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | #N/A
J2001.011328 | PD-01302020-00255 | METRO EAST | SHAWNEE | 7432:ST GREGORY | ST_GREGORY_3231 | 743231 | 2020-01-30 12:09 | 2020-01-30 13:18 | 68.85 | 1 | 1 | 68.85 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SHAWNEE | 207 W.GEORGIA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 114402 | 22118 | 4093 | 1204 | 7.9927e-05 | 1.1609e-06 | 68.85 | 1 | 310 | Customer | 2216 | Load | Tran1phOH | BRYAN K TATUM | 405-659-0746 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011331 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-01-30 12:23 | 2020-01-30 14:27 | 124.95 | 4 | 0 | 466.0667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 11025 S.WESTMINSTER | CMI_PLANNED | YES | NO | NO | 861407 | 159190 | 57006 | 4239 | 1005 | 0.00054105 | 4.6436e-06 | 116.5167 | 1 | 0 | Load | 8364 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011335 | PD-01302020-00260 | METRO SOUTH | SOUTH | 8726:NOBLE | NOBLE_2621 | 872621 | 2020-01-30 12:28 | 2020-01-30 13:59 | 91.45 | 1 | 1 | 80.75 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | NOBLE | 609 MEADOWLAKE DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861407 | 159190 | 57006 | 2969 | 1448 | 9.3742e-05 | 1.1609e-06 | 80.75 | 1 | 320 | Customer | 62481 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011344 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7022 | 817022 | 2020-01-30 12:58 | 2020-01-30 13:02 | 4.52 | 1 | 1 | 4.5167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MOORE | 2500 NOTTINGHAM WY | CMI_MOMENTARY | YES | NO | NO | 861407 | 159190 | 102184 | 9937 | 2104 | 5.2434e-06 | 1.1609e-06 | 4.5167 | 1 | 310 | Customer | 20664 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011351 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7022 | 817022 | 2020-01-30 13:26 | 2020-01-30 13:34 | 7.88 | 1 | 1 | 7.8833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MOORE | 2500 NOTTINGHAM WY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 159190 | 102184 | 9937 | 2104 | 9.1517e-06 | 1.1609e-06 | 7.8833 | 1 | 310 | Customer | 20664 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011355 | PD-01302020-00305 | ARKANSAS | OZARK | 9413:RAZORBACK | RAZORBACK_1362 | 941362 | 2020-01-30 13:26 | 2020-01-30 14:54 | 87.57 | 1 | 1 | 87.5667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | PRAIRIE VIEW | 17582 Prairie View | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 82257 | 7546 | 398 | 398 | 0.00010166 | 1.1609e-06 | 87.5667 | 1 | 310 | Customer | 13146 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | Ark - Series 2
J2001.011358 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7022 | 817022 | 2020-01-30 13:40 | 2020-01-30 13:46 | 6.7 | 1 | 1 | 6.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MOORE | 2500 NOTTINGHAM WY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 159190 | 102184 | 9937 | 2104 | 7.778e-06 | 1.1609e-06 | 6.7 | 1 | 310 | Customer | 20664 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011360 | PD-01302020-00316 | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-01-30 13:47 | 2020-01-30 14:51 | 64.32 | 1 | 1 | 57.5667 | 12 | POOR CONNECTION | 50 | CONNECTOR | ADA | 924 E.ORCHARD | CMI_NORMAL | NO | NO | NO | 861407 | 77628 | 11516 | 2518 | 1090 | 6.6829e-05 | 1.1609e-06 | 57.5667 | 1 | 310 | Customer | 5665 | Load | Tran1phOH | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | #N/A
J2001.011362 | PD-01302020-00340 | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1422 | 911422 | 2020-01-30 13:53 | 2020-01-30 16:10 | 137.37 | 1 | 2 | 1.5167 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | FORT SMITH | WINDSOR DR AND N 46TH TERRACE | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861407 | 82257 | 61217 | 4740 | 1954 | 1.7607e-06 | 1.1609e-06 | 1.5167 | 1 | 320 | Customer | 16040 | Load | Tran1phPad | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-30 | 2020 |  | Ark - Series 1
J2001.011363 | PD-01302020-00330 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2225 | 832225 | 2020-01-30 14:03 | 2020-01-30 14:47 | 43.55 | 1 | 1 | 19.2909 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2208 NW.32 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 168246 | 148422 | 9175 | 2039 | 2.2395e-05 | 1.1609e-06 | 19.2909 | 1 | 310 | Customer | 13701 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | OK - 2021
J2001.011370 | PD-01302020-00358 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-30 14:13 | 2020-01-30 16:25 | 131.72 | 1 | 2 | 127.5 | 27 | TREE:NON PREVENTABLE | 12 | POLE | MOUNTAINBURG | % ROUTE 2 | CMI_NORMAL | NO | NO | NO | 861407 | 82257 | 61217 | 3790 | 2586 | 0.00014801 | 1.1609e-06 | 127.5 | 1 | 310 | Load | 6051 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-01-30 | 2020 |  | Ark - Series 2
J2001.011371 | PD-01302020-00343 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1935 | 851935 | 2020-01-30 14:21 | 2020-01-30 14:38 | 16.92 | 4 | 2 | 293.6 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MIDWEST CITY | .5MW AIR DEPOT + NE.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 114402 | 71204 | 12446 | 2158 | 0.00034084 | 4.6436e-06 | 73.4 | 1 | 310 | Mainline | 1781 | Fuse | FuseOH | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011381 | PD-01302020-00398 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1523 | 811523 | 2020-01-30 14:40 | 2020-01-30 16:49 | 128.63 | 1 | 1 | 128.6333 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1935 SW.15 | CMI_NORMAL | NO | NO | NO | 861407 | 159190 | 102184 | 6065 | 805 | 0.00014933 | 1.1609e-06 | 128.6333 | 1 | 310 | Customer | 388 | Load | TranOpenDelta | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | OK - 2022
J2001.011380 | PD-01302020-00401 | METRO EAST | CHANDLER | 7119:WARWICK | WARWICK_1941 | 711941 | 2020-01-30 14:41 | 2020-01-30 16:58 | 137.33 | 1 | 1 | 137.3333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | LUTHER | 1/2MW-LUTHER ROAD ON 66 NS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 114402 | 7468 | 2420 | 1463 | 0.00015943 | 1.1609e-06 | 137.3333 | 1 | 310 | Load | 20989 | Load | TranOpenDelta | SCOTT C PERRY | 405-258-6044 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | OK - 2021
J2001.011385 |  | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6522 | 836522 | 2020-01-30 14:59 | 2020-01-30 15:50 | 50.6 | 1 | 1 | 50.6 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6713 LYREWOOD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 128844 | 116073 | 7423 | 1863 | 5.8741e-05 | 1.1609e-06 | 50.6 | 1 | 310 | Customer | 47374 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | OK - 2021
J2001.011393 | PD-01302020-00394 | NORTHEAST | MUSKOGEE | 3117:THREE RIVERS | THREE_RIVERS_1724 | 311724 | 2020-01-30 15:36 | 2020-01-30 16:13 | 37.5 | 1 | 1 | 37.5 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 440 N 45TH ST E | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 74060 | 33276 | 2833 | 170 | 4.3533e-05 | 1.1609e-06 | 37.5 | 1 | 310 | Load | 10557 | Load | Tran3phWye | REID R WILLIAMS | 512-618-8800 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-30 | 2020 |  | #N/A
J2001.011394 | PD-01302020-00397 | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2131 | 332131 | 2020-01-30 15:39 | 2020-01-30 17:01 | 81.68 | 1 | 1 | 78.9667 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | OKAY | NORTH OF NEW SCHOOL - OKAY | CMI_NORMAL | NO | NO | NO | 861407 | 74060 | 33276 | 3338 | 1175 | 9.1672e-05 | 1.1609e-06 | 78.9667 | 1 | 310 | Customer | 18135 | Load | Tran1phOH | REID R WILLIAMS | 512-618-8800 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-30 | 2020 |  | #N/A
J2001.011400 |  | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6524 | 836524 | 2020-01-30 15:53 | 2020-01-30 15:59 | 6.2 | 1 | 1 | 6.2 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1/2MW MERIDIAN NS NW.HWY. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 128844 | 116073 | 7423 | 1651 | 7.1975e-06 | 1.1609e-06 | 6.2 | 1 | 310 | Load | 76463 | Load | Tran3phPadWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011403 |  | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2625 | 862625 | 2020-01-30 15:58 | 2020-01-30 16:19 | 20.8 | 1 | 1 | 20.8 | 1 | CANCELLED | 57 | CANCELLED | DEL CITY | 1709 S.SUNNYLANE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 159190 | 102184 | 7418 | 1268 | 2.4147e-05 | 1.1609e-06 | 20.8 | 1 | 310 | Customer | 7524 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | OK - 2022
J2001.011401 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-30 15:58 | 2020-01-30 16:16 | 17.72 | 33 | 0 | 347.05 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | 0 | W 71 + N OF HWY 282 | CMI_PLANNED | YES | NO | NO | 861407 | 82257 | 61217 | 3790 | 2586 | 0.00040289 | 3.8309e-05 | 10.5167 | 1 | 0 | Mainline | 6942 | Fuse | FuseRiser | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-30 | 2020 |  | Ark - Series 2
J2001.011404 | PD-01302020-00419 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5031 | 865031 | 2020-01-30 16:02 | 2020-01-30 17:24 | 82.13 | 1 | 2 | 82.1333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 407 W Fairchild Dr | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 114402 | 71204 | 8631 | 1597 | 9.5348e-05 | 1.1609e-06 | 82.1333 | 1 | 320 | Customer | 345563 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | OK - 2022
J2001.011405 |  | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5429 | 865429 | 2020-01-30 16:11 | 2020-01-30 16:11 | 0.45 | 26 | 0 | 11.164 | 1 | CANCELLED | 57 | CANCELLED | 0 | 0 | CMI_MOMENTARY | YES | NO | NO | 861407 | 159190 | 102184 | 9808 | 1662 | 1.296e-05 | 3.0183e-05 | 0.42938 | 1 | 0 | Mainline | 39602-1 | Switch | SwitchDefault | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011407 | PD-01302020-00422 | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2522 | 512522 | 2020-01-30 16:23 | 2020-01-30 17:36 | 72.65 | 1 | 1 | 72.65 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | LONE GROVE | 70 + NEWPORT RD,1.7N WS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 77628 | 23592 | 3307 | 562 | 8.4339e-05 | 1.1609e-06 | 72.65 | 1 | 320 | Load | 30316 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | OK - 2021
J2001.011410 |  | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1926 | 851926 | 2020-01-30 16:27 | 2020-01-30 16:45 | 18.43 | 1 | 1 | 18.4333 | 1 | CANCELLED | 57 | CANCELLED | MIDWEST CITY | 9916 MARK TR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 114402 | 71204 | 12446 | 2127 | 2.1399e-05 | 1.1609e-06 | 18.4333 | 1 | 320 | Customer | 66179 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | OK - 2021
J2001.011420 | PD-01302020-00441 | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9862 | 839862 | 2020-01-30 16:52 | 2020-01-30 18:42 | 110.22 | 2 | 3 | 146.1667 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | B1,L3B-VINTAGE GARDENS | CMI_NORMAL | NO | NO | NO | 861407 | 168246 | 148422 | 10660 | 2316 | 0.00016968 | 2.3218e-06 | 73.0833 | 1 | 310 | Secondary | 87053 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011419 | PD-01302020-00447 | NORTHWEST | WOODWARD | 4616:NEWMAN AVE | NEWMAN_AVE_1641 | 461641 | 2020-01-30 16:52 | 2020-01-31 08:59 | 967.12 | 1 | 1 | 967.1167 | 1 | CANCELLED | 57 | CANCELLED | GAGE | Hwy 15 & Airport Road | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 53552 | 10428 | 2012 | 2012 | 0.0011227 | 1.1609e-06 | 967.1167 | 1 | 310 | Load | 317979 | Load | Tran1phOH | ROY L THRASH | 580-334-5371 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | OK - 2020
J2001.011425 |  | METRO SOUTH | SOUTH CENTRAL | 8133:WR AIRPORT | WR_AIRPORT_3323 | 813323 | 2020-01-30 17:04 | 2020-01-30 20:12 | 188.32 | 6 | 6 | 1129.9 | 5 | ELECTRICAL TRACKING | 12 | POLE | OKLAHOMA CITY | SW 59TH & PORTLAND AV | CMI_NORMAL | NO | NO | NO | 861407 | 159190 | 102184 | 1489 | 83 | 0.0013117 | 6.9653e-06 | 188.3167 | 1 | 310 | Mainline | 7283 | Switch | SwitchOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011430 | PD-01302020-00448 | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1024 | 311024 | 2020-01-30 17:06 | 2020-01-30 20:48 | 221.68 | 36 | 23 | 7117.8 | 3 | DAMAGED BY PUBLIC | 36 | CONDUCTOR PRIMARY - UG | MUSKOGEE | NORTH ST @ HIDDEN VALL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 74060 | 33276 | 2903 | 1394 | 0.008263 | 4.1792e-05 | 197.7167 | 1 | 310 | Mainline | 26282 | Fuse | FuseRiser | BRUCE A PAULUS | 479-220-7661 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | OK - 2020
J2001.011426 |  | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1024 | 311024 | 2020-01-30 17:06 | 2020-01-30 17:06 | 0 | 1394 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MUSKOGEE | 1541 COUNTRY CLUB PLACE | CMI_MOMENTARY | YES | NO | NO | 861407 | 74060 | 33276 | 2903 | 1394 | 0 | 0.0016183 | 0 | 1 | 0 | Feeder | RIVERSIDE_1024 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-30 | 2020 |  | OK - 2020
J2001.011429 |  | METRO WEST | WEST | 8158:SARA | SARA_5871 | 815871 | 2020-01-30 17:07 | 2020-01-30 17:12 | 5 | 1 | 1 | 5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 10209 DOVER dr | CMI_MOMENTARY | YES | NO | NO | 861407 | 128844 | 116073 | 18255 | 5398 | 5.8045e-06 | 1.1609e-06 | 5 | 1 | 310 | Customer | 58100 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | OK - 2022
J2001.011435 |  | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1724 | 831724 | 2020-01-30 17:16 | 2020-01-30 17:22 | 5.75 | 1 | 1 | 5.75 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 12831 STRATFORD DR BLDG 10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 168246 | 148422 | 6646 | 2777 | 6.6751e-06 | 1.1609e-06 | 5.75 | 1 | 310 | Customer | 75449 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011442 |  | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4124 | 814124 | 2020-01-30 17:21 | 2020-01-30 17:33 | 11.7 | 1 | 1 | 11.7 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 737 SW.35 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 159190 | 102184 | 5809 | 2014 | 1.3582e-05 | 1.1609e-06 | 11.7 | 1 | 310 | Customer | 12915 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | #N/A
J2001.011452 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9929 | 829929 | 2020-01-30 17:33 | 2020-01-30 19:06 | 93.22 | 2 | 3 | 138.0833 | 11 | OVERLOAD | 2 | TRANSFORMER OH | BETHANY | 6812 NW.23 | CMI_PLANNED | YES | NO | NO | 861407 | 128844 | 116073 | 9232 | 2208 | 0.0001603 | 2.3218e-06 | 69.0417 | 1 | 310 | Secondary | 18208 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011453 | PD-01302020-00450 | METRO SOUTH | SOUTH CENTRAL | 8723:INDIAN HILL | INDIAN_HILL_2321 | 872321 | 2020-01-30 17:55 | 2020-01-30 20:33 | 157.98 | 1 | 1 | 106.8333 | 28 | OTHER (DESCRIBE) | 30 | CONDUCTOR SERVICE - UG | MOORE | 210 SE 25TH ST | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861407 | 159190 | 102184 | 3192 | 1739 | 0.00012402 | 1.1609e-06 | 106.8333 | 1 | 310 | Customer | 81922 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011454 |  | ARKANSAS | POTEAU | 3607:ROLAND ROAD | ROLAND_RD_721 | 360721 | 2020-01-30 18:06 | 2020-01-30 18:06 | 0 | 1139 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ROLAND | 103 EAST RAY FINE BLVD | CMI_MOMENTARY | YES | NO | NO | 861407 | 82263 | 13495 | 1139 | 1139 | 0 | 0.0013223 | 0 | 1 | 0 | Feeder | ROLND RD_721 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-01-30 | 2020 |  | #N/A
J2001.011456 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7423 | 847423 | 2020-01-30 18:13 | 2020-01-30 18:21 | 8.5 | 1 | 1 | 8.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1228 NE.15 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 168252 | 148427 | 6170 | 1294 | 9.8676e-06 | 1.1609e-06 | 8.5 | 1 | 310 | Customer | 7583 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | OK - 2022
J2001.011455 | PD-01302020-00453 | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1724 | 831724 | 2020-01-30 18:13 | 2020-01-30 19:03 | 49.83 | 1 | 1 | 49.8333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 12831 STRATFORD DR BLDG 10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 168252 | 148427 | 6647 | 2777 | 5.7851e-05 | 1.1609e-06 | 49.8333 | 1 | 310 | Customer | 75449 | Load | Tran1phPad | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011466 | PD-01302020-00454 | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2824 | 312824 | 2020-01-30 19:01 | 2020-01-30 20:54 | 112.58 | 1 | 3 | 16.8167 | 12 | POOR CONNECTION | 50 | CONNECTOR | MUSKOGEE | 1606 S.ABERDEEN | CMI_NORMAL | NO | NO | NO | 861407 | 74073 | 33285 | 5278 | 1612 | 1.9522e-05 | 1.1609e-06 | 16.8167 | 1 | 310 | Customer | 5199 | Load | Tran1phOH | REID R WILLIAMS | 512-618-8800 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-30 | 2020 |  | OK - 2020
J2001.011468 | PD-01302020-00458 | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_523 | 890523 | 2020-01-30 19:21 | 2020-01-30 21:55 | 153.87 | 1 | 1 | 146.1167 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | EL RENO | 38 SKYVIEW TRAILER | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861407 | 128854 | 12772 | 6953 | 1251 | 0.00016963 | 1.1609e-06 | 146.1167 | 1 | 320 | Customer | 38795 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011470 | PD-01302020-00456 | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9871 | 839871 | 2020-01-30 19:26 | 2020-01-31 04:48 | 561.9 | 26 | 33 | 5016.525 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | WESTERN & WISTER COVE | CMI_NORMAL | NO | NO | NO | 861407 | 168252 | 148427 | 10660 | 2048 | 0.0058236 | 3.0183e-05 | 192.9433 | 1 | 310 | Mainline | 102017 | Fuse | FuseRiser | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | OK - 2022
J2001.011471 | PD-01302020-00457 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-01-30 19:35 | 2020-01-30 21:43 | 127.48 | 1 | 1 | 2.4833 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 1444 NW.95 | CMI_NORMAL | NO | NO | NO | 861407 | 168252 | 148427 | 8788 | 1952 | 2.8829e-06 | 1.1609e-06 | 2.4833 | 1 | 320 | Customer | 23395 | Load | Tran1phOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | OK - 2021
J2001.011483 |  | METRO WEST | WEST | 8335:BETHANY | BETHANY_3527 | 833527 | 2020-01-30 21:24 | 2020-01-30 21:31 | 6.52 | 1 | 1 | 6.5167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | WARR ACRES | 4511 NW.42 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 128854 | 116082 | 7873 | 1664 | 7.5651e-06 | 1.1609e-06 | 6.5167 | 1 | 310 | Customer | 18461 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | OK - 2022
J2001.011488 | PD-01302020-00470 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4033 | 834033 | 2020-01-30 21:53 | 2020-01-31 00:16 | 142.88 | 1 | 1 | 125.2667 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 7324 NW 105th Street | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861407 | 128854 | 116082 | 10844 | 1115 | 0.00014542 | 1.1609e-06 | 125.2667 | 1 | 310 | Customer | 63042 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | #N/A
J2001.011492 | PD-01302020-00472 | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 22 | 570822 | 2020-01-30 22:06 | 2020-01-30 23:24 | 78.02 | 4 | 6 | 232.1333 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | DAVIS | 608 S. 2ND | CMI_NORMAL | NO | NO | NO | 861407 | 77632 | 6816 | 1859 | 955 | 0.00026948 | 4.6436e-06 | 58.0333 | 1 | 310 | Secondary | 4494 | Load | Tran1phOH | CHAD A DOTSON | 405-488-5658 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-30 | 2020 |  | OK - 2021
J2001.011493 |  | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3729 | 833729 | 2020-01-30 22:18 | 2020-01-30 22:26 | 8.08 | 1 | 1 | 8.0833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1005 NW.87 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861407 | 168252 | 148427 | 5767 | 1401 | 9.3839e-06 | 1.1609e-06 | 8.0833 | 1 | 310 | Customer | 35597 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-30 | 2020 |  | OK - 2021
J2001.011531 | PD-01312020-00009 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-01-31 05:49 | 2020-01-31 07:10 | 80.97 | 146 | 44 | 12057.1667 | 5 | ELECTRICAL TRACKING | 2 | TRANSFORMER OH | MOUNTAINBURG | 71 150 S. PIGEON CREEK | CMI_NORMAL | NO | NO | NO | 861497 | 82263 | 61222 | 3791 | 2586 | 0.013996 | 0.00016947 | 82.5833 | 1 | 310 | Mainline | 251208 | Fuse | FuseRiser | MICHAEL L NEWMAN | 479-221-7071 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-31 | 2020 |  | Ark - Series 2
J2001.011547 | PD-01312020-00033 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1935 | 851935 | 2020-01-31 08:15 | 2020-01-31 10:34 | 138.87 | 1 | 1 | 138.8667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 3808 N.SHADYWOOD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 114408 | 71204 | 12446 | 2158 | 0.00016119 | 1.1608e-06 | 138.8667 | 1 | 310 | Customer | 40467 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011552 |  | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_524 | 560524 | 2020-01-31 08:18 | 2020-01-31 08:32 | 14.42 | 1 | 1 | 14.4167 | 1 | CANCELLED | 57 | CANCELLED | PAULS VALLEY | 321 E MARTIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 77632 | 6211 | 2460 | 603 | 1.6734e-05 | 1.1608e-06 | 14.4167 | 1 | 310 | Customer | 2357 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | OK - 2022
J2001.011555 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-01-31 08:26 | 2020-01-31 09:23 | 57.58 | 2 | 1 | 77.9 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 2/3 MS.SE.89 + ANDERSON | CMI_PLANNED | YES | NO | NO | 861497 | 159197 | 57007 | 4239 | 1005 | 9.0424e-05 | 2.3215e-06 | 38.95 | 1 | 308 | Load | 83316 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011556 | PD-01312020-00060 | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9871 | 839871 | 2020-01-31 08:28 | 2020-01-31 14:59 | 391.48 | 1 | 2 | 75.2 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 15817 LACEBARK LANE | CMI_NORMAL | NO | NO | NO | 861497 | 168252 | 148427 | 10660 | 2048 | 8.729e-05 | 1.1608e-06 | 75.2 | 1 | 310 | Customer | 198994 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | OK - 2022
J2001.011557 | PD-01312020-00048 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3022 | 743022 | 2020-01-31 08:29 | 2020-01-31 09:31 | 62.02 | 1 | 1 | 62.0167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SHAWNEE | 712 W.KIRK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 114408 | 22122 | 6650 | 2170 | 7.1987e-05 | 1.1608e-06 | 62.0167 | 1 | 310 | Customer | 2841 | Load | TranOpenDelta | STEVEN CASKEY | 405-777-8855 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | OK - 2020
J2001.011563 | PD-01312020-00077 | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2124 | 332124 | 2020-01-31 08:30 | 2020-01-31 09:52 | 82.32 | 5 | 6 | 389.8333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | FORT GIBSON | FT GIBSON | CMI_NORMAL | NO | NO | NO | 861497 | 74073 | 33285 | 3337 | 1221 | 0.00045251 | 5.8039e-06 | 77.9667 | 1 | 310 | Load | 8422 | Load | Tran1phOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-01-31 | 2020 |  | #N/A
J2001.011559 | PD-01312020-00055 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9929 | 829929 | 2020-01-31 08:31 | 2020-01-31 09:38 | 66.87 | 1 | 2 | 66.8667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BETHANY | 7912 NW.21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 128854 | 116082 | 9233 | 2209 | 7.7617e-05 | 1.1608e-06 | 66.8667 | 1 | 310 | Customer | 38698 | Load | Tran1phPad | BRANDON H SMITH | 405-371-4294 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011560 | PD-01312020-00059 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2129 | 822129 | 2020-01-31 08:34 | 2020-01-31 10:08 | 93.95 | 1 | 2 | 31.2667 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 4308 NW.19 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861497 | 168252 | 148427 | 9251 | 1559 | 3.6293e-05 | 1.1608e-06 | 31.2667 | 1 | 310 | Customer | 30928 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | OK - 2020
J2001.011561 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-01-31 08:35 | 2020-01-31 12:18 | 222.43 | 4 | 3 | 889.6723 | 4 | DETERIORATION | 12 | POLE | POCOLA | STATE LINE RD | CMI_PLANNED | YES | NO | NO | 861497 | 82263 | 61222 | 1457 | 1239 | 0.0010327 | 4.6431e-06 | 222.4181 | 1 | 308 | Load | 13769 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | Ark - Series 2
J2001.011564 |  | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2524 | 512524 | 2020-01-31 08:44 | 2020-01-31 11:00 | 135.28 | 1 | 1 | 122.1833 | 4 | DETERIORATION | 12 | POLE | LONE GROVE | 459 CASE | CMI_PLANNED | YES | NO | NO | 861497 | 77632 | 23592 | 3307 | 1001 | 0.00014183 | 1.1608e-06 | 122.1833 | 1 | 308 | Tap | 329800 | Fuse | FuseRiser | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011572 |  | METRO WEST | WEST | 8321:PIEDMONT | PIEDMONT_2162 | 832162 | 2020-01-31 09:10 | 2020-01-31 13:07 | 236.93 | 35 | 0 | 8293.0032 | 4 | DETERIORATION | 16 | LINE RECLOSER | 0 | W OF HEFNER + CIMARRON | CMI_NORMAL | NO | NO | NO | 861497 | 128854 | 116082 | 6295 | 1630 | 0.0096263 | 4.0627e-05 | 236.9429 | 1 | 0 | Mainline | 18086 | Recloser | Rec3phHydralic | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011575 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-01-31 09:13 | 2020-01-31 12:54 | 221.07 | 2 | 2 | 405.6167 | 4 | DETERIORATION | 12 | POLE | LAMAR | LAMAR AR | CMI_PLANNED | YES | NO | NO | 861497 | 82263 | 7546 | 730 | 0 | 0.00047083 | 2.3215e-06 | 202.8083 | 1 | 308 | Load | 9984 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | #N/A
J2001.011579 | PD-01312020-00110 | METRO WEST | WEST | 8335:BETHANY | BETHANY_3526 | 833526 | 2020-01-31 09:14 | 2020-01-31 10:29 | 74.87 | 1 | 1 | 34.3609 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | BETHANY | 4601 CENTRAL RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 128854 | 116082 | 7873 | 2061 | 3.9885e-05 | 1.1608e-06 | 34.3609 | 1 | 310 | Customer | 19976 | Load | Tran1phOH | BRANDON H SMITH | 405-371-4294 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | #N/A
J2001.011582 |  | METRO WEST | WEST | 8335:BETHANY | BETHANY_3526 | 833526 | 2020-01-31 09:15 | 2020-01-31 12:46 | 210.63 | 4 | 5 | 360.9333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | WARR ACRES | 5925 NW.50 | CMI_NORMAL | NO | NO | NO | 861497 | 128854 | 116082 | 7873 | 2061 | 0.00041896 | 4.6431e-06 | 90.2333 | 1 | 310 | Load | 4463 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | #N/A
J2001.011578 | PD-01312020-00107 | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-01-31 09:16 | 2020-01-31 10:03 | 47.32 | 1 | 1 | 47.3167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7626 NW.10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 128854 | 116082 | 3409 | 2038 | 5.4924e-05 | 1.1608e-06 | 47.3167 | 1 | 310 | Customer | 41080 | Load | Tran1phPad | BRANDON H SMITH | 405-371-4294 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011580 |  | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1721 | 911721 | 2020-01-31 09:16 | 2020-01-31 11:39 | 143.2 | 1 | 1 | 143.2 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | lot 60 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 82263 | 61222 | 4241 | 209 | 0.00016622 | 1.1608e-06 | 143.2 | 1 | 310 | Customer | 400583 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-31 | 2020 |  | #N/A
J2001.011581 | PD-01312020-00085 | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2173 | 862173 | 2020-01-31 09:17 | 2020-01-31 14:46 | 329.33 | 1 | 1 | 319.05 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | NORMAN | 5903 DIXON | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861497 | 159197 | 57007 | 4239 | 164 | 0.00037034 | 1.1608e-06 | 319.05 | 1 | 310 | Customer | 71034 | Load | Tran1phOH | CHAD W GLEAVE | 405-250-7464 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011584 | PD-01312020-00126 | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_622 | 770622 | 2020-01-31 09:20 | 2020-01-31 11:57 | 156.9 | 1 | 1 | 156.1075 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | BRISTOW | 6MN 1/4MW | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861497 | 74073 | 40788 | 3783 | 2010 | 0.0001812 | 1.1608e-06 | 156.1075 | 1 | 310 | Customer | 17213 | Load | Tran1phOH | GREGORY R HOOVER | 918-261-6803 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | #N/A
J2001.011586 |  | METRO NORTH | NORTH | 8493:KELLEY AVE | KELLEY_AVENUE_9329 | 849329 | 2020-01-31 09:23 | 2020-01-31 09:23 | 0 | 234 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 9909 N KELLY AVE | CMI_MOMENTARY | YES | NO | NO | 861497 | 168252 | 148427 | 1481 | 422 | 0 | 0.00027162 | 0 | 1 | 0 | Feeder | KELLY AV_9329 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011588 |  | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1222 | 911222 | 2020-01-31 09:23 | 2020-01-31 09:51 | 28.37 | 1 | 1 | 28.3667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 801 LEXINGTON AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 82263 | 61222 | 6601 | 1289 | 3.2927e-05 | 1.1608e-06 | 28.3667 | 1 | 310 | Customer | 615 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | Ark - Series 1
J2001.011587 | PD-01312020-00109 | NORTHWEST | ENID | 4353:OTTER | OTTER_5341 | 435341 | 2020-01-31 09:24 | 2020-01-31 11:59 | 155.47 | 1 | 1 | 155.4667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MARSHALL | 2S,3W NE COR MARSHALL | CMI_NORMAL | NO | NO | NO | 861497 | 53553 | 37604 | 960 | 792 | 0.00018046 | 1.1608e-06 | 155.4667 | 1 | 310 | Load | 14426 | Load | Tran1phOH | STEVEN LORENZ | 580-822-3566 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | OK - 2021
J2001.011591 | PD-01312020-00123 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2129 | 822129 | 2020-01-31 09:34 | 2020-01-31 10:33 | 59.12 | 3 | 2 | 169.05 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2813 N.WARREN | CMI_NORMAL | NO | NO | NO | 861497 | 168252 | 148427 | 9251 | 1559 | 0.00019623 | 3.4823e-06 | 56.35 | 1 | 310 | Load | 27688 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | OK - 2020
J2001.011596 | PD-01312020-00125 | METRO NORTH | NORTH | 8493:KELLEY AVE | KELLEY_AVENUE_9329 | 849329 | 2020-01-31 09:40 | 2020-01-31 10:53 | 72.85 | 4 | 4 | 285.4 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 225 ALLENHURST | CMI_NORMAL | NO | NO | NO | 861497 | 168252 | 148427 | 1481 | 422 | 0.00033128 | 4.6431e-06 | 71.35 | 1 | 310 | Secondary | 21834 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011599 |  | ARKANSAS | FORT SMITH | 9111:MASSARD | MASSARD_1121 | 911121 | 2020-01-31 09:51 | 2020-01-31 14:04 | 253.37 | 6 | 11 | 465.2 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 5808 S.GARY,ENID PLACE ADDITON | CMI_PLANNED | YES | NO | NO | 861497 | 82263 | 61222 | 4985 | 1019 | 0.00053999 | 6.9646e-06 | 77.5333 | 1 | 308 | Load | 3428 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-31 | 2020 |  | Ark - Series 3
J2001.011609 | PD-01312020-00172 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_723 | 870723 | 2020-01-31 10:18 | 2020-01-31 11:40 | 82.35 | 7 | 8 | 543.7833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | NORMAN | 1710 OAKCLIFF RD | CMI_NORMAL | NO | NO | NO | 861497 | 159197 | 57007 | 11834 | 2044 | 0.00063121 | 8.1254e-06 | 77.6833 | 1 | 310 | Load | 48526 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011608 | PD-01312020-00166 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9921 | 829921 | 2020-01-31 10:20 | 2020-01-31 10:52 | 32.3 | 1 | 1 | 32.3 | 13 | PREMATURE FAILURE | 15 | METER - SECONDARY | BETHANY | 6504 NW.22 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861497 | 128854 | 116082 | 9233 | 1636 | 3.7493e-05 | 1.1608e-06 | 32.3 | 1 | 320 | Customer | 23401 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011620 | PD-01312020-00200 | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9871 | 839871 | 2020-01-31 10:32 | 2020-01-31 17:18 | 405.65 | 17 | 12 | 2727.7917 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | WESTERN & WISTER COVE | CMI_NORMAL | NO | NO | NO | 861497 | 168252 | 148427 | 10660 | 2048 | 0.0031663 | 1.9733e-05 | 160.4583 | 1 | 310 | Mainline | 101280 | Fuse | FuseRiser | CORY J HUFFMAN | 870-668-0377 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | OK - 2022
J2001.011613 | PD-01312020-00179 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-01-31 10:34 | 2020-01-31 14:53 | 259.3 | 1 | 1 | 248.5333 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | DEL CITY | 4704 SE.27 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861497 | 159197 | 102190 | 7418 | 2240 | 0.00028849 | 1.1608e-06 | 248.5333 | 1 | 320 | Customer | 6234 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | OK - 2022
J2001.011617 |  | METRO EAST | SHAWNEE | 7412:PEARSON | PEARSON 21 | 741221 | 2020-01-31 10:42 | 2020-01-31 13:37 | 174.87 | 1 | 1 | 21.0667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | ASHER | 1MW OF ASHER ON HWY 39, NS | CMI_PLANNED | YES | NO | NO | 861497 | 114408 | 22122 | 678 | 678 | 2.4454e-05 | 1.1608e-06 | 21.0667 | 1 | 308 | Tap | 231295 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | OK - 2021
J2001.011629 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-01-31 10:45 | 2020-01-31 14:47 | 241.52 | 3 | 3 | 445.75 | 4 | DETERIORATION | 12 | POLE | BIXBY | 24 E MCKENNON | CMI_PLANNED | YES | NO | NO | 861497 | 74073 | 40788 | 2753 | 1441 | 0.00051741 | 3.4823e-06 | 148.5833 | 1 | 308 | Load | 41167 | Load | TranOpenDelta | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | OK - 2021
J2001.011627 | PD-01312020-00202 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6121 | 836121 | 2020-01-31 11:00 | 2020-01-31 11:28 | 28.3 | 1 | 1 | 28.3 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3511 N.FLORIDA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 168252 | 148427 | 11128 | 1638 | 3.285e-05 | 1.1608e-06 | 28.3 | 1 | 310 | Customer | 18584 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | OK - 2021
J2001.011631 | PD-01312020-00207 | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-01-31 11:04 | 2020-01-31 12:52 | 108.17 | 1 | 1 | 3.9333 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 11300 RYAN DR | CMI_NORMAL | NO | NO | NO | 861497 | 159197 | 57007 | 4239 | 3070 | 4.5657e-06 | 1.1608e-06 | 3.9333 | 1 | 310 | Load | 83329 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011636 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_721 | 870721 | 2020-01-31 11:11 | 2020-01-31 15:37 | 265.88 | 10 | 2 | 624 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | NORMAN | 1714 SHEFFIELD | CMI_PLANNED | YES | NO | NO | 861497 | 159197 | 57007 | 11834 | 1683 | 0.00072432 | 1.1608e-05 | 62.4 | 1 | 308 | Load | 33150 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011635 |  | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_524 | 560524 | 2020-01-31 11:12 | 2020-01-31 13:55 | 163.35 | 5 | 4 | 143.7917 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | PAULS VALLEY | 321 E MARTIN | CMI_NORMAL | NO | NO | NO | 861497 | 77632 | 6211 | 2460 | 603 | 0.00016691 | 5.8039e-06 | 28.7583 | 1 | 308 | Load | 2357 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | OK - 2022
J2001.011640 | PD-01312020-00233 | ARKANSAS | OZARK | 9412:ALTUS | ALTUS_1229 | 941229 | 2020-01-31 11:29 | 2020-01-31 13:04 | 95.45 | 1 | 1 | 95.45 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OZARK | 1 M. SOUTH POND CREEK 1/4M. W. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 82263 | 7546 | 866 | 866 | 0.0001108 | 1.1608e-06 | 95.45 | 1 | 310 | Load | 17744 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-31 | 2020 |  | Ark - Series 2
J2001.011655 | PD-01312020-00241 | METRO EAST | EAST | 8416:DUNJEE | DUNJEE_1623 | 841623 | 2020-01-31 11:52 | 2020-01-31 13:21 | 88.87 | 1 | 1 | 88.8667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NICOMA PARK | 10818 NE.16 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 114408 | 71204 | 3540 | 1989 | 0.00010315 | 1.1608e-06 | 88.8667 | 1 | 310 | Customer | 5498 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011654 |  | SOUTHERN | HEALDTON | 5309:POOLEVILLE | POOLEVILLE_927 | 530927 | 2020-01-31 11:54 | 2020-01-31 13:14 | 80.05 | 2 | 0 | 146.4333 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | 0 | 7-76 2S 4E SS | CMI_PLANNED | YES | NO | NO | 861497 | 77632 | 6800 | 400 | 141 | 0.00016998 | 2.3215e-06 | 73.2167 | 1 | 0 | Load | 24982 | Load | Tran3phWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011664 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-01-31 11:54 | 2020-01-31 12:40 | 46.15 | 8 | 5 | 284 | 5 | ELECTRICAL TRACKING | 34 | CONDUCTOR SECONDARY - OH | FORT SMITH | CAVANAUGH | CMI_NORMAL | NO | NO | NO | 861497 | 82263 | 61222 | 1457 | 1239 | 0.00032966 | 9.2862e-06 | 35.5 | 1 | 308 | Load | 7975 | Load | Tran1phOH | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | Ark - Series 2
J2001.011665 |  | METRO SOUTH | SOUTH CENTRAL | 8723:INDIAN HILL | INDIAN_HILL_2323 | 872323 | 2020-01-31 12:04 | 2020-01-31 14:29 | 144.6 | 3 | 2 | 89.85 | 4 | DETERIORATION | 2 | TRANSFORMER OH | MOORE | 4000 S BRYANT AV | CMI_PLANNED | YES | NO | NO | 861497 | 159197 | 102190 | 3192 | 1453 | 0.0001043 | 3.4823e-06 | 29.95 | 1 | 308 | Load | 39295 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011666 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-01-31 12:26 | 2020-01-31 16:34 | 248.12 | 1 | 1 | 234.7833 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | 10100 WOODVIEW DR | CMI_PLANNED | YES | NO | NO | 861497 | 159197 | 57007 | 4239 | 1005 | 0.00027253 | 1.1608e-06 | 234.7833 | 1 | 308 | Load | 52390 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011668 |  | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2524 | 512524 | 2020-01-31 12:32 | 2020-01-31 14:19 | 107.15 | 3 | 2 | 307.75 | 4 | DETERIORATION | 12 | POLE | LONE GROVE | W CASE RD .5N HWY 70 | CMI_PLANNED | YES | NO | NO | 861497 | 77632 | 23592 | 3307 | 1001 | 0.00035723 | 3.4823e-06 | 102.5833 | 1 | 308 | Load | 29792 | Load | TranOpenDelta | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011670 | PD-01312020-00264 | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2129 | 332129 | 2020-01-31 12:33 | 2020-01-31 13:55 | 82.43 | 1 | 1 | 82.4333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT GIBSON | 1558 KREIDER ROAD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 74073 | 33285 | 3337 | 942 | 9.5686e-05 | 1.1608e-06 | 82.4333 | 1 | 320 | Load | 20903 | Load | Tran1phOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-31 | 2020 |  | #N/A
J2001.011678 | PD-01312020-00277 | NORTHEAST | SAPULPA | 3207:HILL TOP | HILL TOP 23 | 320723 | 2020-01-31 12:59 | 2020-01-31 21:23 | 503.75 | 1 | 1 | 503.75 | 3 | DAMAGED BY PUBLIC | 12 | POLE | GLENPOOL | FERN PL. + 140TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 74073 | 40788 | 993 | 412 | 0.00058474 | 1.1608e-06 | 503.75 | 1 | 310 | Customer | 40985 | Load | Tran1phPad | JOSHUA N MCKINNEY | 918-863-6313 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | #N/A
J2001.011686 | PD-01312020-00282 | NORTHWEST | ENID | 4157:NE ENID | NE_ENID_5723 | 415723 | 2020-01-31 13:10 | 2020-01-31 14:02 | 52.5 | 1 | 1 | 52.5 | 12 | POOR CONNECTION | 50 | CONNECTOR | NORTH ENID | 3/4 N BRECKENRIDGE RD & 16TH | CMI_NORMAL | NO | NO | NO | 861497 | 53553 | 37604 | 1558 | 1311 | 6.094e-05 | 1.1608e-06 | 52.5 | 1 | 320 | Load | 193159 | Load | Tran1phOH | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011688 | PD-01312020-00285 | METRO EAST | SEMINOLE | 7311:BURNETT | BURNETT 21 | 731121 | 2020-01-31 13:17 | 2020-01-31 14:24 | 67.23 | 1 | 1 | 67.2333 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | PRAGUE | 2MW & 3MN OF PADEN | CMI_NORMAL | NO | NO | NO | 861497 | 114408 | 13613 | 44 | 44 | 7.8042e-05 | 1.1608e-06 | 67.2333 | 1 | 310 | Load | 241059 | Load | Tran1phOH | BRADY A HUFF | 405-519-0701 | [5 empty] | Weather | N | DISTRIBUTION | 24.9kV | 2020-01-31 | 2020 |  | #N/A
J2001.011689 | PD-01312020-00291 | NORTHWEST | ALVA | 4707:KNOBHILL | KNOBHILL_732 | 470732 | 2020-01-31 13:20 | 2020-01-31 15:38 | 137.93 | 1 | 1 | 137.9333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ALVA | 1141 8TH-ALVA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 53553 | 5520 | 1743 | 354 | 0.00016011 | 1.1608e-06 | 137.9333 | 1 | 310 | Customer | 9517 | Load | TranOpenDelta | DENNIS PEARSON | 580-541-4106 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | #N/A
J2001.011693 | PD-01312020-00297 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1122 | 511122 | 2020-01-31 13:34 | 2020-01-31 15:24 | 109.68 | 1 | 1 | 109.6833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DICKSON | GA RD/199 .5E SS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 77632 | 23592 | 2209 | 1207 | 0.00012732 | 1.1608e-06 | 109.6833 | 1 | 310 | Load | 31010 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011698 | PD-01312020-00307 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-01-31 13:59 | 2020-01-31 15:12 | 73.38 | 1 | 1 | 42.1333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ARDMORE | MANTOOTH HOMES 61 | CMI_NORMAL | NO | NO | NO | 861497 | 77632 | 23592 | 2209 | 1002 | 4.8907e-05 | 1.1608e-06 | 42.1333 | 1 | 310 | Load | 23008 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011700 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6121 | 836121 | 2020-01-31 14:08 | 2020-01-31 14:42 | 34.28 | 1 | 1 | 34.2833 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1621 NW.32 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 168252 | 148427 | 11128 | 1638 | 3.9795e-05 | 1.1608e-06 | 34.2833 | 1 | 310 | Customer | 345 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | OK - 2021
J2001.011706 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-01-31 14:22 | 2020-01-31 18:08 | 225.28 | 1 | 1 | 224.05 | 4 | DETERIORATION | 12 | POLE | ARKOMA | 729.5 MAIN | CMI_PLANNED | YES | NO | NO | 861497 | 82263 | 61222 | 2938 | 876 | 0.00026007 | 1.1608e-06 | 224.05 | 1 | 308 | Load | 9722 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-01-31 | 2020 |  | Ark - Series 2
J2001.011708 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-01-31 14:25 | 2020-01-31 14:35 | 10.02 | 1 | 1 | 10.0167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | LAVACA | LAVACA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 82263 | 61222 | 2739 | 2127 | 1.1627e-05 | 1.1608e-06 | 10.0167 | 1 | 310 | Customer | 13031 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | Ark - Series 2
J2001.011717 |  | METRO NORTH | NORTH | 8493:KELLEY AVE | KELLEY_AVENUE_9331 | 849331 | 2020-01-31 14:46 | 2020-01-31 14:54 | 8.35 | 1 | 1 | 8.35 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 15 NE.67 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 168252 | 148427 | 1481 | 1059 | 9.6924e-06 | 1.1608e-06 | 8.35 | 1 | 310 | Customer | 18741 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011721 | PD-01312020-00335 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4029 | 834029 | 2020-01-31 14:55 | 2020-01-31 17:06 | 131.45 | 1 | 1 | 122.4167 | 3 | DAMAGED BY PUBLIC | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 7312 NW.120 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 128854 | 116082 | 10844 | 1146 | 0.0001421 | 1.1608e-06 | 122.4167 | 1 | 310 | Customer | 65955 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011723 |  | ARKANSAS | OZARK | 9224:BRANCH | BRANCH_2463 | 922463 | 2020-01-31 14:58 | 2020-01-31 16:44 | 106.72 | 1 | 1 | 78.75 | 1 | CANCELLED | 57 | CANCELLED | RATCLIFF | Hwy 22, ns, County Line School | CMI_PLANNED | YES | NO | NO | 861497 | 82263 | 7546 | 1796 | 822 | 9.1411e-05 | 1.1608e-06 | 78.75 | 1 | 308 | Tap | 259148 | Fuse | FuseRiser | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-01-31 | 2020 |  | Ark - Series 3
J2001.011724 |  | METRO EAST | EAST | 8417:ROUND BARN | ROUND_BARN_1723 | 841723 | 2020-01-31 15:07 | 2020-01-31 15:20 | 12.72 | 1 | 1 | 12.7167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | GUTHRIE | L3 WATERLOO VALLEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 114408 | 71204 | 1007 | 1007 | 1.4761e-05 | 1.1608e-06 | 12.7167 | 1 | 310 | Customer | 72353 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011730 | PD-01312020-00382 | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2224 | 882224 | 2020-01-31 15:27 | 2020-01-31 16:53 | 86.03 | 15 | 5 | 1270.25 | 28 | OTHER (DESCRIBE) | 23 | FUSE - PRIMARY | EDMOND | 6SPS WATERLOO + BLUESA | CMI_NORMAL | NO | NO | NO | 861497 | 168252 | 19825 | 5385 | 1850 | 0.0014745 | 1.7412e-05 | 84.6833 | 1 | 310 | Tap | 35339 | Fuse | FuseOH | JERRY CASNER | 405-620-0772 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011734 |  | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2224 | 882224 | 2020-01-31 15:28 | 2020-01-31 15:58 | 29.62 | 1 | 1 | 29.6167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | GUTHRIE | 4508 VALLEY-VIEW LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 168252 | 19825 | 5385 | 1850 | 3.4378e-05 | 1.1608e-06 | 29.6167 | 1 | 310 | Customer | 68482 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011735 | PD-01312020-00373 | METRO NORTH | NORTH | 8347:WILSHIRE | WILSHIRE_4724 | 834724 | 2020-01-31 15:29 | 2020-01-31 17:42 | 133.25 | 1 | 1 | 133.25 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 8208 LAKEHURST DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 168252 | 148427 | 4624 | 1008 | 0.00015467 | 1.1608e-06 | 133.25 | 1 | 320 | Customer | 27605 | Load | Tran1phOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011732 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1022 | 541022 | 2020-01-31 15:30 | 2020-01-31 15:56 | 26.1 | 1 | 1 | 26.1 | 1 | CANCELLED | 57 | CANCELLED | MADILL | 105 PARKVIEW COURT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 77632 | 7198 | 2379 | 873 | 3.0296e-05 | 1.1608e-06 | 26.1 | 1 | 310 | Customer | 3404 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011740 |  | ARKANSAS | POTEAU | 3506:CAVANAL MTN | CAVANAL MTN 21 | 350621 | 2020-01-31 15:38 | 2020-01-31 15:54 | 16.38 | 1 | 1 | 16.3833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | POTEAU | 110 FERN DR, POTEAU | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 82263 | 13495 | 2052 | 707 | 1.9017e-05 | 1.1608e-06 | 16.3833 | 1 | 310 | Customer | 11225 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | #N/A
J2001.011748 | PD-01312020-00385 | METRO WEST | EL RENO | 8908:ROMAN NOSE | ROMAN_NOSE_852 | 890852 | 2020-01-31 15:58 | 2020-01-31 17:42 | 104.3 | 2 | 2 | 200.7333 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | LOYAL | ACR S HIGH SCHOOL | CMI_NORMAL | NO | NO | NO | 861497 | 128854 | 12772 | 526 | 257 | 0.00023301 | 2.3215e-06 | 100.3667 | 1 | 310 | Secondary | 30455 | Load | Tran1phOH | BRANDON H SMITH | 405-371-4294 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011757 |  | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2222 | 832222 | 2020-01-31 16:32 | 2020-01-31 17:36 | 64.18 | 22 | 25 | 1181.0333 | 29 | TREES : GROW IN | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | 3951 ALTADENA AVE, OKC | CMI_NORMAL | NO | NO | NO | 861497 | 168252 | 148427 | 9176 | 1557 | 0.0013709 | 2.5537e-05 | 53.6833 | 1 | 310 | Tap | 17110 | Fuse | FuseOH | Crew | [6 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | OK - 2022
J2001.011771 |  | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_923 | 910923 | 2020-01-31 17:32 | 2020-01-31 17:47 | 14.63 | 1 | 1 | 14.6333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ARKOMA | STATE LINE RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 82263 | 61222 | 5013 | 901 | 1.6986e-05 | 1.1608e-06 | 14.6333 | 1 | 310 | Customer | 8009 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | Ark - Series 3
J2001.011778 |  | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3221 | 813221 | 2020-01-31 17:47 | 2020-01-31 17:59 | 11.58 | 1 | 1 | 11.5833 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1328 MAGDALENA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 159197 | 102190 | 7607 | 2076 | 1.3446e-05 | 1.1608e-06 | 11.5833 | 1 | 310 | Customer | 7905 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | #N/A
J2001.011780 | PD-01312020-00426 | METRO WEST | WEST | 8150:HOBBY LOBBY | HOBBY_LOBBY_5062 | 815062 | 2020-01-31 17:52 | 2020-01-31 18:36 | 44.35 | 8 | 9 | 338.5333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2716 BATES | CMI_NORMAL | NO | NO | NO | 861497 | 128854 | 116082 | 2510 | 853 | 0.00039296 | 9.2862e-06 | 42.3167 | 1 | 310 | Load | 47616 | Load | Tran1phOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011781 | PD-01312020-00427 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-01-31 17:54 | 2020-01-31 19:09 | 74.47 | 22 | 8 | 815.8333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 225 NW.24 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 168252 | 148427 | 11128 | 2339 | 0.00094699 | 2.5537e-05 | 37.0833 | 1 | 310 | Load | 2231 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | OK - 2020
J2001.011783 | PD-01312020-00428 | METRO SOUTH | SOUTH CENTRAL | 8194:WESTMOORE | WESTMOORE_9431 | 819431 | 2020-01-31 18:05 | 2020-01-31 20:38 | 153.45 | 1 | 1 | 151.0167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 12500 S.WESTERN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 159209 | 102197 | 8106 | 1536 | 0.0001753 | 1.1608e-06 | 151.0167 | 1 | 310 | Customer | 74102 | Load | Tran1phPad | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011785 |  | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2922 | 812922 | 2020-01-31 18:10 | 2020-01-31 18:20 | 9.97 | 1 | 1 | 9.9667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3841 SW.40 PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 159209 | 102197 | 6386 | 1137 | 1.1569e-05 | 1.1608e-06 | 9.9667 | 1 | 310 | Customer | 12380 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | #N/A
J2001.011801 | PD-01312020-00434 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1229 | 831229 | 2020-01-31 19:31 | 2020-01-31 20:07 | 36.2 | 1 | 1 | 36.2 | 28 | OTHER (DESCRIBE) | 23 | FUSE - PRIMARY | OKLAHOMA CITY | 4200 N PENN | CMI_NORMAL | NO | NO | NO | 861497 | 168268 | 148442 | 7752 | 787 | 4.202e-05 | 1.1608e-06 | 36.2 | 1 | 310 | Load | 84622 | Load | Tran3phPadWye | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | OK - 2022
J2001.011802 |  | METRO NORTH | GUTHRIE | 8814:PINE STREET | PINE_STREET_1424 | 881424 | 2020-01-31 19:43 | 2020-01-31 19:50 | 7.15 | 1 | 1 | 7.15 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | GUTHRIE | 624 E.NOBLE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 168268 | 19826 | 3103 | 1238 | 8.2995e-06 | 1.1608e-06 | 7.15 | 1 | 310 | Customer | 40183 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011816 |  | METRO SOUTH | SOUTH CENTRAL | 8194:WESTMOORE | WESTMOORE_9431 | 819431 | 2020-01-31 20:09 | 2020-01-31 20:45 | 36.4 | 1 | 1 | 26.7167 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 12500 S.WESTERN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 159209 | 102197 | 8106 | 1536 | 3.1012e-05 | 1.1608e-06 | 26.7167 | 1 | 310 | Customer | 74102 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2001.011815 |  | NORTHEAST | SAPULPA | 3207:HILL TOP | HILL TOP 23 | 320723 | 2020-01-31 20:09 | 2020-01-31 21:30 | 80.35 | 1 | 1 | 69.2167 | 3 | DAMAGED BY PUBLIC | 12 | POLE | GLENPOOL | GLENN OAKS CENTER(141+FERN PL) | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861497 | 74078 | 40793 | 993 | 412 | 8.0345e-05 | 1.1608e-06 | 69.2167 | 1 | 310 | Customer | 43800 | Load | Tran3phPadWye | Ties | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-01-31 | 2020 |  | #N/A
J2001.011817 | PD-01312020-00445 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4033 | 834033 | 2020-01-31 20:18 | 2020-01-31 21:29 | 70.88 | 1 | 1 | 67 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 7324 NW 105th Street | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861497 | 128878 | 116105 | 10844 | 1115 | 7.7772e-05 | 1.1608e-06 | 67 | 1 | 310 | Customer | 63042 | Load | Tran1phPad | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-01-31 | 2020 |  | #N/A
J2002.000009 |  | NORTHWEST | ENID | 4261:WHITE EAGLE | WHITE_EAGLE_6121 | 426121 | 2020-02-01 01:57 | 2020-02-01 04:21 | 144.23 | 1 | 1 | 123.1833 | 3 | DAMAGED BY PUBLIC | 12 | POLE | PONCA CITY | 13/4S RANCH ELV | CMI_PLANNED | YES | NO | NO | 861497 | 53556 | 37604 | 215 | 215 | 0.00014299 | 1.1608e-06 | 123.1833 | 1 | 308 | Load | 4550 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000019 |  | NORTHEAST | MUSKOGEE | 3327:VIAN | VIAN 22 | 332722 | 2020-02-01 03:49 | 2020-02-01 04:26 | 36.08 | 1 | 1 | 36.0833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | VIAN | HUNTER + BONHAN (NE S) VIAN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 74078 | 33285 | 781 | 781 | 4.188e-05 | 1.1606e-06 | 36.0833 | 1 | 308 | Customer | 1474 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | OK - 2021
J2002.000035 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-02-01 07:20 | 2020-02-01 07:26 | 5.83 | 1 | 1 | 5.8333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7909 NW.7 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128878 | 116105 | 3411 | 2040 | 6.7704e-06 | 1.1606e-06 | 5.8333 | 1 | 310 | Customer | 34502 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000037 |  | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-02-01 07:34 | 2020-02-01 07:34 | 0 | 1090 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ADA | 1806 A ST | CMI_MOMENTARY | YES | NO | NO | 861594 | 77633 | 11518 | 2518 | 1090 | 0 | 0.0012651 | 0 | 1 | 0 | Feeder | VALLEY_VIEW_623 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-01 | 2020 |  | #N/A
J2002.000039 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_724 | 870724 | 2020-02-01 07:54 | 2020-02-01 07:54 | 0 | 647 | 0 | 0 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 1138 E MISSOURI ST | CMI_MOMENTARY | YES | NO | NO | 861594 | 159209 | 57012 | 11834 | 2409 | 0 | 0.00075093 | 0 | 1 | 0 | Mainline | 332720 | Recloser | Rec3phElectronic | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000044 | PD-02012020-00930 | METRO NORTH | NORTH | 8347:WILSHIRE | WILSHIRE_4721 | 834721 | 2020-02-01 07:59 | 2020-02-01 09:05 | 66.25 | 9 | 10 | 574.35 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 6304 NW.GRAND BL | CMI_NORMAL | NO | NO | NO | 861594 | 168268 | 148442 | 4624 | 927 | 0.00066661 | 1.0446e-05 | 63.8167 | 1 | 310 | Load | 14974 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | OK - 2022
J2002.000043 | PD-02012020-00925 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3923 | 833923 | 2020-02-01 08:01 | 2020-02-01 08:45 | 44.37 | 1 | 1 | 41.1 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 4932 N.PORTLAND | CMI_NORMAL | NO | NO | NO | 861594 | 168268 | 148442 | 7852 | 1247 | 4.7702e-05 | 1.1606e-06 | 41.1 | 1 | 310 | Customer | 35923 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | OK - 2022
J2002.000045 | PD-02012020-00935 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7022 | 817022 | 2020-02-01 08:05 | 2020-02-01 09:32 | 87.42 | 1 | 1 | 87.4167 | 13 | PREMATURE FAILURE | 15 | METER - SECONDARY | MOORE | 608 NW.20 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 159209 | 102197 | 9939 | 2104 | 0.00010146 | 1.1606e-06 | 87.4167 | 1 | 310 | Customer | 48117 | Load | Tran1phPad | MONTY WISELEY | 405-471-2592 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000049 | PD-02012020-00958 | METRO WEST | EL RENO | 8908:ROMAN NOSE | ROMAN_NOSE_852 | 890852 | 2020-02-01 08:09 | 2020-02-01 10:31 | 141.65 | 1 | 1 | 139.4667 | 22 | WIND | 21 | FUSE - TRANSFORMER | LOYAL | 17782 N 2730 RD | CMI_NORMAL | NO | NO | NO | 861594 | 128878 | 12773 | 525 | 257 | 0.00016187 | 1.1606e-06 | 139.4667 | 1 | 310 | Load | 401687 | Load | Tran1phOH | BRANDON H SMITH | 405-371-4294 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000051 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-01 08:15 | 2020-02-01 09:29 | 74.23 | 4 | 3 | 272.3333 | 4 | DETERIORATION | 12 | POLE | POCOLA | STATE LINE RD | CMI_PLANNED | YES | NO | NO | 861594 | 82268 | 61223 | 1457 | 1239 | 0.00031608 | 4.6426e-06 | 68.0833 | 1 | 308 | Load | 13769 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | Ark - Series 2
J2002.000052 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-01 08:15 | 2020-02-01 09:29 | 74.03 | 2 | 2 | 139.6 | 4 | DETERIORATION | 12 | POLE | POCOLA | ARKOMA OKLA | CMI_PLANNED | YES | NO | NO | 861594 | 82268 | 61223 | 1457 | 1239 | 0.00016203 | 2.3213e-06 | 69.8 | 1 | 308 | Load | 13917 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | Ark - Series 2
J2002.000054 | PD-02012020-00963 | METRO WEST | WEST | 8157:MACARTHUR | MACARTHUR_5724 | 815724 | 2020-02-01 08:18 | 2020-02-01 10:48 | 150.1 | 1 | 1 | 146.2333 | 3 | DAMAGED BY PUBLIC | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 2400 S.MACARTHUR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128878 | 116105 | 1854 | 1253 | 0.00016972 | 1.1606e-06 | 146.2333 | 1 | 310 | Customer | 38805 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | #N/A
J2002.000055 | PD-02012020-00968 | METRO SOUTH | SOUTH | 8714:LITTLE AXE | LITTLE_AXE_1421 | 871421 | 2020-02-01 08:18 | 2020-02-01 11:13 | 174.95 | 1 | 1 | 173.5667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | NORMAN | 9900 STORM-KING RD. | CMI_NORMAL | NO | NO | NO | 861594 | 159209 | 57012 | 616 | 616 | 0.00020145 | 1.1606e-06 | 173.5667 | 1 | 310 | Load | 83052 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | #N/A
J2002.000060 | PD-02012020-00986 | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_624 | 460624 | 2020-02-01 08:22 | 2020-02-01 14:03 | 340.52 | 10 | 8 | 3294.6667 | 3 | DAMAGED BY PUBLIC | 1 | TRANSFORMER UG | WOODWARD | 3125 BENT CREEK-WOODWARD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 53556 | 10430 | 5686 | 488 | 0.0038239 | 1.1606e-05 | 329.4667 | 1 | 310 | Load | 11259 | Load | Tran1phPad | KEVIN D PETTIGREW | 580-216-6305 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | #N/A
J2002.000058 |  | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_623 | 880623 | 2020-02-01 08:26 | 2020-02-01 08:26 | 0 | 1417 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | GUTHRIE | 800 W INDUSTRIAL RD | CMI_MOMENTARY | YES | NO | NO | 861594 | 168268 | 19826 | 5170 | 1417 | 0 | 0.0016446 | 0 | 1 | 0 | Feeder | COTWD CK_623 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000062 | PD-02012020-01011 | METRO EAST | SHAWNEE | 7407:REMINGTON | REMINGTON 21 | 740721 | 2020-02-01 08:27 | 2020-02-01 09:41 | 73.87 | 2 | 3 | 134.2167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | EARLSBORO | 5001 E.HIGHLAND | CMI_NORMAL | NO | NO | NO | 861594 | 114428 | 22124 | 3667 | 2022 | 0.00015578 | 2.3213e-06 | 67.1083 | 1 | 310 | Load | 10809 | Load | Tran1phOH | BRYAN K TATUM | 405-659-0746 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | OK - 2021
J2002.000069 | PD-02012020-01076 | SOUTHERN | DURANT | 5504:BUTTERFIELD | BUTTERFIELD_424 | 550424 | 2020-02-01 09:06 | 2020-02-01 09:43 | 36.68 | 1 | 1 | 36.6833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DURANT | .3N UNIVERSITY ON LARKSPUR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 77633 | 15496 | 3487 | 1029 | 4.2576e-05 | 1.1606e-06 | 36.6833 | 1 | 310 | Customer | 26714 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000072 | PD-02012020-01085 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5134 | 815134 | 2020-02-01 09:17 | 2020-02-01 10:26 | 69.05 | 1 | 1 | 69.05 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 1401 S.W. 95th CT | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 159209 | 102197 | 13937 | 2469 | 8.0142e-05 | 1.1606e-06 | 69.05 | 1 | 320 | Customer | 363882 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000076 | PD-02012020-01109 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2222 | 832222 | 2020-02-01 09:18 | 2020-02-01 12:05 | 167 | 9 | 11 | 1491.45 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 4925 N.PATE | CMI_NORMAL | NO | NO | NO | 861594 | 168268 | 148442 | 9178 | 1557 | 0.001731 | 1.0446e-05 | 165.7167 | 1 | 310 | Load | 5728 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | OK - 2022
J2002.000077 |  | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2222 | 832222 | 2020-02-01 09:18 | 2020-02-01 16:36 | 437.73 | 1 | 2 | 165.5667 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 2629 NW.49 | CMI_NORMAL | NO | NO | NO | 861594 | 168268 | 148442 | 9178 | 1557 | 0.00019216 | 1.1606e-06 | 165.5667 | 1 | 310 | Customer | 18688 | Load | Tran1phOH | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | OK - 2022
J2002.000074 |  | METRO SOUTH | SOUTH | 8728:CHERRY CREEK | CHERRY_CREEK_2823 | 872823 | 2020-02-01 09:19 | 2020-02-01 09:35 | 15.82 | 1 | 1 | 15.8167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | WS I-35 1/2 M N OF ROBINSON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159209 | 57012 | 7106 | 1300 | 1.8357e-05 | 1.1606e-06 | 15.8167 | 1 | 310 | Customer | 78116 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000080 | PD-02012020-01114 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4024 | 834024 | 2020-02-01 09:26 | 2020-02-01 16:03 | 397.65 | 30 | 30 | 9057.25 | 5 | ELECTRICAL TRACKING | 1 | TRANSFORMER UG | OKLAHOMA CITY | WESTLAKE + WESTPARK | CMI_NORMAL | NO | NO | NO | 861594 | 128878 | 116105 | 10844 | 1677 | 0.010512 | 3.4819e-05 | 301.9083 | 1 | 310 | Mainline | 29874 | Fuse | SwitchCubicleFuse | BROC ROBINSON | 405-312-1688 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000083 |  | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2924 | 812924 | 2020-02-01 09:31 | 2020-02-01 11:53 | 142.08 | 1 | 1 | 122.8667 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 2604 SW.64 | CMI_NORMAL | NO | NO | NO | 861594 | 159209 | 102197 | 6386 | 2129 | 0.0001426 | 1.1606e-06 | 122.8667 | 1 | 310 | Customer | 25754 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | #N/A
J2002.000089 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4024 | 834024 | 2020-02-01 09:36 | 2020-02-01 09:44 | 7.7 | 1 | 1 | 7.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 12421 ACADIA CT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128878 | 116105 | 10844 | 1677 | 8.9369e-06 | 1.1606e-06 | 7.7 | 1 | 310 | Customer | 63804 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000090 | PD-02012020-01132 | SOUTHERN | HEALDTON | 5322:DUNDEE | DUNDEE 22 | 532222 | 2020-02-01 09:40 | 2020-02-01 10:44 | 64.1 | 1 | 1 | 58.2 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | CORNISH | RINGLING MOTEL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 77633 | 6802 | 1014 | 1003 | 6.7549e-05 | 1.1606e-06 | 58.2 | 1 | 321 | Customer | 8882 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000096 | PD-02012020-01160 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_524 | 510524 | 2020-02-01 09:50 | 2020-02-01 10:53 | 63 | 1 | 1 | 63 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ARDMORE | 602 8 SE. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 77633 | 23592 | 4774 | 1432 | 7.312e-05 | 1.1606e-06 | 63 | 1 | 310 | Customer | 8554 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | OK - 2021
J2002.000101 | PD-02012020-01344 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1931 | 851931 | 2020-02-01 10:02 | 2020-02-01 14:17 | 254.72 | 1 | 1 | 254.7167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MIDWEST CITY | 909 ROLLING-MEADOWS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 114428 | 71221 | 12455 | 987 | 0.00029563 | 1.1606e-06 | 254.7167 | 1 | 310 | Customer | 26848 | Load | Tran1phPad | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000106 | PD-02012020-01229 | METRO NORTH | NORTH | 8535:OU MED CENTER | OU_MEDICAL_CEN_3572 | 853572 | 2020-02-01 10:17 | 2020-02-01 11:32 | 74.73 | 499 | 33 | 6541.0167 | 5 | ELECTRICAL TRACKING | 42 | TRANSFORMER - PT | OKLAHOMA CITY | 101 N LOTTIE | CMI_NORMAL | NO | NO | NO | 861594 | 168268 | 148442 | 525 | 499 | 0.0075918 | 0.00057916 | 13.1082 | 1 | 310 | Feeder | OU MED_3572 | Recloser | SubRecloser | [7 empty] | Equipment | N | SUBSTATION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000108 | PD-02012020-01220 | METRO EAST | EAST | 8697:TINKER FIELD 3 | TINKER_3_9723 | 869723 | 2020-02-01 10:22 | 2020-02-01 16:19 | 357.32 | 1 | 1 | 357.3167 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | South of Bldg 5800 | CMI_NORMAL | NO | NO | NO | 861594 | 114428 | 71221 | 68 | 40 | 0.00041472 | 1.1606e-06 | 357.3167 | 1 | 310 | Customer | 346804 | Load | Tran3phPadWye | AUSTIN WELLIVER | 405-221-0200 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000110 |  | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3925 | 833925 | 2020-02-01 10:26 | 2020-02-01 10:34 | 7.97 | 1 | 1 | 7.9667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 5334 WILLOWCLF RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168268 | 148442 | 7852 | 2183 | 9.2464e-06 | 1.1606e-06 | 7.9667 | 1 | 310 | Customer | 47742 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | OK - 2022
J2002.000114 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_863 | 830863 | 2020-02-01 10:37 | 2020-02-01 10:47 | 9.7 | 1 | 1 | 9.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1/2 M.N.OF MEMORIAL ON PENN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168268 | 148442 | 19390 | 1673 | 1.1258e-05 | 1.1606e-06 | 9.7 | 1 | 310 | Customer | 69429 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000118 | PD-02012020-01284 | METRO WEST | WEST | 8359:YUKON | YUKON_5922 | 835922 | 2020-02-01 10:51 | 2020-02-01 15:05 | 253.68 | 1 | 1 | 253.6833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | YUKON | 1200 FAIRBANKS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128878 | 116105 | 6428 | 1639 | 0.00029443 | 1.1606e-06 | 253.6833 | 1 | 310 | Customer | 27964 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | #N/A
J2002.000121 |  | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2924 | 812924 | 2020-02-01 10:52 | 2020-02-01 11:53 | 61.4 | 12 | 10 | 498.6 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 2604 SW.64 | CMI_NORMAL | NO | NO | NO | 861594 | 159209 | 102197 | 6386 | 2129 | 0.00057869 | 1.3928e-05 | 41.55 | 1 | 310 | Load | 25754 | Load | Tran1phOH | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | #N/A
J2002.000124 | PD-02012020-01317 | NORTHEAST | MUSKOGEE | 3117:THREE RIVERS | THREE_RIVERS_1721 | 311721 | 2020-02-01 11:00 | 2020-02-01 12:05 | 65.02 | 13 | 16 | 831.35 | 27 | TREE:NON PREVENTABLE | 21 | FUSE - TRANSFORMER | MUSKOGEE | 2324 ELMIRA | CMI_NORMAL | NO | NO | NO | 861594 | 74078 | 33285 | 2833 | 1047 | 0.0009649 | 1.5088e-05 | 63.95 | 1 | 310 | Load | 1483 | Load | Tran1phOH | REID R WILLIAMS | 512-618-8800 | [5 empty] | Vegetation | N | DISTRIBUTION | 161kV | 2020-02-01 | 2020 |  | #N/A
J2002.000125 | PD-02012020-01322 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3670 | 853670 | 2020-02-01 11:03 | 2020-02-01 13:24 | 141.23 | 1 | 1 | 141.2333 | 5 | ELECTRICAL TRACKING | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | NE 8th St and N Oklahoma Ave | CMI_NORMAL | NO | NO | NO | 861594 | 168268 | 148442 | 5929 | 1565 | 0.00016392 | 1.1606e-06 | 141.2333 | 1 | 320 | Customer | 368867 | Load | Tran3phPadWye | REX R WILSON | 405-535-4507 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | OK - 2022
J2002.000126 | PD-02012020-01335 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3925 | 833925 | 2020-02-01 11:12 | 2020-02-01 15:47 | 274.7 | 1 | 1 | 274.7 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 5334 WILLOWCLF RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168268 | 148442 | 7852 | 2183 | 0.00031883 | 1.1606e-06 | 274.7 | 1 | 310 | Customer | 47742 | Load | Tran1phPad | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | OK - 2022
J2002.000140 | PD-02012020-01347 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-02-01 12:12 | 2020-02-01 17:48 | 336.02 | 1 | 1 | 336.0167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DEL CITY | 2321 MUSTANG | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159209 | 102197 | 7419 | 2240 | 0.00038999 | 1.1606e-06 | 336.0167 | 1 | 320 | Customer | 13886 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | OK - 2022
J2002.000147 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-01 12:41 | 2020-02-01 14:22 | 101.47 | 3 | 2 | 215.5 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 7913 BARTSCH | CMI_PLANNED | YES | NO | NO | 861594 | 82268 | 61223 | 1457 | 1239 | 0.00025012 | 3.4819e-06 | 71.8333 | 1 | 308 | Load | 9244 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | Ark - Series 2
J2002.000151 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-02-01 13:01 | 2020-02-01 14:23 | 81.47 | 12 | 6 | 944.6 | 4 | DETERIORATION | 12 | POLE | ARKOMA | 315 CECILIA | CMI_PLANNED | YES | NO | NO | 861594 | 82268 | 61223 | 2938 | 876 | 0.0010963 | 1.3928e-05 | 78.7167 | 1 | 308 | Load | 11259 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-01 | 2020 |  | Ark - Series 2
J2002.000155 | PD-02012020-01356 | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1724 | 861724 | 2020-02-01 13:11 | 2020-02-01 16:14 | 182.57 | 1 | 1 | 182.5667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 6200 SE.47 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 114428 | 71221 | 6950 | 2058 | 0.00021189 | 1.1606e-06 | 182.5667 | 1 | 310 | Customer | 67003 | Load | Tran1phPad | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | #N/A
J2002.000159 | PD-02012020-01355 | METRO EAST | SEMINOLE | 7506:SASAKWA | SASAKWA 22 | 750622 | 2020-02-01 13:16 | 2020-02-01 16:02 | 166.47 | 1 | 1 | 166.4667 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | WEWOKA | 1S 31/4E SASK | CMI_NORMAL | NO | NO | NO | 861594 | 114428 | 13612 | 300 | 72 | 0.00019321 | 1.1606e-06 | 166.4667 | 1 | 320 | Load | 8357 | Load | Tran3phWye | BRADY A HUFF | 405-519-0701 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | #N/A
J2002.000170 |  | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_624 | 550624 | 2020-02-01 14:25 | 2020-02-01 14:31 | 6.37 | 1 | 1 | 6.3667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DURANT | 812 N 11TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 77633 | 15496 | 6738 | 1155 | 7.3894e-06 | 1.1606e-06 | 6.3667 | 1 | 310 | Customer | 2350 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000175 | PD-02012020-01362 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2122 | 822122 | 2020-02-01 14:34 | 2020-02-01 15:11 | 36.97 | 1 | 1 | 36.9667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3925 NW.14 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168268 | 148442 | 9250 | 1837 | 4.2905e-05 | 1.1606e-06 | 36.9667 | 1 | 310 | Customer | 4229 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | OK - 2020
J2002.000186 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9931 | 829931 | 2020-02-01 15:37 | 2020-02-01 15:55 | 18.83 | 1 | 1 | 18.8333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 713 N.MACARTHUR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128878 | 116105 | 9235 | 2196 | 2.1859e-05 | 1.1606e-06 | 18.8333 | 1 | 310 | Customer | 47822 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000189 |  | METRO SOUTH | SOUTH | 8728:CHERRY CREEK | CHERRY_CREEK_2823 | 872823 | 2020-02-01 15:41 | 2020-02-01 15:52 | 11.15 | 1 | 1 | 11.15 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | WS I-35 1/2 M N OF ROBINSON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159209 | 57012 | 7106 | 1300 | 1.2941e-05 | 1.1606e-06 | 11.15 | 1 | 310 | Customer | 78116 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000190 | PD-02012020-01367 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-02-01 15:46 | 2020-02-01 17:21 | 95.17 | 1 | 1 | 95.1667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 10836 RIDGEVIEW-CRK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 114428 | 71221 | 11639 | 3534 | 0.00011045 | 1.1606e-06 | 95.1667 | 1 | 320 | Customer | 62304 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000192 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4028 | 834028 | 2020-02-01 15:50 | 2020-02-01 15:50 | 0 | 1262 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 10135 ROCKWELL AVE | CMI_MOMENTARY | YES | NO | NO | 861594 | 128878 | 116105 | 10844 | 1262 | 0 | 0.0014647 | 0 | 1 | 0 | Feeder | SILVR LK_4028 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000194 |  | NORTHWEST | ENID | 4518:MENO TAP | MENO TAP 21 | 451821 | 2020-02-01 16:03 | 2020-02-01 16:25 | 21.93 | 10 | 6 | 205.3333 | 5 | ELECTRICAL TRACKING | 28 | CROSSARM | ENID | N2720 Rd. and E0500 Rd. | CMI_NORMAL | NO | NO | NO | 861594 | 53556 | 37604 | 1332 | 502 | 0.00023832 | 1.1606e-05 | 20.5333 | 1 | 308 | Mainline | 652 | Recloser | Tripsaver3ph | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000203 | PD-02012020-01368 | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_622 | 770622 | 2020-02-01 16:20 | 2020-02-01 19:14 | 173.92 | 2 | 3 | 333.1333 | 15 | SQUIRREL | 2 | TRANSFORMER OH | BRISTOW | 1MN ON 66 1ME BRIST | CMI_NORMAL | NO | NO | NO | 861594 | 74078 | 40793 | 3783 | 2010 | 0.00038665 | 2.3213e-06 | 166.5667 | 1 | 310 | Load | 14736 | Load | Tran1phOH | CODY R MCKIM | 918-399-5930 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | #N/A
J2002.000205 | PD-02012020-01369 | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8124 | 838124 | 2020-02-01 16:36 | 2020-02-01 17:23 | 47.25 | 1 | 1 | 47.25 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 8325 NW.99 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128878 | 116105 | 8959 | 1638 | 5.484e-05 | 1.1606e-06 | 47.25 | 1 | 320 | Customer | 47393 | Load | Tran1phPad | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000209 |  | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3622 | 853622 | 2020-02-01 16:49 | 2020-02-01 16:56 | 6.38 | 1 | 1 | 6.3833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 433 TINKER-DIAG | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168268 | 148442 | 5929 | 964 | 7.4087e-06 | 1.1606e-06 | 6.3833 | 1 | 310 | Customer | 45253 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000212 | PD-02012020-01372 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1931 | 851931 | 2020-02-01 17:08 | 2020-02-01 21:05 | 236.58 | 2 | 3 | 459.9 | 4 | DETERIORATION | 2 | TRANSFORMER OH | SPENCER | 8697 NE.46 TR | CMI_NORMAL | NO | NO | NO | 861594 | 114428 | 71221 | 12455 | 987 | 0.00053378 | 2.3213e-06 | 229.95 | 1 | 310 | Load | 24328 | Load | Tran1phOH | JAMES CALDWELL | 405-973-6233 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000214 |  | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2122 | 892122 | 2020-02-01 17:30 | 2020-02-01 17:30 | 0.03 | 883 | 0 | 29.4333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | EL RENO | 803 JENSEN RD | CMI_MOMENTARY | YES | NO | NO | 861594 | 128878 | 12773 | 3195 | 883 | 3.4161e-05 | 0.0010248 | 0.033333 | 1 | 0 | Feeder | JENSN RD_2122 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000216 | PD-02012020-01373 | NORTHEAST | SAPULPA | 7611:MORRISON TAP | MORRISON_TAP_1122 | 761122 | 2020-02-01 17:31 | 2020-02-01 19:31 | 120.48 | 1 | 1 | 110.9833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | GLENCOE | ALLEY N.OF MAIN + W.OF OKLA. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 74078 | 40793 | 894 | 428 | 0.00012881 | 1.1606e-06 | 110.9833 | 1 | 310 | Customer | 40563 | Load | TranOpenDelta | BRAD WRIGHT | 918-629-1747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | OK - 2021
J2002.000222 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5138 | 815138 | 2020-02-01 17:59 | 2020-02-01 19:17 | 78.15 | 1 | 1 | 78.15 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1288 SW.74 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159209 | 102197 | 13937 | 1416 | 9.0704e-05 | 1.1606e-06 | 78.15 | 1 | 310 | Customer | 33849 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000224 | PD-02012020-01376 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-02-01 18:12 | 2020-02-01 19:50 | 98.15 | 1 | 1 | 2.431 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DEL CITY | 4001 SE.22 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 7420 | 2240 | 2.8215e-06 | 1.1606e-06 | 2.431 | 1 | 310 | Customer | 7753 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | OK - 2022
J2002.000233 | PD-02012020-01377 | METRO WEST | WEST | 8359:YUKON | YUKON_5924 | 835924 | 2020-02-01 19:01 | 2020-02-01 21:53 | 172.42 | 21 | 19 | 3378.55 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | YUKON | ES,YUKON / .5MN/MAIN | CMI_NORMAL | NO | NO | NO | 861594 | 128886 | 116112 | 6428 | 1820 | 0.0039213 | 2.4373e-05 | 160.8833 | 1 | 310 | Mainline | 5161 | Fuse | FuseRiser | BAD ORDER PRIMARY RES COORD | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | #N/A
J2002.000237 | PD-02012020-01379 | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1822 | 931822 | 2020-02-01 19:14 | 2020-02-01 20:25 | 70.57 | 1 | 1 | 70.5667 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | ALMA | NS HWY 64 ES LIGHTHOUSE RD | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 82280 | 61234 | 2848 | 786 | 8.1902e-05 | 1.1606e-06 | 70.5667 | 1 | 320 | Customer | 10334 | Load | Tran1phOH | MICHAEL L NEWMAN | 479-221-7071 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | Ark - Series 2
J2002.000239 | PD-02012020-01378 | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1724 | 861724 | 2020-02-01 19:26 | 2020-02-01 23:27 | 240.93 | 1 | 1 | 232.9333 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 6224 SE.50 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 114442 | 71227 | 6951 | 2058 | 0.00027035 | 1.1606e-06 | 232.9333 | 1 | 320 | Customer | 40749 | Load | Tran1phPad | KALEB STEWART | 405-426-9802 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | #N/A
J2002.000244 | PD-02012020-01381 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6924 | 846924 | 2020-02-01 19:41 | 2020-02-01 22:09 | 148.25 | 1 | 2 | 146.1833 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 2329 APPLEWAY | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 7727 | 1143 | 0.00016967 | 1.1606e-06 | 146.1833 | 1 | 320 | Customer | 59723 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000245 | PD-02012020-01382 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-02-01 19:54 | 2020-02-01 20:42 | 48.22 | 1 | 1 | 48.2167 | 12 | POOR CONNECTION | 50 | CONNECTOR | DEL CITY | 2321 MUSTANG | CMI_NORMAL | NO | NO | NO | 861594 | 159220 | 102202 | 7420 | 2240 | 5.5962e-05 | 1.1606e-06 | 48.2167 | 1 | 310 | Customer | 13886 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | OK - 2022
J2002.000254 |  | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1935 | 851935 | 2020-02-01 20:54 | 2020-02-01 21:03 | 9.07 | 1 | 1 | 9.0667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 1441 N.MIDWEST BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 114442 | 71227 | 12457 | 2161 | 1.0523e-05 | 1.1606e-06 | 9.0667 | 1 | 310 | Customer | 51531 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000261 | PD-02012020-01387 | METRO WEST | WEST | 8359:YUKON | YUKON_5924 | 835924 | 2020-02-01 21:03 | 2020-02-02 08:03 | 660.33 | 1 | 1 | 630.3809 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | YUKON | 958 CUMBERLAND MANSION | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 6428 | 1820 | 0.00073164 | 1.1606e-06 | 630.3809 | 1 | 310 | Customer | 70010 | Load | Tran1phPad | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-01 | 2020 |  | #N/A
J2002.000270 | PD-02012020-01389 | NORTHEAST | SAPULPA | 3218:BEGGS | BEGGS_1829 | 321829 | 2020-02-01 22:06 | 2020-02-02 04:34 | 387.92 | 19 | 14 | 4874.6333 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | MOUNDS | 81st W. Ave. & 206th Str. | CMI_NORMAL | NO | NO | NO | 861594 | 74092 | 40794 | 1844 | 904 | 0.0056577 | 2.2052e-05 | 256.5596 | 1 | 310 | Mainline | 340519 | Fuse | FuseOH | CODY R MCKIM | 918-399-5930 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | OK - 2020
J2002.000280 | PD-02012020-01394 | NORTHEAST | SAPULPA | 3214:LONE STAR | LONE_STAR_1421 | 321421 | 2020-02-01 23:19 | 2020-02-02 05:26 | 367.2 | 1 | 2 | 186.8854 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | SAPULPA | FAIRLANE DR HICKORY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 74092 | 40794 | 2659 | 1560 | 0.00021691 | 1.1606e-06 | 186.8854 | 1 | 310 | Customer | 48349 | Load | Tran1phPad | CODY R MCKIM | 918-399-5930 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000282 |  | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1931 | 851931 | 2020-02-01 23:38 | 2020-02-01 23:49 | 11.05 | 1 | 1 | 11.05 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | SPENCER | 8697 NE.46 TR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 114442 | 71227 | 12457 | 987 | 1.2825e-05 | 1.1606e-06 | 11.05 | 1 | 310 | Customer | 24328 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-01 | 2020 |  | #N/A
J2002.000299 | PD-02022020-00004 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6924 | 846924 | 2020-02-02 03:36 | 2020-02-02 05:48 | 132 | 1 | 2 | 33.3667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 13613 PIN-OAK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 7727 | 1143 | 3.8727e-05 | 1.1606e-06 | 33.3667 | 1 | 320 | Customer | 59382 | Load | Tran1phPad | REX R WILSON | 405-535-4507 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000307 | PD-02022020-00005 | NORTHWEST | ENID | 4353:OTTER | OTTER_5341 | 435341 | 2020-02-02 04:52 | 2020-02-02 07:20 | 147.97 | 1 | 1 | 146 | 5 | ELECTRICAL TRACKING | 21 | FUSE - TRANSFORMER | MARSHALL | 1.5MS,1 1/4MW-MARSHALL | CMI_NORMAL | NO | NO | NO | 861594 | 53567 | 37613 | 960 | 792 | 0.00016945 | 1.1606e-06 | 146 | 1 | 310 | Load | 14095 | Load | Tran1phOH | STEVEN LORENZ | 580-822-3566 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | OK - 2021
J2002.000310 | PD-02022020-00006 | METRO WEST | WEST | 8150:HOBBY LOBBY | HOBBY_LOBBY_5061 | 815061 | 2020-02-02 05:17 | 2020-02-02 09:50 | 273.17 | 1 | 1 | 273.1667 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | S/SW 33RD.5E/SPANWAY AVE. | CMI_NORMAL | NO | NO | NO | 861594 | 128886 | 116112 | 2510 | 1655 | 0.00031705 | 1.1606e-06 | 273.1667 | 1 | 310 | Customer | 75239 | Load | Tran1phPad | BROC ROBINSON | 405-312-1688 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000312 | PD-02022020-00007 | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2161 | 892161 | 2020-02-02 05:59 | 2020-02-02 11:27 | 327.88 | 1 | 1 | 320.1667 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | EL RENO | Reno and Legacy Point Cir. | CMI_NORMAL | NO | NO | NO | 861594 | 128886 | 12774 | 3195 | 738 | 0.0003716 | 1.1606e-06 | 320.1667 | 1 | 320 | Customer | 376102 | Load | Tran1phPad | BROC ROBINSON | 405-312-1688 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000316 | PD-02022020-00008 | METRO WEST | WEST | 8335:BETHANY | BETHANY_3526 | 833526 | 2020-02-02 06:43 | 2020-02-02 08:22 | 99.12 | 1 | 1 | 25.9209 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | BETHANY | 3904 N.DONALD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 7876 | 2062 | 3.0085e-05 | 1.1606e-06 | 25.9209 | 1 | 320 | Customer | 8869 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-02 | 2020 |  | #N/A
J2002.000317 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1223 | 831223 | 2020-02-02 06:47 | 2020-02-02 06:54 | 6.6 | 1 | 1 | 6.6 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | The Lincoln at Central Park | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 7753 | 634 | 7.6602e-06 | 1.1606e-06 | 6.6 | 1 | 310 | Customer | 315052 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000323 | PD-02022020-00009 | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_623 | 460623 | 2020-02-02 08:06 | 2020-02-02 09:06 | 60.08 | 16 | 13 | 937.0667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | WOODWARD | 1836 19TH-WOODWARD | CMI_NORMAL | NO | NO | NO | 861594 | 53567 | 10432 | 5686 | 1541 | 0.0010876 | 1.857e-05 | 58.5667 | 1 | 310 | Load | 10992 | Load | Tran1phOH | KEVIN D PETTIGREW | 580-216-6305 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-02 | 2020 |  | #N/A
J2002.000322 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-02-02 08:08 | 2020-02-02 08:17 | 8.95 | 1 | 1 | 8.95 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7909 NW.7 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 3411 | 2040 | 1.0388e-05 | 1.1606e-06 | 8.95 | 1 | 310 | Customer | 34502 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000327 | PD-02022020-00010 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6335 | 816335 | 2020-02-02 08:23 | 2020-02-02 09:24 | 60.78 | 4 | 5 | 237.6333 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | MOORE | 712 LITTLE RIVER CIR. | CMI_NORMAL | NO | NO | NO | 861594 | 159220 | 102202 | 11841 | 1212 | 0.00027581 | 4.6426e-06 | 59.4083 | 1 | 310 | Load | 78350 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | OK - 2022
J2002.000326 |  | METRO WEST | WEST | 8150:HOBBY LOBBY | HOBBY_LOBBY_5061 | 815061 | 2020-02-02 08:35 | 2020-02-02 16:21 | 465.4 | 1 | 1 | 76.3667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | S/SW 33RD.5E/SPANWAY AVE. | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 2510 | 1655 | 8.8634e-05 | 1.1606e-06 | 76.3667 | 1 | 310 | Customer | 75239 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000333 |  | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-02-02 09:07 | 2020-02-02 15:45 | 397.93 | 1 | 1 | 77.6333 | 4 | DETERIORATION | 12 | POLE | ARDMORE | 45 S.MARY NIBLACK RD | CMI_PLANNED | YES | NO | NO | 861594 | 77642 | 23593 | 2208 | 1002 | 9.0104e-05 | 1.1606e-06 | 77.6333 | 1 | 308 | Load | 10348 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000334 | PD-02022020-00012 | NORTHEAST | SAPULPA | 3208:TIBBENS ROAD | TIBBENS_RD_821 | 320821 | 2020-02-02 09:27 | 2020-02-02 10:56 | 89.28 | 1 | 1 | 85.4167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | SAPULPA | 1/2N,1/4E HWY117 + 49-W.AV | CMI_NORMAL | NO | NO | NO | 861594 | 74092 | 40794 | 3146 | 1171 | 9.9138e-05 | 1.1606e-06 | 85.4167 | 1 | 310 | Customer | 18567 | Load | Tran1phOH | CODY R MCKIM | 918-399-5930 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000346 | PD-02022020-00015 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_524 | 510524 | 2020-02-02 09:48 | 2020-02-02 12:08 | 140.1 | 1 | 2 | 139.3 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ARDMORE | LK MURRAY | CMI_NORMAL | NO | NO | NO | 861594 | 77642 | 23593 | 4775 | 1432 | 0.00016168 | 1.1606e-06 | 139.3 | 1 | 310 | Load | 22779 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-02 | 2020 |  | OK - 2021
J2002.000339 |  | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_524 | 510524 | 2020-02-02 09:48 | 2020-02-02 09:48 | 0 | 1432 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 228 C ST | CMI_MOMENTARY | YES | NO | NO | 861594 | 77642 | 23593 | 4775 | 1432 | 0 | 0.001662 | 0 | 1 | 0 | Feeder | ARDMORE_524 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-02 | 2020 |  | OK - 2021
J2002.000344 | PD-02022020-00013 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_871 | 830871 | 2020-02-02 09:59 | 2020-02-02 11:07 | 67.87 | 1 | 1 | 63.55 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 2373 NW 191st CT | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 19395 | 4249 | 7.3759e-05 | 1.1606e-06 | 63.55 | 1 | 320 | Customer | 377942 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | OK - 2021
J2002.000343 | PD-02022020-00014 | SOUTHERN | ARDMORE | 5109:ARDMORE WEST | ARDMORE_WEST_931 | 510931 | 2020-02-02 09:59 | 2020-02-02 11:33 | 93.58 | 1 | 1 | 93.5833 | 5 | ELECTRICAL TRACKING | 23 | FUSE - PRIMARY | ARDMORE | 0.48 Miles SE from Corner of N. Plainview Rd. + NW 12th Ave. | CMI_NORMAL | NO | NO | NO | 861594 | 77642 | 23593 | 1316 | 702 | 0.00010862 | 1.1606e-06 | 93.5833 | 1 | 310 | Load | 336331 | Load | Tran3phWye | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000348 | PD-02022020-00016 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_629 | 870629 | 2020-02-02 10:10 | 2020-02-02 12:06 | 116.2 | 1 | 1 | 83.6833 | 12 | POOR CONNECTION | 50 | CONNECTOR | NORMAN | 301 BASE AV | CMI_NORMAL | NO | NO | NO | 861594 | 159220 | 57018 | 7372 | 1373 | 9.7126e-05 | 1.1606e-06 | 83.6833 | 1 | 310 | Customer | 44500 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000349 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-02 10:17 | 2020-02-02 12:15 | 117.45 | 1 | 1 | 24.85 | 4 | DETERIORATION | 5 | SWITCH - AIR | LAMAR | LAMAR | CMI_PLANNED | YES | NO | NO | 861594 | 82280 | 7548 | 730 | 0 | 2.8842e-05 | 1.1606e-06 | 24.85 | 1 | 308 | Load | 9562 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-02 | 2020 |  | #N/A
J2002.000354 | PD-02022020-00018 | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_433 | 510433 | 2020-02-02 10:22 | 2020-02-02 11:31 | 68.9 | 1 | 2 | 67.1 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | ARDMORE | 202 P SE. | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 77642 | 23593 | 2318 | 1259 | 7.7879e-05 | 1.1606e-06 | 67.1 | 1 | 310 | Load | 7989 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000358 | PD-02022020-00020 | SOUTHERN | HEALDTON | 5311:RATLIFF | RATLIFF_1125 | 531125 | 2020-02-02 10:41 | 2020-02-02 16:51 | 370.32 | 1 | 1 | 360.9167 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | HEALDTON | 7676 RANCH RD. | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 77642 | 6804 | 450 | 217 | 0.00041889 | 1.1606e-06 | 360.9167 | 1 | 320 | Customer | 389777 | Load | Tran1phOH | JIMMY DON ROWE | 580-490-6283 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000361 |  | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1935 | 851935 | 2020-02-02 10:56 | 2020-02-02 11:05 | 9.18 | 1 | 1 | 9.1833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | NE 16 + MIDWEST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 114442 | 71227 | 12457 | 2161 | 1.0659e-05 | 1.1606e-06 | 9.1833 | 1 | 310 | Customer | 72918 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000364 |  | METRO EAST | SHAWNEE | 7410:MAUD TAP | MAUD_TAP_1022 | 741022 | 2020-02-02 11:06 | 2020-02-02 18:09 | 423.18 | 12 | 2 | 688.2 | 4 | DETERIORATION | 28 | CROSSARM | MAUD | 1 MN RAY CITY CORNER | CMI_NORMAL | NO | NO | NO | 861594 | 114442 | 22126 | 1020 | 257 | 0.00079875 | 1.3928e-05 | 57.35 | 1 | 308 | Mainline | 6883 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000365 | PD-02022020-00022 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1524 | 811524 | 2020-02-02 11:08 | 2020-02-02 13:25 | 137.15 | 1 | 1 | 133.8333 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 1408 SW.31 | CMI_NORMAL | NO | NO | NO | 861594 | 159220 | 102202 | 6066 | 2071 | 0.00015533 | 1.1606e-06 | 133.8333 | 1 | 321 | Customer | 17933 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-02 | 2020 |  | OK - 2022
J2002.000369 | PD-02022020-00027 | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1221 | 911221 | 2020-02-02 11:45 | 2020-02-02 13:20 | 95.45 | 1 | 1 | 93.9833 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | FORT SMITH | 2320 S.L | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 82280 | 61234 | 6604 | 1742 | 0.00010908 | 1.1606e-06 | 93.9833 | 1 | 321 | Customer | 10327 | Load | Tran1phOH | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-02 | 2020 |  | Ark - Series 1
J2002.000380 | PD-02022020-00029 | METRO WEST | WEST | 8158:SARA | SARA_5862 | 815862 | 2020-02-02 12:43 | 2020-02-02 14:08 | 84.52 | 1 | 1 | 84.5167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | SW 41st St & County Line Rd | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 18265 | 3613 | 9.8093e-05 | 1.1606e-06 | 84.5167 | 1 | 310 | Customer | 340035 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | OK - 2022
J2002.000383 | PD-02022020-00030 | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5424 | 865424 | 2020-02-02 12:47 | 2020-02-02 15:25 | 157.6 | 1 | 1 | 157.6 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MOORE | 1673 NE 6TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 9810 | 2010 | 0.00018292 | 1.1606e-06 | 157.6 | 1 | 310 | Customer | 71594 | Load | Tran1phPad | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000382 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3631 | 833631 | 2020-02-02 12:48 | 2020-02-02 12:48 | 0 | 1337 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 2204 HEFNER RD | CMI_MOMENTARY | YES | NO | NO | 861594 | 168267 | 148440 | 8788 | 1337 | 0 | 0.0015518 | 0 | 1 | 0 | Feeder | TENNESSE_3631 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-02 | 2020 |  | OK - 2021
J2002.000384 |  | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1935 | 851935 | 2020-02-02 12:49 | 2020-02-02 13:12 | 23.02 | 1 | 1 | 23.0167 | 1 | CANCELLED | 57 | CANCELLED | MIDWEST CITY | MEADOW GLEN APARTMENTS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 114442 | 71227 | 12457 | 2161 | 2.6714e-05 | 1.1606e-06 | 23.0167 | 1 | 310 | Customer | 77182 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000386 |  | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_622 | 580622 | 2020-02-02 12:56 | 2020-02-02 12:56 | 0 | 779 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ADA | 1806 A ST | CMI_MOMENTARY | YES | NO | NO | 861594 | 77642 | 11519 | 2518 | 780 | 0 | 0.00090414 | 0 | 1 | 0 | Feeder | VALLEY_VIEW_622 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-02 | 2020 |  | #N/A
J2002.000388 | PD-02022020-00031 | NORTHEAST | SAPULPA | 3210:HICKORY HILL | HICKORY_HILL_1024 | 321024 | 2020-02-02 12:58 | 2020-02-02 15:31 | 152.92 | 1 | 1 | 145.1667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | SAPULPA | L5 B6 VALLEY RIDGE | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 74092 | 40794 | 2684 | 1247 | 0.00016849 | 1.1606e-06 | 145.1667 | 1 | 310 | Customer | 48316 | Load | Tran1phPad | CONTRACTOR 5 DAVID ELLIOT INC | 918-639-5055 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | OK - 2022
J2002.000396 | PD-02022020-00033 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7022 | 817022 | 2020-02-02 13:39 | 2020-02-02 15:00 | 81.33 | 1 | 1 | 81.3333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 208 E RANCHWOOD CI. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 9938 | 2104 | 9.4399e-05 | 1.1606e-06 | 81.3333 | 1 | 320 | Customer | 4843 | Load | TranOHDeltaSplitBank | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000401 | PD-02022020-00035 | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_649 | 890649 | 2020-02-02 13:58 | 2020-02-02 15:51 | 113.02 | 9 | 9 | 949.95 | 5 | ELECTRICAL TRACKING | 47 | ARRESTOR OH | CANTON | 2ME-1 1/2MS CANTON | CMI_NORMAL | NO | NO | NO | 861594 | 128886 | 12774 | 1364 | 277 | 0.0011025 | 1.0446e-05 | 105.55 | 1 | 310 | Tap | 26606 | Fuse | FuseOH | JAMES CALDWELL | 405-973-6233 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000399 |  | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_649 | 890649 | 2020-02-02 13:58 | 2020-02-02 13:58 | 0 | 277 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | SOUTHARD | HWY 51 AND HWY 51A, GO.5 MILE SOUTH, .5 MILE EAST | CMI_MOMENTARY | YES | NO | NO | 861594 | 128886 | 12774 | 1364 | 277 | 0 | 0.0003215 | 0 | 1 | 0 | Feeder | SOUTHARD_649 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000415 | PD-02022020-00038 | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-02-02 14:46 | 2020-02-02 16:08 | 81.72 | 1 | 1 | 81.7167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ADA | 1414 ARLINGTON BL | CMI_NORMAL | NO | NO | NO | 861594 | 77642 | 11519 | 2518 | 1090 | 9.4844e-05 | 1.1606e-06 | 81.7167 | 1 | 310 | Load | 17937 | Load | Tran3phWye | JORDAN HERBERT-BLUE | 918-839-1152 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-02 | 2020 |  | #N/A
J2002.000416 | PD-02022020-00037 | METRO NORTH | NORTH | 8209:CLASSEN | CLASSEN_965 | 820965 | 2020-02-02 14:46 | 2020-02-02 15:55 | 68.67 | 1 | 1 | 65.1833 | 28 | OTHER (DESCRIBE) | 23 | FUSE - PRIMARY | OKLAHOMA CITY | W Park Place | CMI_NORMAL | NO | NO | NO | 861594 | 168267 | 148440 | 3888 | 831 | 7.5654e-05 | 1.1606e-06 | 65.1833 | 1 | 310 | Customer | 362236 | Load | Tran3phPadWye | ROBERT HALL | 405-757-9640 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000418 | PD-02022020-00039 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1924 | 851924 | 2020-02-02 14:57 | 2020-02-02 18:02 | 184.92 | 1 | 1 | 180.4333 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | SPENCER | 2912 PAXTON PL | CMI_NORMAL | NO | NO | NO | 861594 | 114442 | 71227 | 12457 | 1608 | 0.00020942 | 1.1606e-06 | 180.4333 | 1 | 310 | Customer | 72404 | Load | Tran1phPad | KALEB STEWART | 405-426-9802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000420 | PD-02022020-00041 | NORTHEAST | MUSKOGEE | 3136:EUCLID | EUCLID_3629 | 313629 | 2020-02-02 15:07 | 2020-02-02 16:48 | 100.6 | 81 | 1 | 5950.8 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | MUSKOGEE | DAYTON + "E" ST. | CMI_NORMAL | NO | NO | NO | 861594 | 74092 | 33298 | 990 | 615 | 0.0069067 | 9.4012e-05 | 73.4667 | 1 | 320 | Mainline | 26691 | Fuse | FuseRiser | CONTRACTOR 5 DAVID ELLIOT INC | 918-639-5055 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-02 | 2020 |  | #N/A
J2002.000423 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-02-02 15:13 | 2020-02-02 15:19 | 6.03 | 1 | 1 | 6.0333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7408 NW 10th St | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 3411 | 2040 | 7.0025e-06 | 1.1606e-06 | 6.0333 | 1 | 310 | Customer | 403460 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000426 |  | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6523 | 836523 | 2020-02-02 15:26 | 2020-02-02 15:32 | 5.8 | 1 | 1 | 5.8 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7710 LYREWOOD LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 7425 | 2257 | 6.7317e-06 | 1.1606e-06 | 5.8 | 1 | 310 | Customer | 38289 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | OK - 2022
J2002.000435 | PD-02022020-00047 | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2224 | 882224 | 2020-02-02 15:51 | 2020-02-02 19:56 | 244.88 | 1 | 1 | 240.6833 | 3 | DAMAGED BY PUBLIC | 2 | TRANSFORMER OH | GUTHRIE | COLTRANE + WATERLOO .25W .2N | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 19827 | 5385 | 1850 | 0.00027935 | 1.1606e-06 | 240.6833 | 1 | 310 | Load | 79819 | Load | Tran1phOH | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000438 | PD-02022020-00048 | NORTHEAST | MUSKOGEE | 3316:WARNER | WARNER_1623 | 331623 | 2020-02-02 15:54 | 2020-02-02 17:57 | 123.47 | 2 | 3 | 246.9333 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | WARNER | 3RD STA 7TH AV WRNR | CMI_NORMAL | NO | NO | NO | 861594 | 74092 | 33298 | 882 | 459 | 0.0002866 | 2.3213e-06 | 123.4667 | 1 | 310 | Secondary | 8716 | Load | Tran1phOH | NICHOLAS SELVIDGE | 918-652-1986 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-02 | 2020 |  | #N/A
J2002.000440 | PD-02022020-00049 | NORTHEAST | MUSKOGEE | 3316:WARNER | WARNER_1623 | 331623 | 2020-02-02 15:54 | 2020-02-02 17:55 | 121.47 | 3 | 3 | 897.65 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | WARNER | 3RD ST & 6TH AVE | CMI_NORMAL | NO | NO | NO | 861594 | 74092 | 33298 | 882 | 459 | 0.0010418 | 3.4819e-06 | 299.2167 | 1 | 310 | Load | 138 | Load | Tran1phPad | BRUCE A PAULUS | 479-220-7661 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-02 | 2020 |  | #N/A
J2002.000437 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-02-02 15:55 | 2020-02-02 15:59 | 4.23 | 1 | 1 | 4.2333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7408 NW 10th St | CMI_MOMENTARY | YES | NO | NO | 861594 | 128886 | 116112 | 3411 | 2040 | 4.9134e-06 | 1.1606e-06 | 4.2333 | 1 | 310 | Customer | 403460 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000443 | PD-02022020-00050 | SOUTHERN | PAULS VALLEY | 5619:RUSH CREEK | RUSH_CREEK_1922 | 561922 | 2020-02-02 16:09 | 2020-02-02 16:59 | 50.33 | 17 | 13 | 569.5 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | PAULS VALLEY | US HWY 77 & KENDALL DR | CMI_NORMAL | NO | NO | NO | 861594 | 77642 | 6214 | 2073 | 1193 | 0.00066098 | 1.9731e-05 | 33.5 | 1 | 310 | Tap | 9269 | Fuse | FuseOH | CHAD A DOTSON | 405-488-5658 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-02-02 | 2020 |  | OK - 2021
J2002.000441 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-02-02 16:09 | 2020-02-02 16:12 | 2.98 | 1 | 1 | 2.9833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7408 NW 10th St | CMI_MOMENTARY | YES | NO | NO | 861594 | 128886 | 116112 | 3411 | 2040 | 3.4626e-06 | 1.1606e-06 | 2.9833 | 1 | 310 | Customer | 403460 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000445 | PD-02022020-00052 | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_622 | 730622 | 2020-02-02 16:13 | 2020-02-02 21:10 | 296.57 | 6 | 7 | 1637.3 | 4 | DETERIORATION | 1 | TRANSFORMER UG | SEMINOLE | 2206 NORTHWOOD | CMI_NORMAL | NO | NO | NO | 861594 | 114442 | 13615 | 4069 | 1254 | 0.0019003 | 6.9638e-06 | 272.8833 | 1 | 310 | Load | 15981 | Load | Tran1phPad | KALEB STEWART | 405-426-9802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | OK - 2020
J2002.000449 | PD-02022020-00054 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2022 | 822022 | 2020-02-02 16:32 | 2020-02-02 19:16 | 164.1 | 1 | 1 | 164.1 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2827 NW.PARK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 6038 | 2119 | 0.00019046 | 1.1606e-06 | 164.1 | 1 | 321 | Customer | 1584 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-02 | 2020 |  | OK - 2020
J2002.000451 | PD-02022020-00055 | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-02-02 16:40 | 2020-02-02 17:56 | 75.97 | 1 | 1 | 67.25 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | ADA | 401 E Arlington | CMI_NORMAL | NO | NO | NO | 861594 | 77642 | 11519 | 2518 | 1090 | 7.8053e-05 | 1.1606e-06 | 67.25 | 1 | 310 | Customer | 339804 | Load | Tran1phOH | JORDAN HERBERT-BLUE | 918-839-1152 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-02-02 | 2020 |  | #N/A
J2002.000452 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9931 | 829931 | 2020-02-02 16:44 | 2020-02-02 16:47 | 3.02 | 1 | 1 | 3.0167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 5720 NW.19 | CMI_MOMENTARY | YES | NO | NO | 861594 | 128886 | 116112 | 9238 | 2197 | 3.5013e-06 | 1.1606e-06 | 3.0167 | 1 | 310 | Customer | 42465 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000456 | PD-02022020-00064 | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_450 | 710450 | 2020-02-02 16:48 | 2020-02-02 20:22 | 214.32 | 1 | 2 | 201.3667 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | CHANDLER | 1/2MN OF FOREST BAPTIST ES | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 114442 | 7474 | 2825 | 401 | 0.00023371 | 1.1606e-06 | 201.3667 | 1 | 310 | Load | 170787 | Load | Tran1phOH | STEVEN CASKEY | 405-777-8855 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | OK - 2021
J2002.000465 | PD-02022020-00070 | ARKANSAS | POTEAU | 3608:MULDROW | MULDROW 21 | 360821 | 2020-02-02 17:55 | 2020-02-02 19:01 | 65.88 | 3 | 2 | 162.6 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MULDROW | 2ND POLE E OF MAIN ON PAYNE | CMI_NORMAL | NO | NO | NO | 861594 | 82280 | 13498 | 2273 | 1226 | 0.00018872 | 3.4819e-06 | 54.2 | 1 | 310 | Load | 16350 | Load | Tran1phOH | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-02 | 2020 |  | #N/A
J2002.000468 | PD-02022020-00071 | METRO WEST | WEST | 8335:BETHANY | BETHANY_3526 | 833526 | 2020-02-02 17:58 | 2020-02-02 21:16 | 198.22 | 12 | 12 | 2347.2 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | BETHANY | 4901 N.COLLEGE | CMI_NORMAL | NO | NO | NO | 861594 | 128886 | 116112 | 7876 | 2062 | 0.0027243 | 1.3928e-05 | 195.6 | 1 | 310 | Load | 21852 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-02 | 2020 |  | #N/A
J2002.000467 |  | METRO EAST | SHAWNEE | 7432:ST GREGORY | ST_GREGORY_3229 | 743229 | 2020-02-02 18:03 | 2020-02-02 18:07 | 4.18 | 1 | 1 | 4.1833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SHAWNEE | 1440 N MACARTHUR 250 W ACME | CMI_MOMENTARY | YES | NO | NO | 861594 | 114442 | 22126 | 4094 | 796 | 4.8553e-06 | 1.1606e-06 | 4.1833 | 1 | 310 | Customer | 23161 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000472 |  | METRO WEST | WEST | 8335:BETHANY | BETHANY_3526 | 833526 | 2020-02-02 18:21 | 2020-02-02 22:22 | 240.77 | 1 | 1 | 240.7667 | 1 | CANCELLED | 57 | CANCELLED | BETHANY | 5711 NW 48TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 7876 | 2062 | 0.00027944 | 1.1606e-06 | 240.7667 | 1 | 310 | Customer | 23177 | Load | Tran1phOH | Ties | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-02 | 2020 |  | #N/A
J2002.000476 |  | METRO WEST | WEST | 8335:BETHANY | BETHANY_3526 | 833526 | 2020-02-02 18:35 | 2020-02-02 22:21 | 226.4 | 1 | 1 | 158.45 | 1 | CANCELLED | 57 | CANCELLED | BETHANY | 4710 CENTRAL RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 7876 | 2062 | 0.0001839 | 1.1606e-06 | 158.45 | 1 | 310 | Customer | 5476 | Load | Tran1phOH | Ties | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-02 | 2020 |  | #N/A
J2002.000483 |  | NORTHEAST | MUSKOGEE | 3316:WARNER | WARNER_1623 | 331623 | 2020-02-02 19:07 | 2020-02-03 06:11 | 664.15 | 1 | 1 | 105.8 | 1 | CANCELLED | 57 | CANCELLED | WARNER | 3RD STA 7TH AV WRNR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 74092 | 33298 | 882 | 459 | 0.0001228 | 1.1606e-06 | 105.8 | 1 | 310 | Customer | 8716 | Load | Tran1phOH | Ties | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-02 | 2020 |  | #N/A
J2002.000501 | PD-02022020-00085 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-02-02 21:00 | 2020-02-03 00:33 | 213.73 | 1 | 2 | 71.6235 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DEL CITY | 2504 EPPERLY DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 7420 | 2240 | 8.3129e-05 | 1.1606e-06 | 71.6235 | 1 | 310 | Customer | 6050 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | OK - 2022
J2002.000502 | PD-02022020-00084 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_866 | 830866 | 2020-02-02 21:38 | 2020-02-03 00:03 | 144.55 | 1 | 1 | 140.7667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 14108 OSAGE DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 19395 | 4304 | 0.00016338 | 1.1606e-06 | 140.7667 | 1 | 320 | Customer | 59997 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000506 |  | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8131 | 838131 | 2020-02-02 22:16 | 2020-02-03 15:17 | 1020.83 | 1 | 0 | 656.1833 | 3 | DAMAGED BY PUBLIC | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 7329 W.WILSHIRE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 8958 | 1832 | 0.00076159 | 1.1606e-06 | 656.1833 | 1 | 0 | Load | 42969 | Load | TranOH3phDelta | Crew | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-02 | 2020 |  | #N/A
J2002.000520 |  | SOUTHERN | ARDMORE | 5109:ARDMORE WEST | ARDMORE_WEST_931 | 510931 | 2020-02-03 03:01 | 2020-02-03 03:06 | 4.45 | 1 | 1 | 4.45 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ARDMORE | 1702 Southern Hills Dr Ardmore | CMI_MOMENTARY | YES | NO | NO | 861594 | 77642 | 23593 | 1316 | 702 | 5.1648e-06 | 1.1606e-06 | 4.45 | 1 | 310 | Customer | 25917 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000534 | PD-02032020-00028 | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-03 07:47 | 2020-02-03 08:45 | 57.63 | 1 | 1 | 37.5167 | 5 | ELECTRICAL TRACKING | 21 | FUSE - TRANSFORMER | POCOLA | HWY 112 + BEATY ST | CMI_NORMAL | NO | NO | NO | 861594 | 82280 | 61234 | 1458 | 1240 | 4.3543e-05 | 1.1606e-06 | 37.5167 | 1 | 310 | Customer | 13992 | Load | TranOpenDelta | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | Ark - Series 2
J2002.000538 | PD-02032020-00041 | ARKANSAS | POTEAU | 3608:MULDROW | MULDROW 21 | 360821 | 2020-02-03 08:02 | 2020-02-03 09:05 | 63.5 | 9 | 7 | 532.65 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | MULDROW | SE12TH & DOGWOOD | CMI_NORMAL | NO | NO | NO | 861594 | 82280 | 13498 | 2273 | 1226 | 0.00061821 | 1.0446e-05 | 59.1833 | 1 | 310 | Tap | 70070 | Fuse | FuseOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | #N/A
J2002.000540 | PD-02032020-00040 | SOUTHERN | DURANT | 5511:BOKCHITO | BOKCHITO 21 | 551121 | 2020-02-03 08:14 | 2020-02-03 09:17 | 62.33 | 1 | 1 | 62.3333 | 27 | TREE:NON PREVENTABLE | 31 | CONDUCTOR SERVICE - OH | BENNINGTON | 213 PERRY ST | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 77642 | 15497 | 673 | 673 | 7.2347e-05 | 1.1606e-06 | 62.3333 | 1 | 311 | Customer | 6137 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Vegetation | N | DISTRIBUTION | 34.5/19.9kv | 2020-02-03 | 2020 |  | #N/A
J2002.000539 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-02-03 08:14 | 2020-02-03 09:52 | 97.62 | 7 | 5 | 667.6833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | ARKOMA | 108 HANDLIN | CMI_PLANNED | YES | NO | NO | 861594 | 82280 | 61234 | 2938 | 876 | 0.00077494 | 8.1245e-06 | 95.3833 | 1 | 308 | Load | 7053 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-03 | 2020 |  | Ark - Series 2
J2002.000543 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-02-03 08:21 | 2020-02-03 10:04 | 103.52 | 9 | 5 | 758.55 | 4 | DETERIORATION | 12 | POLE | ARKOMA | 625 OKLAHOMA AVE. | CMI_PLANNED | YES | NO | NO | 861594 | 82280 | 61234 | 2938 | 876 | 0.0008804 | 1.0446e-05 | 84.2833 | 1 | 308 | Load | 6241 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-03 | 2020 |  | Ark - Series 2
J2002.000552 | PD-02032020-00054 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1922 | 851922 | 2020-02-03 08:25 | 2020-02-03 10:06 | 100.55 | 8 | 10 | 768.1333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MIDWEST CITY | 3600 MT-PLEASANT DR | CMI_NORMAL | NO | NO | NO | 861594 | 114442 | 71227 | 12457 | 1795 | 0.00089153 | 9.2851e-06 | 96.0167 | 1 | 310 | Load | 22339 | Load | Tran1phOH | ADAM CLARK | 580-310-8924 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000549 | PD-02032020-00063 | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1722 | 911722 | 2020-02-03 08:29 | 2020-02-03 11:31 | 182.32 | 1 | 1 | 177.7667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | FORT SMITH | S of Cisterna Way | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 82280 | 61234 | 4243 | 1473 | 0.00020632 | 1.1606e-06 | 177.7667 | 1 | 310 | Customer | 310726 | Load | Tran1phPad | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-03 | 2020 |  | #N/A
J2002.000554 | PD-02032020-00059 | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_521 | 560521 | 2020-02-03 08:34 | 2020-02-03 11:28 | 173.92 | 1 | 2 | 171.1167 | 4 | DETERIORATION | 50 | CONNECTOR | PAULS VALLEY | 11O4 EVERGREEN DRIV | CMI_NORMAL | NO | NO | NO | 861594 | 77642 | 6214 | 2463 | 468 | 0.0001986 | 1.1606e-06 | 171.1167 | 1 | 320 | Customer | 9853 | Load | Tran1phOH | BRUCE E BEAM | 405-626-0490 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | OK - 2022
J2002.000556 |  | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4024 | 914024 | 2020-02-03 08:36 | 2020-02-03 10:04 | 87.47 | 4 | 3 | 340.7 | 4 | DETERIORATION | 28 | CROSSARM | FORT SMITH | 2700 S.SAVANNAH | CMI_PLANNED | YES | NO | NO | 861594 | 82280 | 61234 | 4765 | 1167 | 0.00039543 | 4.6426e-06 | 85.175 | 1 | 308 | Load | 7876 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-03 | 2020 |  | Ark - Series 2
J2002.000559 | PD-02032020-00058 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-02-03 08:36 | 2020-02-03 10:16 | 99.8 | 1 | 2 | 28.953 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 525 NW.27 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 11129 | 2339 | 3.3604e-05 | 1.1606e-06 | 28.953 | 1 | 320 | Customer | 18226 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2020
J2002.000560 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5138 | 815138 | 2020-02-03 08:37 | 2020-02-03 08:42 | 5.22 | 1 | 1 | 5.2167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1288 SW.74 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 13937 | 1416 | 6.0547e-06 | 1.1606e-06 | 5.2167 | 1 | 310 | Customer | 33849 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000561 | PD-02032020-00069 | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2922 | 812922 | 2020-02-03 08:40 | 2020-02-03 10:53 | 132.65 | 1 | 1 | 132.65 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | SW.37 + GOFF | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 6387 | 1137 | 0.00015396 | 1.1606e-06 | 132.65 | 1 | 310 | Customer | 7445 | Load | Tran1phOH | SHANE DRAKE | 405-326-9052 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | #N/A
J2002.000562 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2133 | 822133 | 2020-02-03 08:44 | 2020-02-03 08:44 | 0 | 126 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 4431 NW 10TH ST | CMI_MOMENTARY | YES | NO | NO | 861594 | 168267 | 148440 | 9239 | 236 | 0 | 0.00014624 | 0 | 1 | 0 | Feeder | MERIDIAN_2133 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-03 | 2020 |  | OK - 2022
J2002.000566 | PD-02032020-00082 | METRO WEST | EL RENO | 8908:ROMAN NOSE | ROMAN_NOSE_852 | 890852 | 2020-02-03 09:05 | 2020-02-03 11:51 | 165.8 | 1 | 1 | 165.8 | 11 | OVERLOAD | 23 | FUSE - PRIMARY | LOYAL | 3005 E0750 RD | CMI_NORMAL | NO | NO | NO | 861594 | 128886 | 12774 | 525 | 257 | 0.00019243 | 1.1606e-06 | 165.8 | 1 | 320 | Load | 411429 | Load | 0 | MICHAEL T MAHEN | 405-210-6029 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000570 | PD-02032020-00107 | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4023 | 914023 | 2020-02-03 09:13 | 2020-02-03 11:58 | 165.47 | 1 | 1 | 165.4667 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | FORT SMITH | 3400 DUKE 5 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 82280 | 61234 | 4765 | 211 | 0.00019205 | 1.1606e-06 | 165.4667 | 1 | 310 | Customer | 13388 | Load | Tran1phPad | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-03 | 2020 |  | Ark - Series 2
J2002.000573 |  | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_621 | 870621 | 2020-02-03 09:17 | 2020-02-03 09:23 | 5.92 | 1 | 1 | 5.9167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 307 HAL-MULDROW DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 57018 | 7372 | 928 | 6.8671e-06 | 1.1606e-06 | 5.9167 | 1 | 310 | Customer | 46582 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000572 | PD-02032020-00098 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1422 | 311422 | 2020-02-03 09:18 | 2020-02-03 12:28 | 190.48 | 1 | 2 | 159.0333 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | MUSKOGEE | 2627 BOSTON | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 74092 | 33298 | 4573 | 1174 | 0.00018458 | 1.1606e-06 | 159.0333 | 1 | 320 | Customer | 8176 | Load | TranOpenDelta | REID R WILLIAMS | 512-618-8800 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | OK - 2020
J2002.000575 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-02-03 09:20 | 2020-02-03 14:33 | 313.52 | 1 | 1 | 238.7833 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 4th and 24th | CMI_PLANNED | YES | NO | NO | 861594 | 82280 | 61234 | 2739 | 2127 | 0.00027714 | 1.1606e-06 | 238.7833 | 1 | 308 | Mainline | 100833 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | Ark - Series 2
J2002.000576 | PD-02032020-00129 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-02-03 09:20 | 2020-02-03 10:22 | 61.55 | 1 | 1 | 61.55 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DYER | DYER RURAL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 82280 | 61234 | 3791 | 1205 | 7.1437e-05 | 1.1606e-06 | 61.55 | 1 | 310 | Customer | 14950 | Load | Tran1phPad | KRIS L HALMES | 479-430-9447 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-03 | 2020 |  | Ark - Series 2
J2002.000578 | PD-02032020-00099 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1122 | 511122 | 2020-02-03 09:24 | 2020-02-03 10:58 | 94.25 | 1 | 2 | 91.1333 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | DICKSON | Dickson Rd & Mockingbird .5W .7N WS | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 77642 | 23593 | 2208 | 1206 | 0.00010577 | 1.1606e-06 | 91.1333 | 1 | 320 | Load | 352516 | Load | Tran1phOH | JOE LOFTIS | 918-884-5349 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000581 | PD-02032020-00102 | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2122 | 892122 | 2020-02-03 09:25 | 2020-02-03 13:32 | 247.12 | 1 | 2 | 241.5333 | 13 | PREMATURE FAILURE | 2 | TRANSFORMER OH | EL RENO | 3705 S. Choctaw | CMI_NORMAL | NO | NO | NO | 861594 | 128886 | 12774 | 3195 | 883 | 0.00028033 | 1.1606e-06 | 241.5333 | 1 | 310 | Load | 252928 | Load | Tran3phWye | JAMES CALDWELL | 405-973-6233 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000582 | PD-02032020-00121 | NORTHEAST | SAPULPA | 3220:KELLYVILLE | KELLYVILLE_2024 | 322024 | 2020-02-03 09:28 | 2020-02-03 11:11 | 103.43 | 1 | 1 | 95.9 | 11 | OVERLOAD | 21 | FUSE - TRANSFORMER | KELLYVILLE | 1/4NE of SH33 on 177-W.Av | CMI_NORMAL | NO | NO | NO | 861594 | 74092 | 40794 | 2552 | 1581 | 0.00011131 | 1.1606e-06 | 95.9 | 1 | 310 | Load | 415514 | Load | Tran3phWye | GREGORY R HOOVER | 918-261-6803 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2020
J2002.000583 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-03 09:31 | 2020-02-03 13:55 | 263.35 | 7 | 7 | 1767.9667 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 7102 HWY-271 | CMI_PLANNED | YES | NO | NO | 861594 | 82280 | 61234 | 1458 | 1240 | 0.002052 | 8.1245e-06 | 252.5667 | 1 | 308 | Load | 1629 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | Ark - Series 2
J2002.000588 | PD-02032020-00109 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5138 | 815138 | 2020-02-03 09:31 | 2020-02-03 10:37 | 65.75 | 1 | 1 | 65.75 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1288 SW.74 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 13937 | 1416 | 7.6312e-05 | 1.1606e-06 | 65.75 | 1 | 310 | Customer | 33849 | Load | Tran1phPad | SHANE DRAKE | 405-326-9052 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000587 | PD-02032020-00106 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4122 | 814122 | 2020-02-03 09:32 | 2020-02-03 10:48 | 76.18 | 1 | 1 | 76.1833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 700 SE 40TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 5808 | 1272 | 8.8421e-05 | 1.1606e-06 | 76.1833 | 1 | 310 | Customer | 17472 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | #N/A
J2002.000591 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-03 09:39 | 2020-02-03 11:55 | 136.6 | 2 | 0 | 268.75 | 4 | DETERIORATION | 2 | TRANSFORMER OH | CHARLESTON | CO ROAD | CMI_PLANNED | YES | NO | NO | 861594 | 82280 | 61234 | 961 | 490 | 0.00031192 | 2.3213e-06 | 134.375 | 1 | 0 | Load | 8264 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-03 | 2020 |  | Ark - Series 2
J2002.000593 | PD-02032020-00132 | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8121 | 838121 | 2020-02-03 09:43 | 2020-02-03 14:12 | 269.27 | 1 | 1 | 269.2667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | Lot 14, Sec 16,Meadow lake Dr. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 8958 | 2257 | 0.00031252 | 1.1606e-06 | 269.2667 | 1 | 310 | Customer | 354259 | Load | Tran1phPad | PETER BILICKI | 619-726-8332 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000595 | PD-02032020-00120 | METRO EAST | SHAWNEE | 7435:MISSION HILL | MISSION HILL 24 | 743524 | 2020-02-03 09:45 | 2020-02-03 10:38 | 52.52 | 1 | 1 | 52.5167 | 22 | WIND | 31 | CONDUCTOR SERVICE - OH | SHAWNEE | .5S HDSTY ON BEARD | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 114442 | 22126 | 948 | 948 | 6.0953e-05 | 1.1606e-06 | 52.5167 | 1 | 320 | Customer | 14651 | Load | Tran3phPadWye | BRYAN K TATUM | 405-659-0746 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000594 |  | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1724 | 911724 | 2020-02-03 09:46 | 2020-02-03 16:14 | 388.38 | 4 | 2 | 1539.2 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | PAINTER LN - EAST POINT DR. | CMI_NORMAL | NO | NO | NO | 861594 | 82280 | 61234 | 4243 | 612 | 0.0017865 | 4.6426e-06 | 384.8 | 1 | 308 | Load | 18997 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-03 | 2020 |  | #N/A
J2002.000597 | PD-02032020-00130 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_621 | 870621 | 2020-02-03 09:47 | 2020-02-03 12:12 | 145.47 | 1 | 1 | 145.4667 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | NORMAN | 307 HAL-MULDROW DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 57018 | 7372 | 928 | 0.00016883 | 1.1606e-06 | 145.4667 | 1 | 310 | Customer | 46582 | Load | Tran1phPad | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000606 |  | METRO EAST | EAST | 8690:WILD MARY | WILD_MARY_9023 | 869023 | 2020-02-03 09:55 | 2020-02-03 10:21 | 26.25 | 12 | 3 | 193.4 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 2824 SE 90TH ST | CMI_PLANNED | YES | NO | NO | 861594 | 114442 | 71227 | 4023 | 2249 | 0.00022447 | 1.3928e-05 | 16.1167 | 1 | 308 | Load | 71773 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000617 | PD-02032020-00155 | METRO WEST | WEST | 8335:BETHANY | BETHANY_3527 | 833527 | 2020-02-03 10:07 | 2020-02-03 13:25 | 198.07 | 10 | 8 | 1933.1667 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | WARR ACRES | 4709 N.STANLEY | CMI_NORMAL | NO | NO | NO | 861594 | 128886 | 116112 | 7876 | 1666 | 0.0022437 | 1.1606e-05 | 193.3167 | 1 | 310 | Load | 13395 | Load | Tran1phOH | PETER BILICKI | 619-726-8332 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | OK - 2022
J2002.000612 | PD-02032020-00149 | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3724 | 913724 | 2020-02-03 10:08 | 2020-02-03 12:10 | 122.25 | 1 | 1 | 122.25 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | FORT SMITH | 2523 S.57 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 82280 | 61234 | 4571 | 897 | 0.00014189 | 1.1606e-06 | 122.25 | 1 | 310 | Customer | 14941 | Load | Tran1phPad | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | Ark - Series 3
J2002.000615 | PD-02032020-00152 | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5424 | 865424 | 2020-02-03 10:10 | 2020-02-03 11:27 | 77.37 | 1 | 2 | 77.3667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MOORE | 620 RAMBLIN-OAKS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 9810 | 2010 | 8.9795e-05 | 1.1606e-06 | 77.3667 | 1 | 310 | Customer | 64541 | Load | Tran1phPad | SHANE DRAKE | 405-326-9052 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000616 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-02-03 10:12 | 2020-02-03 11:17 | 65.68 | 1 | 1 | 58.5833 | 4 | DETERIORATION | 12 | POLE | LAVACA | 6 POLE N-HWY 22 ON 96,S-LAVACA | CMI_PLANNED | YES | NO | NO | 861594 | 82280 | 61234 | 2739 | 2127 | 6.7994e-05 | 1.1606e-06 | 58.5833 | 1 | 308 | Load | 3662 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | Ark - Series 2
J2002.000622 | PD-02032020-00158 | NORTHEAST | SAPULPA | 3210:HICKORY HILL | HICKORY_HILL_1021 | 321021 | 2020-02-03 10:21 | 2020-02-03 10:56 | 35.42 | 1 | 1 | 35.4167 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | SAPULPA | 1020 N BROWN ST | CMI_NORMAL | NO | NO | NO | 861594 | 74092 | 40794 | 2684 | 1437 | 4.1106e-05 | 1.1606e-06 | 35.4167 | 1 | 320 | Customer | 21907 | Load | Tran3phPadWye | CGI ADMIN | 918-261-6802 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2022
J2002.000625 | PD-02032020-00166 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3621 | 853621 | 2020-02-03 10:30 | 2020-02-03 11:19 | 49.47 | 1 | 1 | 49.4667 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 1513 NE.PARK | CMI_NORMAL | NO | NO | NO | 861594 | 168267 | 148440 | 5930 | 2171 | 5.7413e-05 | 1.1606e-06 | 49.4667 | 1 | 320 | Customer | 12675 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2022
J2002.000628 |  | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4823 | 824823 | 2020-02-03 10:34 | 2020-02-03 11:11 | 36.58 | 7 | 6 | 256.0334 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 2932 SW.21 | CMI_PLANNED | YES | NO | NO | 861594 | 168267 | 148440 | 4199 | 1797 | 0.00029716 | 8.1245e-06 | 36.5762 | 1 | 308 | Load | 3229 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000629 | PD-02032020-00174 | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_521 | 560521 | 2020-02-03 10:35 | 2020-02-03 12:28 | 113.33 | 1 | 1 | 113.3333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | PAULS VALLEY | 115 S PEAR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 77642 | 6214 | 2463 | 468 | 0.00013154 | 1.1606e-06 | 113.3333 | 1 | 310 | Customer | 14416 | Load | Tran1phOH | BRUCE E BEAM | 405-626-0490 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | OK - 2022
J2002.000634 | PD-02032020-00189 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2024 | 822024 | 2020-02-03 10:43 | 2020-02-03 11:29 | 45.57 | 5 | 6 | 214.5833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2641 NW.25 | CMI_NORMAL | NO | NO | NO | 861594 | 168267 | 148440 | 6038 | 1778 | 0.00024905 | 5.8032e-06 | 42.9167 | 1 | 310 | Load | 6864 | Load | TranOpenDelta | REX R WILSON | 405-535-4507 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | OK - 2020
J2002.000635 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-03 10:54 | 2020-02-03 10:57 | 2.68 | 2 | 0 | 5.3737 | 1 | CANCELLED | 57 | CANCELLED | CHARLESTON | 1/4M W-CHARLESTN ON HWY 22 | CMI_MOMENTARY | YES | NO | NO | 861594 | 82280 | 61234 | 961 | 490 | 6.2369e-06 | 2.3213e-06 | 2.6868 | 1 | 0 | Load | 5698 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-03 | 2020 |  | Ark - Series 2
J2002.000636 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-02-03 10:58 | 2020-02-03 11:14 | 16.08 | 1 | 1 | 16.0833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DYER | DYER RURAL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 82280 | 61234 | 3791 | 1205 | 1.8667e-05 | 1.1606e-06 | 16.0833 | 1 | 315 | Customer | 14950 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-03 | 2020 |  | Ark - Series 2
J2002.000637 |  | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2022 | 822022 | 2020-02-03 11:04 | 2020-02-03 14:49 | 225.1 | 14 | 0 | 152.1333 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | VILLA / .3MS, NW 10TH | CMI_NORMAL | NO | NO | NO | 861594 | 168267 | 148440 | 6038 | 2119 | 0.00017657 | 1.6249e-05 | 10.8667 | 1 | 0 | Mainline | 8895 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | OK - 2020
J2002.000645 | PD-02032020-00233 | METRO SOUTH | SOUTH | 8722:MILLENNIUM | MILLENNIUM_2222 | 872222 | 2020-02-03 11:20 | 2020-02-03 12:56 | 96.28 | 1 | 1 | 96.2833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | NORMAN | 618 SINCLAIR DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 57018 | 4205 | 737 | 0.00011175 | 1.1606e-06 | 96.2833 | 1 | 310 | Customer | 44852 | Load | Tran1phPad | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000652 |  | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4024 | 914024 | 2020-02-03 11:26 | 2020-02-03 13:58 | 152.17 | 11 | 12 | 1636.9833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 5022.5 S.22 | CMI_PLANNED | YES | NO | NO | 861594 | 82280 | 61234 | 4765 | 1167 | 0.0018999 | 1.2767e-05 | 148.8167 | 1 | 310 | Load | 4342 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-03 | 2020 |  | Ark - Series 2
J2002.000656 | PD-02032020-00240 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-02-03 11:31 | 2020-02-03 12:56 | 84.72 | 1 | 1 | 84.7167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4636 NW.19 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 9239 | 1941 | 9.8326e-05 | 1.1606e-06 | 84.7167 | 1 | 310 | Customer | 24601 | Load | Tran1phPad | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000658 |  | METRO EAST | SHAWNEE | 7412:PEARSON | PEARSON 21 | 741221 | 2020-02-03 11:32 | 2020-02-03 16:32 | 299.93 | 1 | 0 | 21.7667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | 0 | 2MW HWY 177 NS HWY 39 | CMI_PLANNED | YES | NO | NO | 861594 | 114442 | 22126 | 678 | 678 | 2.5263e-05 | 1.1606e-06 | 21.7667 | 1 | 0 | Tap | 143096 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000660 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-02-03 11:35 | 2020-02-03 15:22 | 226.93 | 11 | 7 | 1080.2 | 4 | DETERIORATION | 12 | POLE | BIXBY | 119 E NEEDLES | CMI_PLANNED | YES | NO | NO | 861594 | 74092 | 40794 | 2753 | 1441 | 0.0012537 | 1.2767e-05 | 98.2 | 1 | 308 | Load | 40102 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000661 | PD-02032020-00254 | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1724 | 831724 | 2020-02-03 11:35 | 2020-02-03 12:29 | 53.7 | 1 | 1 | 53.7 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 12831 STRATFORD DR BLDG 10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 6647 | 2777 | 6.2326e-05 | 1.1606e-06 | 53.7 | 1 | 310 | Customer | 75449 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000664 |  | ARKANSAS | OZARK | 9406:HELBERG | HELBERG_621 | 940621 | 2020-02-03 11:41 | 2020-02-03 14:04 | 142.63 | 1 | 1 | 142.6333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OZARK | 900' S. OF LAMAR SCHOOL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 82280 | 7548 | 1721 | 835 | 0.00016555 | 1.1606e-06 | 142.6333 | 1 | 310 | Customer | 10890 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | Ark - Series 3
J2002.000676 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-02-03 11:41 | 2020-02-03 15:25 | 223.4 | 12 | 6 | 1146 | 4 | DETERIORATION | 12 | POLE | BIXBY | 221 E NEEDLES | CMI_PLANNED | YES | NO | NO | 861594 | 74092 | 40794 | 2753 | 1441 | 0.0013301 | 1.3928e-05 | 95.5 | 1 | 308 | Load | 43621 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000666 | PD-02032020-00252 | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_429 | 580429 | 2020-02-03 11:45 | 2020-02-03 12:37 | 52.37 | 1 | 1 | 52.3667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ADA | 2405 ARLINGTON BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 77642 | 11519 | 3416 | 1343 | 6.0779e-05 | 1.1606e-06 | 52.3667 | 1 | 320 | Customer | 4417 | Load | Tran1phOH | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000690 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-02-03 11:47 | 2020-02-03 15:28 | 220.67 | 4 | 3 | 324.2667 | 4 | DETERIORATION | 12 | POLE | BIXBY | BTW MCKENA+NEEDLES W OF MONTG. | CMI_PLANNED | YES | NO | NO | 861594 | 74092 | 40794 | 2753 | 1441 | 0.00037636 | 4.6426e-06 | 81.0667 | 1 | 308 | Load | 18759 | Load | TranOpenDelta | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000668 |  | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4823 | 824823 | 2020-02-03 11:52 | 2020-02-03 12:34 | 41.97 | 9 | 6 | 305.25 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 3340 SW.23 | CMI_PLANNED | YES | NO | NO | 861594 | 168267 | 148440 | 4199 | 1797 | 0.00035429 | 1.0446e-05 | 33.9167 | 1 | 310 | Load | 31165 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000672 | PD-02032020-00264 | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5822 | 845822 | 2020-02-03 11:52 | 2020-02-03 12:26 | 33.7 | 1 | 1 | 33.7 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SPENCER | 8727 NE.52 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 114442 | 71227 | 2985 | 935 | 3.9114e-05 | 1.1606e-06 | 33.7 | 1 | 310 | Customer | 18001 | Load | Tran1phOH | ADAM CLARK | 580-310-8924 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | #N/A
J2002.000670 |  | NORTHWEST | ENID | 4109:WAUKOMIS | WAUKOMIS 23 | 410923 | 2020-02-03 11:52 | 2020-02-03 14:44 | 171.52 | 1 | 1 | 121.4833 | 4 | DETERIORATION | 12 | POLE | WAUKOMIS | 1W,1N OF PIONEER SCHOOL | CMI_PLANNED | YES | NO | NO | 861594 | 53567 | 37613 | 1558 | 572 | 0.000141 | 1.1606e-06 | 121.4833 | 1 | 308 | Load | 8995 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000689 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-02-03 11:54 | 2020-02-03 15:25 | 211.6 | 11 | 11 | 916.85 | 4 | DETERIORATION | 12 | POLE | BIXBY | 325 E NEEDLES | CMI_PLANNED | YES | NO | NO | 861594 | 74092 | 40794 | 2753 | 1441 | 0.0010641 | 1.2767e-05 | 83.35 | 1 | 310 | Load | 45067 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000675 | PD-02032020-00260 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2021 | 822021 | 2020-02-03 11:55 | 2020-02-03 12:10 | 14.6 | 1 | 1 | 14.6 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 3028 NW 11TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 6038 | 1113 | 1.6945e-05 | 1.1606e-06 | 14.6 | 1 | 310 | Customer | 13247 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | OK - 2020
J2002.000681 |  | METRO EAST | EAST | 8542:RENO | RENO_4222 | 854222 | 2020-02-03 12:06 | 2020-02-03 12:11 | 4.88 | 1 | 1 | 4.8833 | 1 | CANCELLED | 57 | CANCELLED | MIDWEST CITY | 7020 E.RENO | CMI_MOMENTARY | YES | NO | NO | 861594 | 114442 | 71227 | 5215 | 1689 | 5.6678e-06 | 1.1606e-06 | 4.8833 | 1 | 310 | Customer | 32833 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000680 | PD-02032020-00275 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1226 | 831226 | 2020-02-03 12:07 | 2020-02-03 13:07 | 59.52 | 1 | 1 | 59.5167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1540 NW.46 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 7753 | 1748 | 6.9077e-05 | 1.1606e-06 | 59.5167 | 1 | 320 | Customer | 27072 | Load | Tran1phOH | REX R WILSON | 405-535-4507 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000683 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-03 12:14 | 2020-02-03 18:02 | 348.42 | 2 | 2 | 656.2333 | 4 | DETERIORATION | 12 | POLE | CHARLESTON | 1/4M W-CHARLESTN ON HWY 22 | CMI_PLANNED | YES | NO | NO | 861594 | 82280 | 61234 | 961 | 490 | 0.00076165 | 2.3213e-06 | 328.1167 | 1 | 308 | Load | 5698 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-03 | 2020 |  | Ark - Series 2
J2002.000684 | PD-02032020-00277 | METRO EAST | EAST | 8542:RENO | RENO_4222 | 854222 | 2020-02-03 12:15 | 2020-02-03 14:44 | 148.53 | 1 | 1 | 148.5333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 7020 E.RENO | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 114442 | 71227 | 5215 | 1689 | 0.00017239 | 1.1606e-06 | 148.5333 | 1 | 310 | Customer | 32833 | Load | Tran1phPad | ADAM CLARK | 580-310-8924 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000686 |  | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2222 | 832222 | 2020-02-03 12:15 | 2020-02-03 14:51 | 155.82 | 22 | 21 | 411.7667 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | OKLAHOMA CITY | 3951 ALTADENA AVE, OKC | CMI_NORMAL | NO | NO | NO | 861594 | 168267 | 148440 | 9178 | 1557 | 0.00047791 | 2.5534e-05 | 18.7167 | 1 | 310 | Tap | 17110 | Fuse | FuseOH | [7 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | OK - 2022
J2002.000685 | PD-02032020-00279 | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9862 | 839862 | 2020-02-03 12:18 | 2020-02-03 13:12 | 53.92 | 1 | 1 | 53.9167 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 15501 N PENN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 10663 | 2316 | 6.2578e-05 | 1.1606e-06 | 53.9167 | 1 | 310 | Customer | 389319 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000692 | PD-02032020-00293 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4026 | 834026 | 2020-02-03 12:30 | 2020-02-03 14:46 | 136.27 | 1 | 1 | 136.2667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 6624 W.HEFNER RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 10844 | 1210 | 0.00015816 | 1.1606e-06 | 136.2667 | 1 | 310 | Customer | 58168 | Load | Tran1phPad | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000697 | PD-02032020-00299 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1223 | 831223 | 2020-02-03 12:32 | 2020-02-03 12:59 | 26.98 | 1 | 1 | 26.9833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | The Lincoln at Central Park | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 7753 | 634 | 3.1318e-05 | 1.1606e-06 | 26.9833 | 1 | 310 | Customer | 315052 | Load | Tran1phPad | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000698 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-03 12:40 | 2020-02-03 15:14 | 154.05 | 1 | 1 | 130.1667 | 4 | DETERIORATION | 12 | POLE | CHARLESTON | COUNTY LINE RD, CHARLESTON | CMI_PLANNED | YES | NO | NO | 861594 | 82280 | 61234 | 961 | 490 | 0.00015108 | 1.1606e-06 | 130.1667 | 1 | 308 | Load | 14348 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-03 | 2020 |  | Ark - Series 2
J2002.000699 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-02-03 12:43 | 2020-02-03 16:55 | 252.17 | 1 | 1 | 248.35 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | 8301 S WESTMINSTER | CMI_PLANNED | YES | NO | NO | 861594 | 159220 | 57018 | 4239 | 1005 | 0.00028824 | 1.1606e-06 | 248.35 | 1 | 308 | Load | 74745 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000700 |  | ARKANSAS | POTEAU | 3516:TARBY | TARBY_1625 | 351625 | 2020-02-03 12:45 | 2020-02-03 14:05 | 80.1 | 3 | 2 | 125.075 | 4 | DETERIORATION | 2 | TRANSFORMER OH | POTEAU | 29189 OLD TARBY RD | CMI_PLANNED | YES | NO | NO | 861594 | 82280 | 13498 | 1677 | 1197 | 0.00014517 | 3.4819e-06 | 41.6917 | 1 | 308 | Load | 3150 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-03 | 2020 |  | #N/A
J2002.000704 | PD-02032020-00323 | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-03 12:46 | 2020-02-03 14:48 | 121.58 | 1 | 1 | 121.5833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | BRANCH | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 0 | 0 | 0 | 0 | 0.00014111 | 1.1606e-06 | 121.5833 | 1 | 320 | Customer |  | 0 | 0 | ANTHONY SELF | 479-719-0734 |  |  |  |  | 06/10/2020 note from burchamc. Reference J2002.000704 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Emailed Brent Miller with blank transformer and circuit #'s. Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-03 | 2020 |  | Ark - Series 2
J2002.000705 | PD-02032020-00310 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6328 | 816328 | 2020-02-03 12:50 | 2020-02-03 13:31 | 41.38 | 1 | 1 | 41.3833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MOORE | 111 NE.9 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 11841 | 1188 | 4.8031e-05 | 1.1606e-06 | 41.3833 | 1 | 310 | Customer | 39551 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000707 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-03 12:55 | 2020-02-03 15:14 | 139.05 | 8 | 6 | 953.0667 | 4 | DETERIORATION | 12 | POLE | LAMAR | 438 N SEMINARY | CMI_PLANNED | YES | NO | NO | 861594 | 82280 | 7548 | 730 | 0 | 0.0011062 | 9.2851e-06 | 119.1333 | 1 | 310 | Load | 2045 | Load | TranOpenDelta | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | #N/A
J2002.000709 |  | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4823 | 824823 | 2020-02-03 12:55 | 2020-02-03 13:51 | 55.8 | 2 | 1 | 97.2667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 3001 SW.16 | CMI_PLANNED | YES | NO | NO | 861594 | 168267 | 148440 | 4199 | 1797 | 0.00011289 | 2.3213e-06 | 48.6333 | 1 | 308 | Load | 33521 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000708 |  | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_521 | 320521 | 2020-02-03 12:56 | 2020-02-03 13:14 | 17.93 | 1 | 1 | 6.3761 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SAPULPA | 305 W.JOHNSON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 74092 | 40794 | 3850 | 1610 | 7.4004e-06 | 1.1606e-06 | 6.3761 | 1 | 310 | Customer | 41164 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | OK - 2022
J2002.000710 | PD-02032020-00316 | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1623 | 581623 | 2020-02-03 13:01 | 2020-02-03 15:46 | 165.25 | 1 | 2 | 160.7167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ADA | HWY 1/ HWY 3 .5MN ES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 77642 | 11519 | 3462 | 1654 | 0.00018653 | 1.1606e-06 | 160.7167 | 1 | 320 | Load | 258235 | Load | Tran3phWye | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000711 | PD-02032020-00319 | NORTHWEST | ENID | 4109:WAUKOMIS | WAUKOMIS 23 | 410923 | 2020-02-03 13:01 | 2020-02-03 14:40 | 98.78 | 1 | 1 | 98.7833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | WAUKOMIS | 221 E.KING ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 53567 | 37613 | 1558 | 572 | 0.00011465 | 1.1606e-06 | 98.7833 | 1 | 320 | Customer | 4530 | Load | Tran1phOH | WILLIAM R PETHICK | 580-278-8129 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000713 | PD-02032020-00315 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-02-03 13:04 | 2020-02-03 13:52 | 48.27 | 1 | 1 | 8.5304 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4520 NW.19 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 9239 | 1941 | 9.9008e-06 | 1.1606e-06 | 8.5304 | 1 | 310 | Customer | 2868 | Load | Tran1phOH | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000715 |  | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2222 | 832222 | 2020-02-03 13:06 | 2020-02-03 13:19 | 13.13 | 1 | 1 | 13.1333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2833 NW.43 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 9178 | 1557 | 1.5243e-05 | 1.1606e-06 | 13.1333 | 1 | 310 | Customer | 27171 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | OK - 2022
J2002.000721 |  | SOUTHERN | ARDMORE | 5109:ARDMORE WEST | ARDMORE_WEST_931 | 510931 | 2020-02-03 13:25 | 2020-02-03 14:13 | 47.48 | 2 | 1 | 72.6667 | 4 | DETERIORATION | 1 | TRANSFORMER UG | ARDMORE | 4303 HESS RD | CMI_PLANNED | YES | NO | NO | 861594 | 77642 | 23593 | 1316 | 702 | 8.434e-05 | 2.3213e-06 | 36.3333 | 1 | 308 | Load | 198646 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000726 |  | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1822 | 931822 | 2020-02-03 13:31 | 2020-02-03 13:45 | 13.37 | 1 | 1 | 13.3667 | 1 | CANCELLED | 57 | CANCELLED | ALMA | SCH ADMIN BLDG, 704 HWY 64E | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 82280 | 61234 | 2848 | 786 | 1.5514e-05 | 1.1606e-06 | 13.3667 | 1 | 310 | Customer | 14726 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | Ark - Series 2
J2002.000728 | PD-02032020-00344 | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1371 | 831371 | 2020-02-03 13:33 | 2020-02-03 14:49 | 75.58 | 1 | 1 | 75.5833 | 4 | DETERIORATION | 21 | FUSE - TRANSFORMER | YUKON | N-HWY 66,WS-FRISCO RD | CMI_NORMAL | NO | NO | NO | 861594 | 128886 | 116112 | 7901 | 3782 | 8.7725e-05 | 1.1606e-06 | 75.5833 | 1 | 310 | Load | 34483 | Load | Tran1phOH | COLTON RACKLEY | 405-779-5033 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000727 |  | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1721 | 861721 | 2020-02-03 13:34 | 2020-02-03 15:49 | 135.33 | 9 | 1 | 559.95 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | DEL CITY | 4113 MONICA DR | CMI_PLANNED | YES | NO | NO | 861594 | 114442 | 71227 | 6951 | 1507 | 0.0006499 | 1.0446e-05 | 62.2167 | 1 | 308 | Load | 46666 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | #N/A
J2002.000730 | PD-02032020-00342 | METRO EAST | EAST | 8411:ACORN | ACORN_1170 | 841170 | 2020-02-03 13:37 | 2020-02-03 15:57 | 139.73 | 1 | 1 | 113.7833 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 12321 HUNTER DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 114442 | 71227 | 1796 | 1091 | 0.00013206 | 1.1606e-06 | 113.7833 | 1 | 320 | Customer | 61900 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000739 | PD-02032020-00374 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3629 | 833629 | 2020-02-03 13:52 | 2020-02-03 15:27 | 95.48 | 42 | 43 | 3842.3 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | THE VILLAGE | 9520 N.MAY AVE | CMI_NORMAL | NO | NO | NO | 861594 | 168267 | 148440 | 8788 | 1397 | 0.0044595 | 4.8747e-05 | 91.4833 | 1 | 310 | Mainline | 20671 | Fuse | FuseOH | JAMES CALDWELL | 405-973-6233 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000736 |  | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-02-03 13:52 | 2020-02-03 15:11 | 78.88 | 8 | 8 | 425.3333 | 5 | ELECTRICAL TRACKING | 2 | TRANSFORMER OH | DEL CITY | 2605 MICKEY RD | CMI_PLANNED | YES | NO | NO | 861594 | 159220 | 102202 | 7420 | 2240 | 0.00049366 | 9.2851e-06 | 53.1667 | 1 | 310 | Load | 6111 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2022
J2002.000738 |  | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 22 | 570822 | 2020-02-03 13:55 | 2020-02-03 14:04 | 8.65 | 1 | 1 | 8.65 | 1 | CANCELLED | 57 | CANCELLED | DAVIS | 200 SO D | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 77642 | 6817 | 1859 | 955 | 1.004e-05 | 1.1606e-06 | 8.65 | 1 | 310 | Customer | 6834 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000741 | PD-02032020-00379 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1122 | 511122 | 2020-02-03 14:12 | 2020-02-03 14:44 | 32.42 | 1 | 1 | 24.6 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DICKSON | GA RD/199 .5E SS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 77642 | 23593 | 2208 | 1206 | 2.8552e-05 | 1.1606e-06 | 24.6 | 1 | 310 | Load | 31010 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000751 | PD-02032020-00409 | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_722 | 510722 | 2020-02-03 14:39 | 2020-02-03 16:22 | 103.33 | 1 | 1 | 98.5667 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | ARDMORE | 1701 1 SW. | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 77642 | 23593 | 4512 | 985 | 0.0001144 | 1.1606e-06 | 98.5667 | 1 | 310 | Customer | 8943 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | #N/A
J2002.000756 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-02-03 14:48 | 2020-02-03 16:56 | 127.9 | 4 | 4 | 504.5333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | ARKOMA | MAIN ST. PHILLIPS 66 | CMI_PLANNED | YES | NO | NO | 861594 | 82280 | 61234 | 2938 | 876 | 0.00058558 | 4.6426e-06 | 126.1333 | 1 | 308 | Load | 13785 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-03 | 2020 |  | Ark - Series 2
J2002.000753 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7031 | 817031 | 2020-02-03 14:49 | 2020-02-03 15:02 | 12.95 | 1 | 1 | 12.95 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 10300 S WESTERN AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 9938 | 1892 | 1.503e-05 | 1.1606e-06 | 12.95 | 1 | 310 | Customer | 78296 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000757 | PD-02032020-00453 | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2923 | 812923 | 2020-02-03 15:09 | 2020-02-03 16:30 | 80.53 | 1 | 1 | 80.5333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 5423 S.LINN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 6387 | 1636 | 9.347e-05 | 1.1606e-06 | 80.5333 | 1 | 320 | Customer | 36482 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | #N/A
J2002.000760 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6331 | 816331 | 2020-02-03 15:23 | 2020-02-03 15:44 | 20.98 | 1 | 1 | 20.9833 | 1 | CANCELLED | 57 | CANCELLED | MOORE | 709 SW.11 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 11841 | 1365 | 2.4354e-05 | 1.1606e-06 | 20.9833 | 1 | 310 | Customer | 62041 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000761 | PD-02032020-00442 | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-02-03 15:28 | 2020-02-03 15:59 | 30.8 | 1 | 1 | 22.6 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ADA | 401 WEST MAIN | CMI_NORMAL | NO | NO | NO | 861594 | 77642 | 11519 | 2518 | 1090 | 2.623e-05 | 1.1606e-06 | 22.6 | 1 | 310 | Load | 15254 | Load | Tran1phOH | JORDAN HERBERT-BLUE | 918-839-1152 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | #N/A
J2002.000765 | PD-02032020-00451 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2625 | 862625 | 2020-02-03 15:41 | 2020-02-03 18:03 | 142.15 | 12 | 16 | 1666.6 | 15 | SQUIRREL | 20 | FUSE BARREL | DEL CITY | 4006 SE.14 PL | CMI_NORMAL | NO | NO | NO | 861594 | 159220 | 102202 | 7420 | 1269 | 0.0019343 | 1.3928e-05 | 138.8833 | 1 | 310 | Load | 26676 | Load | Tran1phOH | JAMES CALDWELL | 405-973-6233 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2022
J2002.000764 |  | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2625 | 862625 | 2020-02-03 15:41 | 2020-02-03 15:41 | 0.05 | 1269 | 0 | 21.15 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 2401 S BRYANT AVE | CMI_MOMENTARY | YES | NO | NO | 861594 | 159220 | 102202 | 7420 | 1269 | 2.4548e-05 | 0.0014729 | 0.016667 | 1 | 0 | Feeder | TROSPER_2625 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-03 | 2020 |  | OK - 2022
J2002.000772 | PD-02032020-00459 | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9871 | 839871 | 2020-02-03 15:52 | 2020-02-03 20:35 | 283.55 | 1 | 1 | 271.3167 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 16409 CHABLIS DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 10663 | 2048 | 0.0003149 | 1.1606e-06 | 271.3167 | 1 | 320 | Customer | 382314 | Load | Tran1phPad | BAD ORDER UG RES COORD | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2022
J2002.000777 | PD-02032020-00476 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_623 | 870623 | 2020-02-03 16:07 | 2020-02-03 19:14 | 187.48 | 1 | 1 | 187.4833 | 12 | POOR CONNECTION | 50 | CONNECTOR | NORMAN | 912 MCNAMEE | CMI_NORMAL | NO | NO | NO | 861594 | 159220 | 57018 | 7372 | 1900 | 0.0002176 | 1.1606e-06 | 187.4833 | 1 | 320 | Customer | 31808 | Load | TranOpenDelta | THOMAS E COLE | 405-623-9338 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000778 | PD-02032020-00474 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2126 | 822126 | 2020-02-03 16:10 | 2020-02-03 16:57 | 47.33 | 1 | 1 | 47.3333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 4063 NW.3 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 9239 | 676 | 5.4937e-05 | 1.1606e-06 | 47.3333 | 1 | 310 | Customer | 62163 | Load | Tran3phPadWye | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000781 |  | METRO EAST | SHAWNEE | 7407:REMINGTON | REMINGTON 21 | 740721 | 2020-02-03 16:15 | 2020-02-03 16:30 | 15.78 | 1 | 1 | 15.7833 | 1 | CANCELLED | 57 | CANCELLED | SHAWNEE | 424 N.CLEVELAND | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 114442 | 22126 | 3667 | 2022 | 1.8319e-05 | 1.1606e-06 | 15.7833 | 1 | 310 | Customer | 11317 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000783 |  | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4122 | 814122 | 2020-02-03 16:19 | 2020-02-03 16:58 | 39.75 | 1 | 1 | 39.75 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 225 SE.46 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 5808 | 1272 | 4.6135e-05 | 1.1606e-06 | 39.75 | 1 | 310 | Customer | 680 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | #N/A
J2002.000784 | PD-02032020-00494 | SOUTHERN | ARDMORE | 5124:BERWYN | BERWYN_2423 | 512423 | 2020-02-03 16:26 | 2020-02-03 17:45 | 79.2 | 1 | 1 | 36.0973 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | SPRINGER | 3N 3W SPRINGER | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 77642 | 23593 | 1035 | 775 | 4.1896e-05 | 1.1606e-06 | 36.0973 | 1 | 310 | Load | 17080 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000786 | PD-02032020-00488 | METRO EAST | SHAWNEE | 7412:PEARSON | PEARSON 21 | 741221 | 2020-02-03 16:29 | 2020-02-03 17:50 | 80.92 | 1 | 1 | 80.9167 | 15 | SQUIRREL | 2 | TRANSFORMER OH | ST. LOUIS | 1MW ST.LOUIS STORE NS HWY 59 | CMI_NORMAL | NO | NO | NO | 861594 | 114442 | 22126 | 678 | 678 | 9.3915e-05 | 1.1606e-06 | 80.9167 | 1 | 310 | Load | 21908 | Load | TranOpenDelta | KYLE L GOODIN | 405-426-9802 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000793 | PD-02032020-00496 | METRO WEST | WEST | 8321:PIEDMONT | PIEDMONT_2169 | 832169 | 2020-02-03 16:43 | 2020-02-03 21:20 | 277.15 | 1 | 3 | 22.4167 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | PIEDMONT | 360 CANDICE DR NW | CMI_NORMAL | NO | NO | NO | 861594 | 128886 | 116112 | 6302 | 1664 | 2.6018e-05 | 1.1606e-06 | 22.4167 | 1 | 320 | Customer | 81866 | Load | Tran1phPad | BROC ROBINSON | 405-312-1688 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000801 |  | METRO NORTH | GUTHRIE | 8814:PINE STREET | PINE_STREET_1429 | 881429 | 2020-02-03 17:11 | 2020-02-03 17:17 | 5.35 | 1 | 1 | 5.35 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | GUTHRIE | 508 E.GRANT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 19827 | 3103 | 1714 | 6.2094e-06 | 1.1606e-06 | 5.35 | 1 | 310 | Customer | 43785 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000805 | PD-02032020-00502 | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2824 | 312824 | 2020-02-03 17:26 | 2020-02-03 18:37 | 71.42 | 1 | 1 | 74.3833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 216 E.S BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 74092 | 33298 | 5281 | 1614 | 8.6332e-05 | 1.1606e-06 | 74.3833 | 1 | 310 | Customer | 14448 | Load | Tran1phOH | REID R WILLIAMS | 512-618-8800 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-03 | 2020 |  | OK - 2020
J2002.000820 | PD-02032020-00506 | NORTHWEST | ENID | 4353:OTTER | OTTER_5342 | 435342 | 2020-02-03 17:39 | 2020-02-03 22:26 | 287.15 | 17 | 12 | 4716.3667 | 27 | TREE:NON PREVENTABLE | 37 | CONDUCTOR PRIMARY - OH | LUCIEN | E & 3RD ST | CMI_NORMAL | NO | NO | NO | 861594 | 53567 | 37613 | 960 | 168 | 0.005474 | 1.9731e-05 | 277.4333 | 1 | 310 | Mainline | 168811 | Fuse | FuseOH | JOSH SHEPHERD | 580-583-5632 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2022
J2002.000814 | PD-02032020-00503 | ARKANSAS | POTEAU | 3505:POTEAU | POTEAU_531 | 350531 | 2020-02-03 17:43 | 2020-02-03 18:36 | 52.95 | 5 | 6 | 241.5833 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | POTEAU | % 1000 SO CHURCH | CMI_NORMAL | NO | NO | NO | 861594 | 82280 | 13498 | 2303 | 781 | 0.00028039 | 5.8032e-06 | 48.3167 | 1 | 310 | Load | 4414 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | #N/A
J2002.000815 |  | ARKANSAS | FORT SMITH | 9508:WHITESIDE | WHITESIDE_824 | 950824 | 2020-02-03 17:49 | 2020-02-03 17:56 | 6.43 | 1 | 1 | 6.4333 | 1 | CANCELLED | 57 | CANCELLED | VAN BUREN | TRAILBLAZER 3 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 82280 | 61234 | 1920 | 393 | 7.4668e-06 | 1.1606e-06 | 6.4333 | 1 | 310 | Customer | 17092 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-03 | 2020 |  | Ark - Series 2
J2002.000821 | PD-02032020-00507 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5021 | 865021 | 2020-02-03 17:59 | 2020-02-03 19:39 | 100.38 | 1 | 2 | 84.3 | 12 | POOR CONNECTION | 50 | CONNECTOR | MIDWEST CITY | 2205 harold ct | CMI_NORMAL | NO | NO | NO | 861594 | 114442 | 71227 | 8632 | 1293 | 9.7842e-05 | 1.1606e-06 | 84.3 | 1 | 320 | Customer | 16786 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000822 | PD-02032020-00509 | METRO WEST | WEST | 8359:YUKON | YUKON_5923 | 835923 | 2020-02-03 18:22 | 2020-02-03 20:24 | 122.43 | 1 | 1 | 120.2667 | 12 | POOR CONNECTION | 50 | CONNECTOR | YUKON | 910 ELM AVE | CMI_NORMAL | NO | NO | NO | 861594 | 128886 | 116112 | 6428 | 1150 | 0.00013959 | 1.1606e-06 | 120.2667 | 1 | 310 | Customer | 19396 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-03 | 2020 |  | #N/A
J2002.000823 |  | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_623 | 870623 | 2020-02-03 18:22 | 2020-02-03 19:24 | 61.23 | 4 | 1 | 244.9739 | 12 | POOR CONNECTION | 50 | CONNECTOR | NORMAN | 912 MCNAMEE | CMI_NORMAL | NO | NO | NO | 861594 | 159220 | 57018 | 7372 | 1900 | 0.00028433 | 4.6426e-06 | 61.2435 | 1 | 310 | Load | 31808 | Load | TranOpenDelta | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000827 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1223 | 831223 | 2020-02-03 18:37 | 2020-02-03 18:44 | 7.05 | 1 | 1 | 7.05 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | The Lincoln at Central Park | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 7753 | 634 | 8.1825e-06 | 1.1606e-06 | 7.05 | 1 | 310 | Customer | 315052 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000828 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-02-03 18:44 | 2020-02-03 18:47 | 2.95 | 1 | 1 | 2.95 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 9017 N UNIVERSITY AV | CMI_MOMENTARY | YES | NO | NO | 861594 | 168267 | 148440 | 8788 | 1952 | 3.4239e-06 | 1.1606e-06 | 2.95 | 1 | 310 | Customer | 372819 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000835 | PD-02032020-00511 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4033 | 834033 | 2020-02-03 19:33 | 2020-02-04 03:18 | 465.17 | 1 | 1 | 264.4667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 7417 NW 105 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 10844 | 1115 | 0.00030695 | 1.1606e-06 | 264.4667 | 1 | 320 | Customer | 63040 | Load | Tran1phPad | BROC ROBINSON | 405-312-1688 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | #N/A
J2002.000842 | PD-02032020-00515 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-02-03 20:25 | 2020-02-03 21:18 | 53.42 | 1 | 2 | 53.4167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 9017 N UNIVERSITY AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 8788 | 1952 | 6.1997e-05 | 1.1606e-06 | 53.4167 | 1 | 310 | Customer | 372819 | Load | Tran1phPad | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000866 | PD-02032020-00523 | NORTHWEST | ENID | 4353:OTTER | OTTER_5342 | 435342 | 2020-02-03 21:21 | 2020-02-04 01:03 | 222.37 | 166 | 56 | 34460.95 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | LUCIEN | 19800-20998 E Longhorn Trl | CMI_NORMAL | NO | NO | NO | 861594 | 53567 | 37613 | 960 | 168 | 0.039997 | 0.00019267 | 207.5961 | 1 | 310 | Mainline | 260419 | Recloser | Rec3phHydralic | KEVIN N PERRYMAN | 601-528-2473 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2022
J2002.000860 | PD-02032020-00521 | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2163 | 892163 | 2020-02-03 22:04 | 2020-02-04 01:47 | 223.15 | 1 | 1 | 217.0833 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 4801 STONE LANE | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 128886 | 12774 | 3195 | 1144 | 0.00025196 | 1.1606e-06 | 217.0833 | 1 | 320 | Customer | 222208 | Load | Tran1phOH | BROC ROBINSON | 405-312-1688 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000862 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-02-03 22:21 | 2020-02-03 22:25 | 4.65 | 1 | 1 | 4.65 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4748 NW.23 | CMI_MOMENTARY | YES | NO | NO | 861594 | 168267 | 148440 | 9239 | 1941 | 5.397e-06 | 1.1606e-06 | 4.65 | 1 | 310 | Customer | 35035 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000865 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-02-03 22:38 | 2020-02-03 22:44 | 5.97 | 1 | 1 | 5.9667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4748 NW.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 9239 | 1941 | 6.9251e-06 | 1.1606e-06 | 5.9667 | 1 | 310 | Customer | 35035 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-03 | 2020 |  | OK - 2021
J2002.000883 |  | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8122 | 838122 | 2020-02-04 01:08 | 2020-02-04 12:38 | 689.4 | 3 | 5 | 688.65 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 7324 SKYLARK CT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 8958 | 971 | 0.00079927 | 3.4819e-06 | 229.55 | 1 | 310 | Secondary | 53488 | Load | Tran1phPad | Ties | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.000880 | PD-02042020-00009 | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8122 | 838122 | 2020-02-04 01:08 | 2020-02-04 06:55 | 346.73 | 47 | 46 | 10227.2 | 5 | ELECTRICAL TRACKING | 1 | TRANSFORMER UG | OKLAHOMA CITY | 7213 SKYLARK LN | CMI_NORMAL | NO | NO | NO | 861594 | 128886 | 116112 | 8958 | 971 | 0.01187 | 5.455e-05 | 217.6 | 1 | 310 | Mainline | 10854 | Fuse | SwitchCubicleFuse | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.000890 |  | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_424 | 580424 | 2020-02-04 02:50 | 2020-02-04 03:09 | 18.48 | 1 | 1 | 18.4833 | 1 | CANCELLED | 57 | CANCELLED | STONEWALL | W OF STORE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 77642 | 11519 | 3416 | 436 | 2.1452e-05 | 1.1606e-06 | 18.4833 | 1 | 310 | Customer | 21358 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.000896 | PD-02042020-00013 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1423 | 311423 | 2020-02-04 03:38 | 2020-02-04 08:56 | 318.53 | 5 | 4 | 1185.0583 | 5 | ELECTRICAL TRACKING | 28 | CROSSARM | MUSKOGEE | 1203 S.21 | CMI_NORMAL | NO | NO | NO | 861594 | 74092 | 33298 | 4573 | 1498 | 0.0013754 | 5.8032e-06 | 237.0117 | 1 | 310 | Load | 6434 | Load | Tran1phOH | BRUCE A PAULUS | 479-220-7661 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | OK - 2020
J2002.000917 |  | SOUTHERN | ADA | 5813:BYNG SPA | BYNG_SPA_1322 | 581322 | 2020-02-04 07:05 | 2020-02-04 07:23 | 17.62 | 1 | 1 | 17.6167 | 1 | CANCELLED | 57 | CANCELLED | FRANCIS | 104 E.3RD - FRANCIS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 77642 | 11519 | 546 | 546 | 2.0447e-05 | 1.1606e-06 | 17.6167 | 1 | 310 | Customer | 8570 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | #N/A
J2002.000924 | PD-02042020-00035 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1522 | 811522 | 2020-02-04 07:40 | 2020-02-04 19:05 | 685 | 2 | 3 | 1363.95 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 2801 SW.34 | CMI_NORMAL | NO | NO | NO | 861594 | 159220 | 102202 | 6066 | 1943 | 0.0015831 | 2.3213e-06 | 681.975 | 1 | 310 | Secondary | 16807 | Load | Tran1phOH | BROC ROBINSON | 405-312-1688 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | OK - 2022
J2002.000926 | PD-02042020-00041 | NORTHEAST | MUSKOGEE | 3117:THREE RIVERS | THREE_RIVERS_1724 | 311724 | 2020-02-04 08:07 | 2020-02-04 08:58 | 50.62 | 1 | 1 | 50.6167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MUSKOGEE | MADEWELL METALS ON NE 48TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 74092 | 33298 | 2833 | 170 | 5.8748e-05 | 1.1606e-06 | 50.6167 | 1 | 320 | Load | 18381 | Load | Tran3phPadWye | JAMES C EVANS | 918-869-1174 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-04 | 2020 |  | #N/A
J2002.000932 | PD-02042020-00052 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4821 | 824821 | 2020-02-04 08:15 | 2020-02-04 13:29 | 314.3 | 15 | 16 | 413.3612 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | 2236 NW.10 | CMI_NORMAL | NO | NO | NO | 861594 | 168267 | 148440 | 4199 | 242 | 0.00047976 | 1.741e-05 | 27.5574 | 1 | 310 | Load | 71380 | Load | Tran3phPadWye | CORY J HUFFMAN | 870-668-0377 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2022
J2002.000931 | PD-02042020-00053 | METRO SOUTH | SOUTH | 8728:CHERRY CREEK | CHERRY_CREEK_2823 | 872823 | 2020-02-04 08:22 | 2020-02-04 09:14 | 51.7 | 1 | 1 | 51.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | WS I-35 1/2 M N OF ROBINSON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 57018 | 7108 | 1302 | 6.0005e-05 | 1.1606e-06 | 51.7 | 1 | 310 | Customer | 78116 | Load | Tran1phPad | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.000936 | PD-02042020-00054 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-02-04 08:35 | 2020-02-04 10:51 | 136.62 | 2 | 2 | 47.0833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1301 W.HEFNER RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 8788 | 1952 | 5.4647e-05 | 2.3213e-06 | 23.5417 | 1 | 310 | Customer | 75516 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.000945 | PD-02042020-00080 | METRO WEST | WEST | 8158:SARA | SARA_5871 | 815871 | 2020-02-04 09:02 | 2020-02-04 14:48 | 345.68 | 1 | 1 | 345.6833 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 11320 SW 33rd Te | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 18265 | 5404 | 0.00040121 | 1.1606e-06 | 345.6833 | 1 | 320 | Customer | 384072 | Load | Tran1phPad | BROC ROBINSON | 405-312-1688 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2022
J2002.000949 |  | NORTHEAST | SAPULPA | 7605:DRUMRIGHT | DRUMRIGHT_544 | 760544 | 2020-02-04 09:16 | 2020-02-04 16:03 | 406.83 | 26 | 0 | 10577.6238 | 4 | DETERIORATION | 12 | POLE | OILTON | 106 E FIRST ST OILTON | CMI_PLANNED | YES | NO | NO | 861594 | 74092 | 40794 | 1694 | 1114 | 0.012277 | 3.0177e-05 | 406.8317 | 1 | 0 | Tap | 308394 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | #N/A
J2002.000952 |  | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_724 | 510724 | 2020-02-04 09:27 | 2020-02-04 09:48 | 21.75 | 1 | 1 | 21.75 | 1 | CANCELLED | 57 | CANCELLED | ARDMORE | "H" ST S.W. + BROADWAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 77642 | 23593 | 4512 | 1625 | 2.5244e-05 | 1.1606e-06 | 21.75 | 1 | 310 | Customer | 1392 | Load | TranOH3phDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | #N/A
J2002.000957 | PD-02042020-00107 | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-02-04 09:37 | 2020-02-04 11:37 | 119.97 | 1 | 1 | 111.8167 | 4 | DETERIORATION | 50 | CONNECTOR | BIXBY | 1/4 N OF LEONARD ON 161TH | CMI_NORMAL | NO | NO | NO | 861594 | 74092 | 40794 | 2753 | 1441 | 0.00012978 | 1.1606e-06 | 111.8167 | 1 | 310 | Customer | 43117 | Load | Tran1phOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.000958 | PD-02042020-00103 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4033 | 834033 | 2020-02-04 09:39 | 2020-02-04 10:23 | 44 | 1 | 1 | 6.8205 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7417 NW 105 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 10844 | 1115 | 7.9162e-06 | 1.1606e-06 | 6.8205 | 1 | 320 | Customer | 63040 | Load | Tran1phPad | COLTON RACKLEY | 405-779-5033 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.000960 | PD-02042020-00118 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9931 | 829931 | 2020-02-04 09:42 | 2020-02-04 10:57 | 74.88 | 2 | 2 | 149.7667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 5001 NW 10TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 9238 | 2197 | 0.00017383 | 2.3213e-06 | 74.8833 | 1 | 310 | Secondary | 47894 | Load | Tran1phPad | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.000959 | PD-02042020-00116 | NORTHWEST | ENID | 4109:WAUKOMIS | WAUKOMIS 23 | 410923 | 2020-02-04 09:42 | 2020-02-04 10:47 | 64.67 | 1 | 1 | 64.6667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | WAUKOMIS | 221 E.KING ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 53567 | 37613 | 1558 | 572 | 7.5055e-05 | 1.1606e-06 | 64.6667 | 1 | 310 | Customer | 4530 | Load | Tran1phOH | WILLIAM R PETHICK | 580-278-8129 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.000962 | PD-02042020-00121 | SOUTHERN | ADA | 5813:BYNG SPA | BYNG_SPA_1322 | 581322 | 2020-02-04 10:01 | 2020-02-04 12:50 | 168.83 | 1 | 2 | 166.1 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | FRANCIS | 104 E.3RD - FRANCIS | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 77642 | 11519 | 546 | 546 | 0.00019278 | 1.1606e-06 | 166.1 | 1 | 321 | Customer | 8570 | Load | Tran1phOH | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | #N/A
J2002.000964 | PD-02042020-00128 | METRO SOUTH | SOUTH CENTRAL | 8717:TURNER | TURNER_1721 | 871721 | 2020-02-04 10:04 | 2020-02-04 11:31 | 87.1 | 2 | 5 | 125.5 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | MOORE | 1817 SW.28 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 3083 | 1986 | 0.00014566 | 2.3213e-06 | 62.75 | 1 | 310 | Secondary | 64017 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.000966 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-02-04 10:16 | 2020-02-04 10:22 | 6.02 | 1 | 1 | 6.0167 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1301 W.HEFNER RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 8788 | 1952 | 6.9832e-06 | 1.1606e-06 | 6.0167 | 1 | 310 | Customer | 75517 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.000968 | PD-02042020-00133 | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2922 | 812922 | 2020-02-04 10:18 | 2020-02-04 12:58 | 160.32 | 1 | 1 | 1.2833 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 3521 SW.41 | CMI_NORMAL | NO | NO | NO | 861594 | 159220 | 102202 | 6387 | 1137 | 1.4895e-06 | 1.1606e-06 | 1.2833 | 1 | 320 | Customer | 20601 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | #N/A
J2002.000973 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2173 | 862173 | 2020-02-04 10:37 | 2020-02-04 10:57 | 19.4 | 1 | 1 | 19.4 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | LOT26 BLK1 EASTRIDGE SEC 14 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 57018 | 4239 | 164 | 2.2516e-05 | 1.1606e-06 | 19.4 | 1 | 310 | Customer | 102909 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.000976 | PD-02042020-00151 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-02-04 10:47 | 2020-02-04 11:23 | 35.7 | 1 | 1 | 35.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4748 NW.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 9239 | 1941 | 4.1435e-05 | 1.1606e-06 | 35.7 | 1 | 310 | Customer | 35035 | Load | Tran1phPad | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.000977 | PD-02042020-00163 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_524 | 510524 | 2020-02-04 10:54 | 2020-02-04 12:43 | 108.83 | 1 | 1 | 106 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ARDMORE | 1307.5 C SE. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 77642 | 23593 | 4775 | 1432 | 0.00012303 | 1.1606e-06 | 106 | 1 | 310 | Customer | 1727 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.000979 |  | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4121 | 814121 | 2020-02-04 11:02 | 2020-02-04 11:10 | 7.32 | 1 | 1 | 7.3167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 5554 S.WALKER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 5808 | 1200 | 8.492e-06 | 1.1606e-06 | 7.3167 | 1 | 310 | Customer | 54216 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | #N/A
J2002.000985 | PD-02042020-00173 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3024 | 743024 | 2020-02-04 11:21 | 2020-02-04 13:16 | 115.4 | 1 | 2 | 5.1 | 12 | POOR CONNECTION | 50 | CONNECTOR | SHAWNEE | 220 N HARRISON | CMI_NORMAL | NO | NO | NO | 861594 | 114442 | 22126 | 6651 | 1640 | 5.9193e-06 | 1.1606e-06 | 5.1 | 1 | 320 | Customer | 9006 | Load | Tran1phOH | KEVIN M RICH | 405-802-2121 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.000986 | PD-02042020-00177 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4122 | 814122 | 2020-02-04 11:22 | 2020-02-04 12:20 | 57.87 | 1 | 1 | 57.8667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 508 SE.48 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 5808 | 1272 | 6.7162e-05 | 1.1606e-06 | 57.8667 | 1 | 310 | Customer | 540 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | #N/A
J2002.000988 | PD-02042020-00174 | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_523 | 890523 | 2020-02-04 11:24 | 2020-02-04 12:48 | 83.63 | 1 | 1 | 62.075 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | EL RENO | 69 SKYVIEW TRAILER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128886 | 12774 | 6956 | 1252 | 7.2047e-05 | 1.1606e-06 | 62.075 | 1 | 310 | Load | 65394 | Load | Tran1phPad | MICHAEL T MAHEN | 405-210-6029 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.000987 | PD-02042020-00175 | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5231 | 835231 | 2020-02-04 11:25 | 2020-02-04 12:05 | 40.32 | 1 | 1 | 40.3167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 11032 SPRINGHOLLOW RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 6518 | 638 | 4.6793e-05 | 1.1606e-06 | 40.3167 | 1 | 310 | Customer | 28611 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.000992 | PD-02042020-00190 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1423 | 311423 | 2020-02-04 11:49 | 2020-02-04 13:33 | 104.17 | 1 | 1 | 104.1667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MUSKOGEE | 420 S.14 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 74092 | 33298 | 4573 | 1498 | 0.0001209 | 1.1606e-06 | 104.1667 | 1 | 310 | Customer | 2488 | Load | Tran1phOH | JOSH CHENEY | 918-619-3590 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | OK - 2020
J2002.000993 | PD-02042020-00189 | METRO EAST | EAST | 8416:DUNJEE | DUNJEE_1621 | 841621 | 2020-02-04 11:55 | 2020-02-04 13:09 | 73.55 | 1 | 1 | 73.55 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | CHOCTAW | 1401 N.CHOCTAW RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 114442 | 71227 | 3541 | 1552 | 8.5365e-05 | 1.1606e-06 | 73.55 | 1 | 310 | Customer | 37813 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.000995 | PD-02042020-00194 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_861 | 830861 | 2020-02-04 11:59 | 2020-02-04 12:48 | 49 | 1 | 1 | 49 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 8320 NW 138TH CI | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 19395 | 3942 | 5.6871e-05 | 1.1606e-06 | 49 | 1 | 310 | Customer | 357819 | Load | Tran1phPad | COLTON RACKLEY | 405-779-5033 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.000999 | PD-02042020-00204 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_621 | 870621 | 2020-02-04 12:18 | 2020-02-04 20:07 | 469.2 | 4 | 4 | 1839.6667 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | NORMAN | ALB.APTS 209 HAL MULDROW DR | CMI_NORMAL | NO | NO | NO | 861594 | 159220 | 57018 | 7372 | 928 | 0.0021352 | 4.6426e-06 | 459.9167 | 1 | 310 | Secondary | 33964 | Load | Tran1phPad | CHAD W GLEAVE | 405-250-7464 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001007 |  | METRO EAST | EAST | 8618:BARNES | BARNES_1822 | 861822 | 2020-02-04 12:31 | 2020-02-04 13:44 | 73.55 | 2 | 1 | 145.0333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 5700 S BERRYMAN RD | CMI_PLANNED | YES | NO | NO | 861594 | 114442 | 71227 | 953 | 420 | 0.00016833 | 2.3213e-06 | 72.5167 | 1 | 308 | Load | 43892 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001010 | PD-02042020-00218 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3921 | 833921 | 2020-02-04 12:41 | 2020-02-04 13:21 | 40.3 | 1 | 1 | 16.3329 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3610 NW.52 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 7852 | 620 | 1.8957e-05 | 1.1606e-06 | 16.3329 | 1 | 310 | Customer | 3245 | Load | Tran1phOH | REX R WILSON | 405-535-4507 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2022
J2002.001014 | PD-02042020-00219 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-02-04 12:47 | 2020-02-04 13:20 | 33.13 | 1 | 1 | 33.1333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4636 NW.19 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 9239 | 1941 | 3.8456e-05 | 1.1606e-06 | 33.1333 | 1 | 310 | Customer | 24601 | Load | Tran1phPad | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.001018 | PD-02042020-00226 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7422 | 847422 | 2020-02-04 12:50 | 2020-02-04 13:29 | 39.15 | 10 | 13 | 340.1667 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 737 NE.24 | CMI_NORMAL | NO | NO | NO | 861594 | 168267 | 148440 | 6171 | 1215 | 0.00039481 | 1.1606e-05 | 34.0167 | 1 | 310 | Load | 5758 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2022
J2002.001017 | PD-02042020-00221 | NORTHWEST | ENID | 4157:NE ENID | NE_ENID_5723 | 415723 | 2020-02-04 12:51 | 2020-02-04 14:07 | 76.05 | 1 | 1 | 76.05 | 23 | CUSTOMER EQUIPMENT | 21 | FUSE - TRANSFORMER | NORTH ENID | 5916 N 16TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 53567 | 37613 | 1558 | 1311 | 8.8267e-05 | 1.1606e-06 | 76.05 | 1 | 310 | Load | 331953 | Load | Tran1phOH | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001022 | PD-02042020-00235 | METRO EAST | SHAWNEE | 7407:REMINGTON | REMINGTON 22 | 740722 | 2020-02-04 13:03 | 2020-02-04 14:00 | 57.3 | 1 | 2 | 29.9 | 12 | POOR CONNECTION | 50 | CONNECTOR | SHAWNEE | 1506 N.HARRISON | CMI_NORMAL | NO | NO | NO | 861594 | 114442 | 22126 | 3667 | 1645 | 3.4703e-05 | 1.1606e-06 | 29.9 | 1 | 310 | Customer | 3477 | Load | TranOpenDelta | KEVIN M RICH | 405-802-2121 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | #N/A
J2002.001020 | PD-02042020-00230 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4033 | 834033 | 2020-02-04 13:04 | 2020-02-04 14:15 | 70.87 | 1 | 1 | 70.8667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7417 NW 105 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 10844 | 1115 | 8.2251e-05 | 1.1606e-06 | 70.8667 | 1 | 310 | Customer | 63040 | Load | Tran1phPad | COLTON RACKLEY | 405-779-5033 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001024 | PD-02042020-00242 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1524 | 811524 | 2020-02-04 13:17 | 2020-02-04 15:23 | 125.87 | 1 | 1 | 125.8667 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 1304 SW.24 | CMI_NORMAL | NO | NO | NO | 861594 | 159220 | 102202 | 6066 | 2071 | 0.00014609 | 1.1606e-06 | 125.8667 | 1 | 310 | Customer | 25871 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | OK - 2022
J2002.001036 | PD-02042020-00268 | NORTHWEST | ENID | 4119:GLENWOOD | GLENWOOD_1922 | 411922 | 2020-02-04 13:43 | 2020-02-04 16:59 | 196.25 | 1 | 1 | 189.7 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | ENID | 4110 GRAHAM | CMI_NORMAL | NO | NO | NO | 861594 | 53567 | 37613 | 5418 | 1561 | 0.00022017 | 1.1606e-06 | 189.7 | 1 | 310 | Customer | 12554 | Load | Tran1phPad | C-TSENID1 TOM SEEDORF | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001043 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-04 13:43 | 2020-02-04 16:01 | 138.07 | 2 | 1 | 261.2667 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | CHARLESTON | HWY 22 E.-WOOD ST | CMI_PLANNED | YES | NO | NO | 861594 | 82280 | 61234 | 961 | 490 | 0.00030324 | 2.3213e-06 | 130.6333 | 1 | 308 | Tap | 3738 | Fuse | FuseRiser | [7 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-04 | 2020 |  | Ark - Series 2
J2002.001037 | PD-02042020-00264 | NORTHEAST | MUSKOGEE | 3325:WELLS | WELLS_2549 | 332549 | 2020-02-04 13:44 | 2020-02-04 14:31 | 46.68 | 22 | 3 | 1027.0333 | 22 | WIND | 21 | FUSE - TRANSFORMER | EUFAULA | TEXANNA,2 1/2 M.E.69 | CMI_NORMAL | NO | NO | NO | 861594 | 74092 | 33298 | 2381 | 1052 | 0.001192 | 2.5534e-05 | 46.6833 | 1 | 310 | Tap | 27395 | Fuse | FuseOH | NICHOLAS SELVIDGE | 918-652-1986 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.001046 | PD-02042020-00278 | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-02-04 14:08 | 2020-02-04 15:17 | 68.97 | 1 | 1 | 68.9667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 7576 NW.10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 3411 | 2040 | 8.0045e-05 | 1.1606e-06 | 68.9667 | 1 | 310 | Customer | 42156 | Load | Tran1phPad | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001048 | PD-02042020-00284 | NORTHEAST | SAPULPA | 3214:LONE STAR | LONE_STAR_1421 | 321421 | 2020-02-04 14:20 | 2020-02-04 15:02 | 42.18 | 1 | 1 | 42.1833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SAPULPA | GUNNER LOOP | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 74092 | 40794 | 2659 | 1560 | 4.896e-05 | 1.1606e-06 | 42.1833 | 1 | 310 | Customer | 345906 | Load | Tran1phPad | STEPHEN BURKS | 918-639-0130 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001057 |  | METRO WEST | EL RENO | 8908:ROMAN NOSE | ROMAN_NOSE_852 | 890852 | 2020-02-04 14:36 | 2020-02-04 15:52 | 75.93 | 257 | 67 | 13192.6667 | 17 | TRANSMISSION OPERATION | 45 | SUBSTATION CIRCUIT | RURAL | 6006 ST HWY 3 | CMI_NORMAL | NO | NO | NO | 861594 | 128886 | 12774 | 525 | 0 | 0.015312 | 0.00029828 | 51.3333 | 1 | 310 | Substation | ROMAN_NOSE_124M | Switch | 0 | [6 empty] | 06/10/2020 note from burchamc. Reference J2002.001057 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Manually completed blank Job Region, Job Area, etc. | Equipment | N | TRANSMISSION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001095 |  | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_647 | 890647 | 2020-02-04 14:36 | 2020-02-04 15:52 | 76.37 | 1069 | 69 | 81635.9667 | 17 | TRANSMISSION OPERATION | 45 | SUBSTATION CIRCUIT | SOUTHARD | HWY 51 AND HWY 51A, GO.5 MILE SOUTH, .5 MILE EAST | CMI_NORMAL | NO | NO | NO | 861594 | 128886 | 12774 | 1364 | 1069 | 0.09475 | 0.0012407 | 76.3667 | 1 | 310 | Feeder | SOUTHARD_647 | Recloser | SubRecloser | [7 empty] | Equipment | N | TRANSMISSION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001055 | PD-02042020-00320 | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3722 | 913722 | 2020-02-04 14:37 | 2020-02-04 16:04 | 87.2 | 1 | 1 | 87.2 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 5900 KINKEAD AV 122 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 82280 | 61234 | 4571 | 1442 | 0.00010121 | 1.1606e-06 | 87.2 | 1 | 310 | Customer | 12438 | Load | Tran1phPad | MARK A. SAWYER | 479-462-4457 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | Ark - Series 3
J2002.001053 |  | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_622 | 890622 | 2020-02-04 14:37 | 2020-02-04 14:37 | 0.03 | 1 | 0 | 0.033333 | 1 | CANCELLED | 57 | CANCELLED | SOUTHARD | HWY 51 AND HWY 51A, GO.5 MILE SOUTH, .5 MILE EAST | CMI_MOMENTARY | YES | NO | NO | 861594 | 128886 | 12774 | 1364 | 1 | 3.8688e-08 | 1.1606e-06 | 0.033333 | 1 | 0 | Feeder | SOUTHARD_622 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001060 |  | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_646 | 890646 | 2020-02-04 14:38 | 2020-02-04 15:00 | 21.87 | 6 | 4 | 128.35 | 17 | TRANSMISSION OPERATION | 45 | SUBSTATION CIRCUIT | OKEENE | 1/2 mile south of HWY 51 and N 2620 RD | CMI_NORMAL | NO | NO | NO | 861594 | 128886 | 12774 | 1364 | 17 | 0.00014897 | 6.9638e-06 | 21.3917 | 1 | 308 | Mainline | 373620 | Recloser | Rec3phElectronic | [7 empty] | Equipment | N | TRANSMISSION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001070 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4028 | 834028 | 2020-02-04 14:42 | 2020-02-04 15:40 | 57.8 | 1 | 1 | 57.8 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 9907 HUMMINGBIRD LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 10844 | 1262 | 6.7085e-05 | 1.1606e-06 | 57.8 | 1 | 310 | Customer | 53487 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001059 |  | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_646 | 890646 | 2020-02-04 14:42 | 2020-02-04 15:00 | 17.6 | 6 | 0 | 105.6 | 17 | TRANSMISSION OPERATION | 45 | SUBSTATION CIRCUIT | 0 | 1/2 mile south of HWY 51 and N 2620 RD | CMI_NORMAL | NO | NO | NO | 861594 | 128886 | 12774 | 1364 | 17 | 0.00012256 | 6.9638e-06 | 17.6 | 1 | 0 | Mainline | 373620 | Recloser | Rec3phElectronic | [7 empty] | Equipment | N | TRANSMISSION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001076 |  | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_649 | 890649 | 2020-02-04 14:44 | 2020-02-04 15:52 | 68.32 | 277 | 18 | 18923.7167 | 17 | TRANSMISSION OPERATION | 45 | SUBSTATION CIRCUIT | SOUTHARD | HWY 51 AND HWY 51A, GO.5 MILE SOUTH, .5 MILE EAST | CMI_NORMAL | NO | NO | NO | 861594 | 128886 | 12774 | 1364 | 277 | 0.021964 | 0.0003215 | 68.3167 | 1 | 310 | Feeder | SOUTHARD_649 | Recloser | SubRecloser | [7 empty] | Equipment | N | TRANSMISSION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001096 | PD-02042020-00312 | METRO SOUTH | SOUTH | 8722:MILLENNIUM | MILLENNIUM_2231 | 872231 | 2020-02-04 14:48 | 2020-02-04 23:30 | 522.12 | 2 | 4 | 129 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | NORMAN | HALLBROOKE DR & HALLBROOKE CT | CMI_NORMAL | NO | NO | NO | 861594 | 159220 | 57018 | 4205 | 2053 | 0.00014972 | 2.3213e-06 | 64.5 | 1 | 310 | Secondary | 242507 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001157 | PD-02042020-00324 | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1621 | 581621 | 2020-02-04 14:57 | 2020-02-04 15:54 | 57.03 | 1 | 1 | 57.0333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ADA | 403 W.12 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 77642 | 11519 | 3462 | 1808 | 6.6195e-05 | 1.1606e-06 | 57.0333 | 1 | 310 | Customer | 537 | Load | TranOpenDelta | JORDAN HERBERT-BLUE | 918-839-1152 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001150 |  | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_622 | 890622 | 2020-02-04 14:58 | 2020-02-04 15:00 | 1.95 | 1 | 1 | 1.95 | 17 | TRANSMISSION OPERATION | 45 | SUBSTATION CIRCUIT | SOUTHARD | HWY 51 AND HWY 51A, GO.5 MILE SOUTH, .5 MILE EAST | CMI_MOMENTARY | YES | NO | NO | 861594 | 128886 | 12774 | 1364 | 1 | 2.2632e-06 | 1.1606e-06 | 1.95 | 1 | 310 | Feeder | SOUTHARD_622 | Recloser | SubRecloser | [7 empty] | Equipment | N | TRANSMISSION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001174 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-02-04 15:04 | 2020-02-04 18:12 | 188.77 | 1 | 0 | 188.7674 | 4 | DETERIORATION | 12 | POLE | BARLING | 3RD STR. | CMI_PLANNED | YES | NO | NO | 861594 | 82280 | 61234 | 2739 | 2127 | 0.00021909 | 1.1606e-06 | 188.7674 | 1 | 0 | Tap | 100958 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | Ark - Series 2
J2002.001179 | PD-02042020-00321 | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_631 | 730631 | 2020-02-04 15:14 | 2020-02-04 19:13 | 238.98 | 1 | 1 | 235.0333 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | LITTLE | .7MW OF HWY#99/HWY#99A,SS | CMI_NORMAL | NO | NO | NO | 861594 | 114442 | 13615 | 4069 | 669 | 0.00027279 | 1.1606e-06 | 235.0333 | 1 | 310 | Load | 242617 | Load | Tran1phOH | KALEB STEWART | 405-426-9802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001187 | PD-02042020-00358 | METRO EAST | EAST | 8471:NE 30TH ST | NE_30TH_ST_7122 | 847122 | 2020-02-04 15:15 | 2020-02-04 17:27 | 132.17 | 3 | 3 | 378.05 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 3812 HALE TR | CMI_NORMAL | NO | NO | NO | 861594 | 114442 | 71227 | 2403 | 766 | 0.00043878 | 3.4819e-06 | 126.0167 | 1 | 310 | Secondary | 51091 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | OK - 2022
J2002.001184 |  | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_646 | 890646 | 2020-02-04 15:21 | 2020-02-04 15:52 | 31.47 | 17 | 0 | 534.9333 | 17 | TRANSMISSION OPERATION | 45 | SUBSTATION CIRCUIT | SOUTHARD | HWY 51 AND HWY 51A, GO.5 MILE SOUTH, .5 MILE EAST | CMI_NORMAL | NO | NO | NO | 861594 | 128886 | 12774 | 1364 | 17 | 0.00062086 | 1.9731e-05 | 31.4667 | 1 | 0 | Feeder | SOUTHARD_646 | Recloser | SubRecloser | [7 empty] | Equipment | N | TRANSMISSION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001188 | PD-02042020-00338 | METRO EAST | SEMINOLE | 7506:SASAKWA | SASAKWA 29 | 750629 | 2020-02-04 15:24 | 2020-02-04 17:13 | 108.53 | 1 | 1 | 108.5333 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | WEWOKA | 1.5MN-SASAKWA,WS-HWY 56 | CMI_NORMAL | NO | NO | NO | 861594 | 114442 | 13615 | 300 | 228 | 0.00012597 | 1.1606e-06 | 108.5333 | 1 | 310 | Load | 9945 | Load | Tran3phWye | BRADY A HUFF | 405-519-0701 | [5 empty] | Other | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | #N/A
J2002.001193 | PD-02042020-00352 | METRO SOUTH | SOUTH CENTRAL | 8133:WR AIRPORT | WR_AIRPORT_3321 | 813321 | 2020-02-04 15:35 | 2020-02-04 18:11 | 156.22 | 2 | 4 | 167 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 2940 SW.55 | CMI_NORMAL | NO | NO | NO | 861594 | 159220 | 102202 | 1489 | 1406 | 0.00019383 | 2.3213e-06 | 83.5 | 1 | 320 | Secondary | 17548 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.001195 | PD-02042020-00344 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1421 | 311421 | 2020-02-04 15:39 | 2020-02-04 17:16 | 96.67 | 1 | 1 | 96.6667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MUSKOGEE | 3602 W BDWY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 74092 | 33298 | 4573 | 1104 | 0.0001122 | 1.1606e-06 | 96.6667 | 1 | 310 | Customer | 8603 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | #N/A
J2002.001197 | PD-02042020-00362 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4821 | 824821 | 2020-02-04 15:58 | 2020-02-04 18:18 | 139.8 | 2 | 2 | 279.6 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2236 NW.10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 4199 | 242 | 0.00032451 | 2.3213e-06 | 139.8 | 1 | 310 | Secondary | 71380 | Load | Tran3phPadWye | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2022
J2002.001198 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-02-04 15:59 | 2020-02-04 16:23 | 23.97 | 1 | 1 | 23.9667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1301 W.HEFNER RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 8788 | 1952 | 2.7817e-05 | 1.1606e-06 | 23.9667 | 1 | 320 | Customer | 75517 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.001199 | PD-02042020-00363 | METRO SOUTH | SOUTH | 8726:NOBLE | NOBLE_2623 | 872623 | 2020-02-04 16:01 | 2020-02-04 17:54 | 113.05 | 2 | 2 | 188.5 | 3 | DAMAGED BY PUBLIC | 30 | CONDUCTOR SERVICE - UG | NOBLE | BLK 1 LOT 4 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 57018 | 2969 | 1521 | 0.00021878 | 2.3213e-06 | 94.25 | 1 | 311 | Secondary | 74665 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001203 |  | METRO WEST | EL RENO | 8908:ROMAN NOSE | ROMAN_NOSE_852 | 890852 | 2020-02-04 16:14 | 2020-02-04 16:17 | 2.77 | 1 | 1 | 2.7667 | 1 | CANCELLED | 57 | CANCELLED | LOYAL | 13895 N 2720 Rd | CMI_MOMENTARY | YES | NO | NO | 861594 | 128886 | 12774 | 525 | 257 | 3.2111e-06 | 1.1606e-06 | 2.7667 | 1 | 310 | Load | 401810 | Load | Tran3phWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001205 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-02-04 16:15 | 2020-02-04 16:18 | 3.72 | 1 | 1 | 3.7167 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 4748 NW.23 | CMI_MOMENTARY | YES | NO | NO | 861594 | 168267 | 148440 | 9239 | 1941 | 4.3137e-06 | 1.1606e-06 | 3.7167 | 1 | 310 | Customer | 35035 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.001206 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-02-04 16:21 | 2020-02-04 16:25 | 4.15 | 1 | 1 | 4.15 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 4748 NW.23 | CMI_MOMENTARY | YES | NO | NO | 861594 | 168267 | 148440 | 9239 | 1941 | 4.8167e-06 | 1.1606e-06 | 4.15 | 1 | 310 | Customer | 35035 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.001207 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-02-04 16:27 | 2020-02-04 16:37 | 10.05 | 1 | 2 | 10.05 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1947 NW 13TH ST OKLAHOMA CITY 731062009 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 11129 | 2058 | 1.1664e-05 | 1.1606e-06 | 10.05 | 1 | 310 | Customer | 334221 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.001214 |  | NORTHWEST | ENID | 4119:GLENWOOD | GLENWOOD_1922 | 411922 | 2020-02-04 16:33 | 2020-02-04 17:41 | 68.05 | 6 | 6 | 119.4 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | ENID | 4110 GRAHAM | CMI_NORMAL | NO | NO | NO | 861594 | 53567 | 37613 | 5418 | 1561 | 0.00013858 | 6.9638e-06 | 19.9 | 1 | 310 | Secondary | 12554 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001216 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-02-04 16:57 | 2020-02-04 17:07 | 10.42 | 1 | 1 | 10.4167 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 4748 NW.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 9239 | 1941 | 1.209e-05 | 1.1606e-06 | 10.4167 | 1 | 310 | Customer | 35035 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.001217 |  | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_526 | 510526 | 2020-02-04 16:58 | 2020-02-04 17:09 | 11.28 | 1 | 1 | 11.2833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ARDMORE | 1105 C NE. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 77642 | 23593 | 4775 | 1622 | 1.3096e-05 | 1.1606e-06 | 11.2833 | 1 | 310 | Customer | 1898 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | OK - 2020
J2002.001218 |  | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2922 | 812922 | 2020-02-04 16:58 | 2020-02-04 17:15 | 16.9 | 1 | 1 | 16.9 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 3608 S.GOFF | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 6387 | 1137 | 1.9615e-05 | 1.1606e-06 | 16.9 | 1 | 310 | Customer | 7350 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | #N/A
J2002.001221 |  | METRO EAST | EAST | 8471:NE 30TH ST | NE_30TH_ST_7122 | 847122 | 2020-02-04 17:15 | 2020-02-04 17:23 | 8.6 | 1 | 1 | 6 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 3816 HALE ST. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 114442 | 71227 | 2403 | 766 | 6.9638e-06 | 1.1606e-06 | 6 | 1 | 310 | Customer | 51093 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | OK - 2022
J2002.001223 | PD-02042020-00409 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5022 | 865022 | 2020-02-04 17:28 | 2020-02-04 23:02 | 334 | 2 | 2 | 651.5833 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | MIDWEST CITY | 2506 COACHLIGHT DR | CMI_NORMAL | NO | NO | NO | 861594 | 114442 | 71227 | 8632 | 1662 | 0.00075625 | 2.3213e-06 | 325.7917 | 1 | 310 | Secondary | 32754 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2022
J2002.001227 |  | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6523 | 836523 | 2020-02-04 17:44 | 2020-02-04 17:52 | 8.07 | 1 | 1 | 8.0667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7317 KNIGHT LAKE DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128886 | 116112 | 7425 | 2257 | 9.3625e-06 | 1.1606e-06 | 8.0667 | 1 | 310 | Customer | 38611 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2022
J2002.001230 | PD-02042020-00414 | ARKANSAS | POTEAU | 3506:CAVANAL MTN | CAVANAL MTN 21 | 350621 | 2020-02-04 17:52 | 2020-02-04 20:37 | 164.97 | 1 | 1 | 164.9667 | 28 | OTHER (DESCRIBE) | 45 | SUBSTATION CIRCUIT | POTEAU | 114 TEAKWOOD, POTEAU | CMI_NORMAL | NO | NO | NO | 861594 | 82280 | 13498 | 2051 | 707 | 0.00019147 | 1.1606e-06 | 164.9667 | 1 | 310 | Customer | 12184 | Load | Tran1phPad | JOHN MEEH | 918-413-0959 | [5 empty] | Other | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | #N/A
J2002.001234 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-02-04 17:58 | 2020-02-04 18:09 | 10.65 | 1 | 1 | 10.65 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1301 W.HEFNER RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 8788 | 1952 | 1.2361e-05 | 1.1606e-06 | 10.65 | 1 | 310 | Customer | 75517 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.001233 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-02-04 17:59 | 2020-02-04 18:06 | 6.85 | 1 | 1 | 6.85 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 9017 N UNIVERSITY AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168267 | 148440 | 8788 | 1952 | 7.9504e-06 | 1.1606e-06 | 6.85 | 1 | 310 | Customer | 372819 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.001236 | PD-02042020-00415 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6523 | 836523 | 2020-02-04 18:00 | 2020-02-04 19:02 | 61.78 | 1 | 1 | 61.7833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 7317 KNIGHT LAKE DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 128890 | 116115 | 7425 | 2257 | 7.1708e-05 | 1.1606e-06 | 61.7833 | 1 | 310 | Customer | 38611 | Load | Tran1phPad | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2022
J2002.001237 |  | METRO SOUTH | SOUTH | 8728:CHERRY CREEK | CHERRY_CREEK_2823 | 872823 | 2020-02-04 18:03 | 2020-02-04 18:32 | 28.85 | 1 | 1 | 28.85 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | WS I-35 1/2 M N OF ROBINSON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 57018 | 7108 | 1302 | 3.3484e-05 | 1.1606e-06 | 28.85 | 1 | 310 | Customer | 78116 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001239 |  | NORTHEAST | SAPULPA | 7632:OAK GROVE | OAK_GROVE_3221 | 763221 | 2020-02-04 18:09 | 2020-02-04 18:09 | 0 | 1020 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | DRUMRIGHT | 210 S CREEK RD | CMI_MOMENTARY | YES | NO | NO | 861594 | 74092 | 40794 | 1020 | 1020 | 0 | 0.0011839 | 0 | 1 | 0 | Feeder | OAK GRV_3221 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.001241 | PD-02042020-00420 | METRO EAST | SHAWNEE | 7432:ST GREGORY | ST_GREGORY_3224 | 743224 | 2020-02-04 18:22 | 2020-02-04 20:16 | 113.73 | 1 | 1 | 113.7333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | SHAWNEE | 2801 N.UNION | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 114447 | 22126 | 4094 | 1373 | 0.000132 | 1.1606e-06 | 113.7333 | 1 | 310 | Customer | 16747 | Load | Tran1phPad | KYLE L GOODIN | 405-426-9802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001245 | PD-02042020-00423 | METRO EAST | EAST | 8542:RENO | RENO_4231 | 854231 | 2020-02-04 18:54 | 2020-02-04 21:47 | 173.18 | 1 | 1 | 140.8333 | 27 | TREE:NON PREVENTABLE | 31 | CONDUCTOR SERVICE - OH | DEL CITY | 852 BRIARLANE RD | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 114447 | 71230 | 5215 | 959 | 0.00016346 | 1.1606e-06 | 140.8333 | 1 | 320 | Customer | 20997 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.001247 | PD-02042020-00424 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-02-04 19:04 | 2020-02-04 20:49 | 104.87 | 1 | 1 | 104.8667 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 1947 NW 13TH ST OKLAHOMA CITY 731062009 | CMI_NORMAL | NO | NO | NO | 861594 | 168282 | 148455 | 11129 | 2058 | 0.00012171 | 1.1606e-06 | 104.8667 | 1 | 320 | Customer | 334221 | Load | Tran1phOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.001249 |  | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2022 | 822022 | 2020-02-04 19:15 | 2020-02-04 19:22 | 7.1 | 1 | 1 | 7.1 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2709 NW.21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 168282 | 148455 | 6038 | 2119 | 8.2405e-06 | 1.1606e-06 | 7.1 | 1 | 310 | Customer | 27390 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | OK - 2020
J2002.001251 |  | SOUTHERN | PAULS VALLEY | 5619:RUSH CREEK | RUSH_CREEK_1922 | 561922 | 2020-02-04 19:20 | 2020-02-04 19:25 | 5.12 | 1 | 1 | 5.1167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | PAULS VALLEY | #8 WS CHAPPEL RDG APT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 77647 | 6214 | 2073 | 1193 | 5.9386e-06 | 1.1606e-06 | 5.1167 | 1 | 310 | Customer | 141957 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.001252 | PD-02042020-00425 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2623 | 862623 | 2020-02-04 19:23 | 2020-02-04 20:37 | 73.52 | 1 | 1 | 73.5167 | 11 | OVERLOAD | 54 | LIGHTING - SECURITY | OKLAHOMA CITY | 1616 SE.23 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 7420 | 297 | 8.5326e-05 | 1.1606e-06 | 73.5167 | 1 | 310 | Customer | 62667 | Load | TranOpenDelta | 1337: NOT FOUND 1337: NOT FOUND | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001256 | PD-02042020-00426 | SOUTHERN | PAULS VALLEY | 5619:RUSH CREEK | RUSH_CREEK_1922 | 561922 | 2020-02-04 19:42 | 2020-02-04 20:19 | 37.15 | 1 | 1 | 37.15 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | PAULS VALLEY | #8 WS CHAPPEL RDG APT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 77647 | 6214 | 2073 | 1193 | 4.3118e-05 | 1.1606e-06 | 37.15 | 1 | 310 | Customer | 141957 | Load | Tran1phPad | CHAD A DOTSON | 405-488-5658 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.001266 | PD-02042020-00431 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7429 | 847429 | 2020-02-04 20:56 | 2020-02-04 22:09 | 72.83 | 8 | 10 | 542.4667 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 1621 NE.33 | CMI_NORMAL | NO | NO | NO | 861594 | 168282 | 148455 | 6171 | 681 | 0.00062961 | 9.2851e-06 | 67.8083 | 1 | 310 | Load | 4226 | Load | Tran1phOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | OK - 2022
J2002.001275 |  | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4122 | 814122 | 2020-02-04 21:51 | 2020-02-04 22:01 | 9.9 | 1 | 1 | 9.9 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 338 SE.48 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 5808 | 1272 | 1.149e-05 | 1.1606e-06 | 9.9 | 1 | 320 | Customer | 9591 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | #N/A
J2002.001277 | PD-02042020-00433 | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-02-04 21:52 | 2020-02-05 01:23 | 211.28 | 164 | 72 | 25911.55 | 27 | TREE:NON PREVENTABLE | 16 | LINE RECLOSER | TISHOMINGO | 6th & neshoba | CMI_NORMAL | NO | NO | NO | 861594 | 77647 | 7198 | 2189 | 1670 | 0.030074 | 0.00019034 | 157.9973 | 1 | 310 | Mainline | 335074 | Recloser | Rec3phHydralic | GARRETT YOUNG | 580-276-6194 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-04 | 2020 |  | #N/A
J2002.001290 | PD-02042020-00432 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4123 | 814123 | 2020-02-04 22:03 | 2020-02-04 23:30 | 86.55 | 1 | 1 | 86.55 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 5900 S.SHIELDS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 159220 | 102202 | 5808 | 1322 | 0.00010045 | 1.1606e-06 | 86.55 | 1 | 310 | Customer | 8900 | Load | TranOHDeltaSplitBank | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | #N/A
J2002.001300 | PD-02042020-00434 | METRO EAST | SEMINOLE | 7505:WEWOKA | WEWOKA 24 | 750524 | 2020-02-04 22:16 | 2020-02-05 00:10 | 113.72 | 1 | 1 | 113.7167 | 13 | PREMATURE FAILURE | 15 | METER - SECONDARY | WEWOKA | 403 N.WEWOKA | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861594 | 114447 | 13617 | 2477 | 1193 | 0.00013198 | 1.1606e-06 | 113.7167 | 1 | 310 | Customer | 12417 | Load | TranOpenDelta | BRADY A HUFF | 405-519-0701 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | OK - 2021
J2002.001311 | PD-02052020-00004 | ARKANSAS | POTEAU | 3608:MULDROW | MULDROW 21 | 360821 | 2020-02-04 23:12 | 2020-02-05 00:27 | 75.13 | 1 | 1 | 75.1333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MULDROW | 12TH + CADDO - MULDROW | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861594 | 82281 | 13499 | 2273 | 1226 | 8.7203e-05 | 1.1606e-06 | 75.1333 | 1 | 310 | Customer | 1802 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-04 | 2020 |  | #N/A
J2002.001337 | PD-02052020-00015 | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9869 | 839869 | 2020-02-05 04:25 | 2020-02-05 10:31 | 365.97 | 12 | 15 | 4348 | 3 | DAMAGED BY PUBLIC | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | 1/4N-NW 164TH, WS-PENN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 10663 | 3001 | 0.0050456 | 1.3925e-05 | 362.3333 | 1 | 310 | Load | 16722 | Load | Tran1phOH | DARREN L STOCKTON | 918-777-1697 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001349 | PD-02052020-00020 | METRO EAST | SEMINOLE | 7505:WEWOKA | WEWOKA 21 | 750521 | 2020-02-05 04:46 | 2020-02-05 07:40 | 173.93 | 31 | 19 | 4179.8333 | 7 | ICE / SLEET / SNOW | 23 | FUSE - PRIMARY | WEWOKA | 1MI W DIXON ADD HWY270 | CMI_NORMAL | NO | NO | NO | 861739 | 114447 | 13617 | 2477 | 1284 | 0.0048505 | 3.5974e-05 | 134.8333 | 1 | 310 | Mainline | 7364 | Fuse | FuseOH | BRADY A HUFF | 405-519-0701 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | OK - 2021
J2002.001341 | PD-02052020-00018 | SOUTHERN | PAULS VALLEY | 5620:PRAIRIE POINT | PRAIRIE_POINT_2021 | 562021 | 2020-02-05 04:49 | 2020-02-05 06:25 | 95.7 | 1 | 1 | 84.6667 | 7 | ICE / SLEET / SNOW | 21 | FUSE - TRANSFORMER | ELMORE CITY | 1MN SH29 ON SH74 | CMI_NORMAL | NO | NO | NO | 861739 | 77647 | 6214 | 607 | 569 | 9.8251e-05 | 1.1604e-06 | 84.6667 | 1 | 310 | Load | 30313 | Load | Tran1phOH | CHAD A DOTSON | 405-488-5658 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2021
J2002.001485 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_824 | 870824 | 2020-02-05 05:08 | 2020-02-05 09:30 | 261.83 | 1 | 0 | 261.8333 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 1607 WESTBROOK TR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 57018 | 6776 | 1462 | 0.00030384 | 1.1604e-06 | 261.8333 | 1 | 0 | Customer | 46072 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001487 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_824 | 870824 | 2020-02-05 05:08 | 2020-02-05 09:30 | 261.4 | 1 | 0 | 237.6667 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 2751 MEADOWBROOK DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 57018 | 6776 | 1462 | 0.0002758 | 1.1604e-06 | 237.6667 | 1 | 0 | Customer | 33125 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001488 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_824 | 870824 | 2020-02-05 05:08 | 2020-02-05 09:29 | 260.92 | 1 | 0 | 260.9167 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 2510 CYPRESS AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 57018 | 6776 | 1462 | 0.00030278 | 1.1604e-06 | 260.9167 | 1 | 0 | Customer | 46021 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001347 | PD-02052020-00019 | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_821 | 870821 | 2020-02-05 05:08 | 2020-02-05 08:04 | 175.55 | 1060 | 457 | 186083 | 13 | PREMATURE FAILURE | 45 | SUBSTATION CIRCUIT | NORMAN | 537 BRATCHER-MINER RD | CMI_NORMAL | NO | NO | NO | 861739 | 159220 | 57018 | 6776 | 1129 | 0.21594 | 0.0012301 | 175.55 | 1 | 310 | Feeder | CEDAR LN_821 | Recloser | SubRecloser | [7 empty] | Equipment | N | SUBSTATION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001356 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_823 | 870823 | 2020-02-05 05:17 | 2020-02-05 08:59 | 221.78 | 4789 | 1387 | 1405641.4 | 13 | PREMATURE FAILURE | 45 | SUBSTATION CIRCUIT | NORMAN | 537 BRATCHER-MINER RD | CMI_NORMAL | NO | NO | NO | 861739 | 159220 | 57018 | 6776 | 0 | 1.6312 | 0.0055574 | 293.5146 | 1 | 310 | Substation | CEDAR LN_121 | Breaker | SubRecloser | Crew | [5 empty] | 08/12/2020 note from burchamc. Reference J2002.001356 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Manually completed blank Job Region, Job Area, etc. | Equipment | N | SUBSTATION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001360 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_822 | 870822 | 2020-02-05 05:17 | 2020-02-05 09:45 | 268.22 | 20 | 9 | 4146.6667 | 13 | PREMATURE FAILURE | 45 | SUBSTATION CIRCUIT | NORMAN | EASTGATE DR | CMI_NORMAL | NO | NO | NO | 861739 | 159220 | 57018 | 6776 | 1805 | 0.004812 | 2.3209e-05 | 207.3333 | 1 | 310 | Load | 71916 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001372 | PD-02052020-00022 | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9869 | 839869 | 2020-02-05 05:18 | 2020-02-05 10:31 | 313.2 | 2989 | 972 | 463989.3167 | 3 | DAMAGED BY PUBLIC | 28 | CROSSARM | OKLAHOMA CITY | 1418 NW 164TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 10663 | 3001 | 0.53843 | 0.0034686 | 155.2323 | 1 | 310 | Feeder | CHISHOLM_CREEK_9869 | Recloser | 0 | BRIAN E WHITE | 405-642-7075 | [5 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001358 |  | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_622 | 580622 | 2020-02-05 05:22 | 2020-02-05 05:32 | 10.1 | 1 | 1 | 10.1 | 1 | CANCELLED | 57 | CANCELLED | ADA | 908 N.CNTRY-CLB RD 29 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 77647 | 11520 | 2519 | 780 | 1.172e-05 | 1.1604e-06 | 10.1 | 1 | 310 | Customer | 20873 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | #N/A
J2002.001365 | PD-02052020-00028 | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2731 | 872731 | 2020-02-05 05:25 | 2020-02-05 09:31 | 245.63 | 1 | 1 | 201.95 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | 614 UTAH AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 57018 | 6493 | 1352 | 0.00023435 | 1.1604e-06 | 201.95 | 1 | 310 | Customer | 44657 | Load | Tran1phOH | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001392 |  | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9869 | 839869 | 2020-02-05 05:33 | 2020-02-05 13:27 | 474.57 | 1 | 2 | 101.6667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 0 | 0 | 0 | 0 | 0.00011798 | 1.1604e-06 | 101.6667 | 1 | 310 | Customer |  | 0 | 0 | [6 empty] | 06/10/2020 note from burchamc. Reference J2002.001392 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001416 | PD-02052020-00027 | NORTHWEST | ENID | 4210:MEDFORD | MEDFORD 22 | 421022 | 2020-02-05 06:23 | 2020-02-05 06:45 | 21.73 | 1 | 1 | 37.8 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MEDFORD | E.EDGE-MEDFORD ON CHEROKEE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 53567 | 37614 | 744 | 681 | 4.3865e-05 | 1.1604e-06 | 37.8 | 1 | 310 | Customer | 8273 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | #N/A
J2002.001417 |  | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_622 | 580622 | 2020-02-05 06:30 | 2020-02-05 06:30 | 0 | 779 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ADA | 1806 A ST | CMI_MOMENTARY | YES | NO | NO | 861739 | 77647 | 11520 | 2519 | 780 | 0 | 0.00090399 | 0 | 1 | 0 | Feeder | VALLEY_VIEW_622 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-05 | 2020 |  | #N/A
J2002.001420 | PD-02052020-00029 | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_822 | 870822 | 2020-02-05 06:34 | 2020-02-05 09:41 | 186.65 | 1 | 1 | 94.4333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | Norman Sewer Plant | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 57018 | 6776 | 1805 | 0.00010958 | 1.1604e-06 | 94.4333 | 1 | 310 | Load | 373822 | Load | Tran3phPadWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001421 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_871 | 830871 | 2020-02-05 06:40 | 2020-02-05 08:05 | 85.13 | 1 | 1 | 85.1333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | Valencia II - NW 184th Lot 4 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 19396 | 4249 | 9.8792e-05 | 1.1604e-06 | 85.1333 | 1 | 310 | Customer | 302412 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2021
J2002.001422 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_871 | 830871 | 2020-02-05 06:42 | 2020-02-05 08:11 | 89.78 | 1 | 1 | 33.35 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2604 NW 186TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 19396 | 4249 | 3.8701e-05 | 1.1604e-06 | 33.35 | 1 | 310 | Customer | 333640 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2021
J2002.001425 |  | METRO SOUTH | SOUTH | 8722:MILLENNIUM | MILLENNIUM_2229 | 872229 | 2020-02-05 06:56 | 2020-02-05 07:05 | 9.22 | 1 | 1 | 9.2167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 1305 12 AV NE. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 57018 | 4205 | 775 | 1.0695e-05 | 1.1604e-06 | 9.2167 | 1 | 310 | Customer | 44392 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001432 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_822 | 870822 | 2020-02-05 07:17 | 2020-02-05 07:54 | 36.65 | 1 | 1 | 24.55 | 13 | PREMATURE FAILURE | 45 | SUBSTATION CIRCUIT | NORMAN | 2316 HOUSTON AV | CMI_NORMAL | NO | NO | NO | 861739 | 159220 | 57018 | 6776 | 1805 | 2.8489e-05 | 1.1604e-06 | 24.55 | 1 | 310 | Customer | 46622 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001431 | PD-02052020-00031 | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-02-05 07:18 | 2020-02-05 08:55 | 97.18 | 1 | 1 | 97.1833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BIXBY | 1/8 N. of 151st Str. on Armstrong Str. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 74092 | 40794 | 2753 | 1441 | 0.00011278 | 1.1604e-06 | 97.1833 | 1 | 310 | Customer | 333475 | Load | Tran3phPadWye | JOSHUA N MCKINNEY | 918-863-6313 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | OK - 2021
J2002.001433 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_822 | 870822 | 2020-02-05 07:19 | 2020-02-05 09:47 | 148.28 | 1 | 1 | 23.0333 | 13 | PREMATURE FAILURE | 45 | SUBSTATION CIRCUIT | NORMAN | 2275 DONNA DR | CMI_NORMAL | NO | NO | NO | 861739 | 159220 | 57018 | 6776 | 1805 | 2.6729e-05 | 1.1604e-06 | 23.0333 | 1 | 310 | Customer | 39236 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001434 |  | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6022 | 836022 | 2020-02-05 07:30 | 2020-02-05 07:30 | 0 | 1234 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 4315 N COUNCIL RD | CMI_MOMENTARY | YES | NO | NO | 861739 | 128890 | 116115 | 5508 | 1234 | 0 | 0.001432 | 0 | 1 | 0 | Feeder | WOODLAWN_6022 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001436 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_823 | 870823 | 2020-02-05 07:32 | 2020-02-05 07:55 | 23.88 | 1 | 1 | 10 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 0 | 0 | 0 | 0 | 1.1604e-05 | 1.1604e-06 | 10 | 1 | 310 | Customer |  | 0 | 0 | [6 empty] | 06/10/2020 note from burchamc. Reference J2002.001436 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001439 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_871 | 830871 | 2020-02-05 07:34 | 2020-02-05 08:19 | 45.47 | 1 | 1 | 45.4667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | .5ME-PENN ON NW.178 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 19396 | 4249 | 5.2762e-05 | 1.1604e-06 | 45.4667 | 1 | 310 | Customer | 75375 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2021
J2002.001438 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3829 | 913829 | 2020-02-05 07:40 | 2020-02-05 07:40 | 0 | 1187 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | FT SMITH | 1904 SOUTH 7TH ST | CMI_MOMENTARY | YES | NO | NO | 861739 | 82281 | 61234 | 2938 | 1187 | 0 | 0.0013774 | 0 | 1 | 0 | Feeder | ARKOMA_3829 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-02-05 | 2020 |  | Ark - Series 2
J2002.001442 |  | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9871 | 839871 | 2020-02-05 07:51 | 2020-02-05 08:13 | 22.05 | 1 | 1 | 22.05 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 16417 BORDEAUS DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 10663 | 2048 | 2.5588e-05 | 1.1604e-06 | 22.05 | 1 | 310 | Customer | 382311 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001443 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_871 | 830871 | 2020-02-05 07:53 | 2020-02-05 08:14 | 20.8 | 1 | 1 | 20.8 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 18600 MULHOLLAND DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 19396 | 4249 | 2.4137e-05 | 1.1604e-06 | 20.8 | 1 | 310 | Customer | 85526 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2021
J2002.001444 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-05 08:03 | 2020-02-05 11:19 | 196.55 | 3 | 3 | 561.05 | 4 | DETERIORATION | 12 | POLE | LAMAR | 300 W-JOHNSONVILLE ON 64,LAMAR | CMI_PLANNED | YES | NO | NO | 861739 | 82281 | 7548 | 730 | 0 | 0.00065107 | 3.4813e-06 | 187.0167 | 1 | 308 | Load | 4895 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | #N/A
J2002.001445 | PD-02052020-00050 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_871 | 830871 | 2020-02-05 08:05 | 2020-02-05 09:12 | 67.32 | 1 | 1 | 67.3167 | 3 | DAMAGED BY PUBLIC | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | Silver Hawk blk 9, | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 19396 | 4249 | 7.8117e-05 | 1.1604e-06 | 67.3167 | 1 | 310 | Customer | 256454 | Load | Tran3phPadWye | DARREN L STOCKTON | 918-777-1697 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2021
J2002.001446 |  | METRO SOUTH | SOUTH | 8728:CHERRY CREEK | CHERRY_CREEK_2823 | 872823 | 2020-02-05 08:06 | 2020-02-05 08:16 | 10.65 | 1 | 1 | 10.65 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | WS I-35 1/2 M N OF ROBINSON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 57018 | 7108 | 1302 | 1.2359e-05 | 1.1604e-06 | 10.65 | 1 | 310 | Customer | 78116 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001479 | PD-02052020-00081 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4864 | 824864 | 2020-02-05 08:37 | 2020-02-05 11:56 | 198.7 | 1 | 1 | 198.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2416 SW 21ST ST OKLAHOMA CITY 731086005 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 4199 | 2030 | 0.00023058 | 1.1604e-06 | 198.7 | 1 | 310 | Customer | 347693 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2021
J2002.001481 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_823 | 870823 | 2020-02-05 08:39 | 2020-02-05 08:49 | 9.95 | 1 | 1 | 9.95 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | Jenkins Ave. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 57018 | 6776 | 2379 | 1.1546e-05 | 1.1604e-06 | 9.95 | 1 | 310 | Customer | 33749 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001482 | PD-02052020-00077 | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_622 | 410622 | 2020-02-05 08:39 | 2020-02-05 09:47 | 67.68 | 1 | 1 | 67.6833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ENID | 1809 GINGHAM | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 53567 | 37614 | 6021 | 1509 | 7.8543e-05 | 1.1604e-06 | 67.6833 | 1 | 320 | Customer | 11913 | Load | Tran1phPad | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | #N/A
J2002.001483 | PD-02052020-00082 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2023 | 822023 | 2020-02-05 08:43 | 2020-02-05 10:24 | 100.92 | 1 | 1 | 66.1786 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3100 W.PIONEER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 6038 | 1028 | 7.6797e-05 | 1.1604e-06 | 66.1786 | 1 | 310 | Customer | 3413 | Load | Tran1phOH | REX R WILSON | 405-535-4507 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001484 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_823 | 870823 | 2020-02-05 08:44 | 2020-02-05 08:44 | 0 | 879 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | NORMAN | JENKINS AV & W TIMBERDELL RD | CMI_MOMENTARY | YES | NO | NO | 861739 | 159220 | 57018 | 6776 | 2379 | 0 | 0.00102 | 0 | 1 | 0 | Mainline | 332650 | Recloser | Rec3phElectronic | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001489 | PD-02052020-00086 | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2129 | 332129 | 2020-02-05 08:51 | 2020-02-05 10:40 | 109.27 | 1 | 1 | 102.3333 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | FORT GIBSON | FT GIBSON,203 GLAD STR. | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861739 | 74092 | 33298 | 3337 | 942 | 0.00011875 | 1.1604e-06 | 102.3333 | 1 | 310 | Customer | 13622 | Load | Tran1phPad | CONTRACTOR 5 DAVID ELLIOT INC | 918-639-5055 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-05 | 2020 |  | #N/A
J2002.001490 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6328 | 816328 | 2020-02-05 08:55 | 2020-02-05 09:07 | 11.73 | 1 | 1 | 11.7333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MOORE | 441 S.TELEPHONE RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 102202 | 11841 | 1188 | 1.3616e-05 | 1.1604e-06 | 11.7333 | 1 | 310 | Customer | 56266 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001492 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_871 | 830871 | 2020-02-05 09:06 | 2020-02-05 09:09 | 2.93 | 1 | 1 | 2.9333 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | NW 17604 IRON LANE | CMI_MOMENTARY | YES | NO | NO | 861739 | 168282 | 148455 | 19396 | 4249 | 3.404e-06 | 1.1604e-06 | 2.9333 | 1 | 310 | Customer | 85118 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2021
J2002.001497 | PD-02052020-00110 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7422 | 847422 | 2020-02-05 09:14 | 2020-02-05 11:11 | 117.47 | 1 | 1 | 117.4667 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 3003 N Oklahoma | CMI_NORMAL | NO | NO | NO | 861739 | 168282 | 148455 | 6171 | 1215 | 0.00013631 | 1.1604e-06 | 117.4667 | 1 | 310 | Load | 254839 | Load | TranOpenDelta | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001499 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-02-05 09:18 | 2020-02-05 09:25 | 6.77 | 1 | 1 | 6.7667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 11601 SE 156TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 57018 | 4239 | 1005 | 7.8523e-06 | 1.1604e-06 | 6.7667 | 1 | 310 | Customer | 78787 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001504 |  | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1421 | 311421 | 2020-02-05 09:28 | 2020-02-05 09:43 | 15.57 | 1 | 1 | 15.5667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 4115 ROBB | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 74092 | 33298 | 4572 | 1104 | 1.8064e-05 | 1.1604e-06 | 15.5667 | 1 | 310 | Customer | 5191 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | #N/A
J2002.001507 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_823 | 870823 | 2020-02-05 09:33 | 2020-02-05 09:38 | 5.28 | 1 | 1 | 5.2833 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 2001 TEXAS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 57018 | 6776 | 2379 | 6.131e-06 | 1.1604e-06 | 5.2833 | 1 | 315 | Customer | 33384 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001508 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_823 | 870823 | 2020-02-05 09:34 | 2020-02-05 09:41 | 6.9 | 1 | 1 | 6.9 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 1500 E.LINDSEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 57018 | 6776 | 2379 | 8.0071e-06 | 1.1604e-06 | 6.9 | 1 | 310 | Customer | 74283 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001511 | PD-02052020-00133 | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9862 | 839862 | 2020-02-05 09:38 | 2020-02-05 10:21 | 43.35 | 1 | 1 | 43.35 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 15800 SHADOW MTN-DRIVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 10663 | 2316 | 5.0305e-05 | 1.1604e-06 | 43.35 | 1 | 310 | Customer | 83068 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001510 | PD-02052020-00132 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6523 | 836523 | 2020-02-05 09:38 | 2020-02-05 11:21 | 103.22 | 1 | 1 | 77.6519 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7317 KNIGHT LAKE DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 128890 | 116115 | 7425 | 2257 | 9.0111e-05 | 1.1604e-06 | 77.6519 | 1 | 310 | Customer | 38611 | Load | Tran1phPad | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001521 | PD-02052020-00139 | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-02-05 09:39 | 2020-02-05 12:56 | 197.1 | 355 | 143 | 46321.5833 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | TISHOMINGO | 6th & neshoba | CMI_NORMAL | NO | NO | NO | 861739 | 77647 | 7198 | 2189 | 1670 | 0.053754 | 0.00041196 | 130.4833 | 1 | 321 | Mainline | 335074 | Recloser | Rec3phHydralic | DAVID TAYLOR | 580-574-4517 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001514 |  | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_923 | 910923 | 2020-02-05 09:43 | 2020-02-05 10:19 | 36.28 | 1 | 1 | 36.2833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 320 N-S.UTICA + 115 W-S.11TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 82281 | 61234 | 5015 | 902 | 4.2105e-05 | 1.1604e-06 | 36.2833 | 1 | 310 | Customer | 3456 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | Ark - Series 3
J2002.001516 |  | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-02-05 09:44 | 2020-02-05 12:24 | 160.75 | 1 | 1 | 160.75 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | TISHOMINGO | 405 N NESHOBA | CMI_NORMAL | NO | NO | NO | 861739 | 77647 | 7198 | 2189 | 1670 | 0.00018654 | 1.1604e-06 | 160.75 | 1 | 320 | Customer | 1004 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001524 | PD-02052020-00134 | METRO SOUTH | SOUTH | 8722:MILLENNIUM | MILLENNIUM_2222 | 872222 | 2020-02-05 09:46 | 2020-02-05 10:30 | 44.15 | 1 | 1 | 44.15 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | 603 OKMULGEE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 57018 | 4205 | 737 | 5.1234e-05 | 1.1604e-06 | 44.15 | 1 | 310 | Customer | 44282 | Load | TranOpenDelta | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001525 |  | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-02-05 09:47 | 2020-02-05 13:58 | 251.07 | 3 | 3 | 367.05 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | TISHOMINGO | W 12TH ST | CMI_NORMAL | NO | NO | NO | 861739 | 77647 | 7198 | 2189 | 1670 | 0.00042594 | 3.4813e-06 | 122.35 | 1 | 310 | Secondary | 12205 | Load | Tran1phOH | Ties | [6 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001528 | PD-02052020-00141 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1522 | 811522 | 2020-02-05 09:47 | 2020-02-05 12:10 | 142.92 | 1 | 1 | 142.9167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3408 S.YOUNGS BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 102202 | 6066 | 1943 | 0.00016585 | 1.1604e-06 | 142.9167 | 1 | 310 | Customer | 25353 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001536 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_823 | 870823 | 2020-02-05 09:50 | 2020-02-05 09:54 | 3.45 | 1 | 1 | 3.45 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 1621 PARKVIEW TR | CMI_MOMENTARY | YES | NO | NO | 861739 | 159220 | 57018 | 6776 | 2379 | 4.0035e-06 | 1.1604e-06 | 3.45 | 1 | 310 | Customer | 31658 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001543 | PD-02052020-00147 | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8123 | 838123 | 2020-02-05 09:58 | 2020-02-05 11:34 | 95.97 | 1 | 1 | 57.0164 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 8301 N. COUNCIL, #1601 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 128890 | 116115 | 8958 | 1216 | 6.6164e-05 | 1.1604e-06 | 57.0164 | 1 | 310 | Customer | 73564 | Load | Tran1phPad | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001546 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_823 | 870823 | 2020-02-05 10:03 | 2020-02-05 10:08 | 4.68 | 1 | 1 | 4.6833 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 1027 BILOXI DR | CMI_MOMENTARY | YES | NO | NO | 861739 | 159220 | 57018 | 6776 | 2379 | 5.4347e-06 | 1.1604e-06 | 4.6833 | 1 | 310 | Customer | 46864 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001547 |  | NORTHEAST | MUSKOGEE | 3325:WELLS | WELLS_2549 | 332549 | 2020-02-05 10:03 | 2020-02-05 10:13 | 10.45 | 1 | 1 | 10.45 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | COUNCIL HILL | COUNCL HL OK 74428 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 74092 | 33298 | 2381 | 1052 | 1.2127e-05 | 1.1604e-06 | 10.45 | 1 | 310 | Customer | 9367 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | OK - 2021
J2002.001549 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_823 | 870823 | 2020-02-05 10:09 | 2020-02-05 10:18 | 8.82 | 1 | 1 | 8.8167 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 817 E LINDSEY 819 NORMAN 73071 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 57018 | 6776 | 2379 | 1.0231e-05 | 1.1604e-06 | 8.8167 | 1 | 310 | Customer | 36555 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001552 | PD-02052020-00168 | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3829 | 913829 | 2020-02-05 10:26 | 2020-02-05 11:11 | 45.3 | 1 | 1 | 45.3 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | FORT SMITH | 428 S. U - ALANTIS PLASTICS | CMI_NORMAL | NO | NO | NO | 861739 | 82281 | 61234 | 2938 | 1187 | 5.2568e-05 | 1.1604e-06 | 45.3 | 1 | 321 | Load | 15396 | Load | Tran3phPadWye | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-02-05 | 2020 |  | Ark - Series 2
J2002.001554 | PD-02052020-00166 | NORTHEAST | SAPULPA | 4239:OTOE | OTOE 22 | 423922 | 2020-02-05 10:28 | 2020-02-05 12:32 | 124.37 | 1 | 1 | 124.3667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | RED ROCK | SOONER PLANT - CONST POWER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 74092 | 40794 | 136 | 136 | 0.00014432 | 1.1604e-06 | 124.3667 | 1 | 310 | Load | 378996 | Load | Tran3phPadWye | BRAD WRIGHT | 918-629-1747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001557 | PD-02052020-00197 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-02-05 10:34 | 2020-02-05 11:50 | 75.9 | 1 | 1 | 75.9 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | ARDMORE | SPDL RD 3.6E 1S .1W | CMI_NORMAL | NO | NO | NO | 861739 | 77647 | 23595 | 2208 | 1002 | 8.8078e-05 | 1.1604e-06 | 75.9 | 1 | 310 | Customer | 21559 | Load | Tran1phOH | RANDAL G CALLAWAY | 580-220-8449 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001559 |  | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9869 | 839869 | 2020-02-05 10:38 | 2020-02-05 11:02 | 24.52 | 2 | 2 | 48.1167 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1925 NW 173RD STREET | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 10663 | 3001 | 5.5837e-05 | 2.3209e-06 | 24.0583 | 1 | 310 | Customer | 199006 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001568 |  | NORTHWEST | WOODWARD | 4616:NEWMAN AVE | NEWMAN_AVE_1641 | 461641 | 2020-02-05 10:51 | 2020-02-05 17:56 | 424.47 | 1 | 1 | 368.2333 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | SHATTUCK | 3NE-.5SEC LINE,HWY15 S SHATTUCK | CMI_PLANNED | YES | NO | NO | 861739 | 53567 | 10430 | 2012 | 2012 | 0.00042731 | 1.1604e-06 | 368.2333 | 1 | 308 | Load | 10614 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | OK - 2020
J2002.001563 | PD-02052020-00187 | METRO NORTH | NORTH | 8209:CLASSEN | CLASSEN_961 | 820961 | 2020-02-05 10:52 | 2020-02-05 11:57 | 65.18 | 1 | 1 | 38.57 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 50 N Fred Jones Ave | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 3888 | 868 | 4.4758e-05 | 1.1604e-06 | 38.57 | 1 | 310 | Customer | 391091 | Load | Tran3phPadWye | REX R WILSON | 405-535-4507 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001569 |  | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-02-05 10:52 | 2020-02-05 13:57 | 184.93 | 1 | 2 | 56.8833 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | TISHOMINGO | W OF TISH | CMI_NORMAL | NO | NO | NO | 861739 | 77647 | 7198 | 2189 | 1670 | 6.601e-05 | 1.1604e-06 | 56.8833 | 1 | 310 | Load | 14625 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001566 | PD-02052020-00194 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_530 | 510530 | 2020-02-05 10:53 | 2020-02-05 11:34 | 41.43 | 1 | 1 | 41.4333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ARDMORE | 128 F NW. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 77647 | 23595 | 4777 | 600 | 4.8081e-05 | 1.1604e-06 | 41.4333 | 1 | 310 | Customer | 2016 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | #N/A
J2002.001565 |  | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_722 | 510722 | 2020-02-05 10:54 | 2020-02-05 10:54 | 0.02 | 1286 | 0 | 21.4333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 101 D ST NW | CMI_MOMENTARY | YES | NO | NO | 861739 | 77647 | 23595 | 4512 | 985 | 2.4872e-05 | 0.0014923 | 0.016667 | 1 | 0 | Feeder | TOWER_HEIGHTS_722 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-05 | 2020 |  | #N/A
J2002.001571 |  | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1122 | 511122 | 2020-02-05 10:57 | 2020-02-05 12:14 | 77.68 | 1 | 1 | 52.4333 | 29 | TREES : GROW IN | 37 | CONDUCTOR PRIMARY - OH | DICKSON | 70 7E NS | CMI_NORMAL | NO | NO | NO | 861739 | 77647 | 23595 | 2208 | 1206 | 6.0846e-05 | 1.1604e-06 | 52.4333 | 1 | 310 | Customer | 2335 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001570 | PD-02052020-00198 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-02-05 10:57 | 2020-02-05 14:04 | 186.87 | 207 | 72 | 37649.85 | 22 | WIND | 37 | CONDUCTOR PRIMARY - OH | ARDMORE | .5MS/SPRGDL ES M.NIBLK | CMI_NORMAL | NO | NO | NO | 861739 | 77647 | 23595 | 2208 | 1002 | 0.043691 | 0.00024021 | 181.8833 | 1 | 310 | Mainline | 9103 | Recloser | Rec3phHydralic | JIMMY DON ROWE | 580-490-6283 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001574 |  | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-02-05 11:07 | 2020-02-05 13:56 | 168.52 | 1 | 1 | 168.5167 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | RAVIA | 10058 S BULLET PRAIRIE RD | CMI_NORMAL | NO | NO | NO | 861739 | 77647 | 7198 | 2189 | 1670 | 0.00019555 | 1.1604e-06 | 168.5167 | 1 | 310 | Load | 16650 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001575 | PD-02052020-00208 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1229 | 831229 | 2020-02-05 11:09 | 2020-02-05 13:14 | 125.32 | 11 | 12 | 1332.8333 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 2017 NW 47 | CMI_NORMAL | NO | NO | NO | 861739 | 168282 | 148455 | 7753 | 787 | 0.0015467 | 1.2765e-05 | 121.1667 | 1 | 310 | Load | 15952 | Load | TranOpenDelta | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001576 |  | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1823 | 931823 | 2020-02-05 11:12 | 2020-02-05 11:43 | 31.42 | 1 | 1 | 31.4167 | 1 | CANCELLED | 57 | CANCELLED | ALMA | ALMA GARDENS, | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 82281 | 61234 | 2848 | 1240 | 3.6457e-05 | 1.1604e-06 | 31.4167 | 1 | 310 | Customer | 225308 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | Ark - Series 2
J2002.001579 |  | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-02-05 11:13 | 2020-02-05 13:52 | 159.45 | 2 | 2 | 72.4833 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | TISHOMINGO | SH22 + SLIPPERY FALLS RD SS | CMI_NORMAL | NO | NO | NO | 861739 | 77647 | 7198 | 2189 | 1670 | 8.4113e-05 | 2.3209e-06 | 36.2417 | 1 | 310 | Secondary | 28391 | Load | Tran1phPad | [7 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001578 |  | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1823 | 931823 | 2020-02-05 11:13 | 2020-02-05 11:36 | 22.77 | 1 | 1 | 22.7667 | 1 | CANCELLED | 57 | CANCELLED | ALMA | KENTUCKY FRIED CHICK - ALMA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 82281 | 61234 | 2848 | 1240 | 2.6419e-05 | 1.1604e-06 | 22.7667 | 1 | 310 | Load | 2901 | Load | Tran3phPadWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | Ark - Series 2
J2002.001580 |  | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-02-05 11:14 | 2020-02-05 13:53 | 158.78 | 1 | 1 | 158.7833 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | TISHOMINGO | 1W TISH WYE, 1BKS HWY 22 | CMI_NORMAL | NO | NO | NO | 861739 | 77647 | 7198 | 2189 | 1670 | 0.00018426 | 1.1604e-06 | 158.7833 | 1 | 310 | Customer | 29377 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001581 | PD-02052020-00211 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3629 | 833629 | 2020-02-05 11:18 | 2020-02-05 11:52 | 34.15 | 1 | 1 | 34.15 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | THE VILLAGE | 1929 HASLEY DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 8789 | 1397 | 3.9629e-05 | 1.1604e-06 | 34.15 | 1 | 310 | Customer | 59501 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001585 | PD-02052020-00218 | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9869 | 839869 | 2020-02-05 11:26 | 2020-02-05 12:38 | 71.77 | 1 | 1 | 71.7667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1932 MULHOLLAND DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 10663 | 3001 | 8.3281e-05 | 1.1604e-06 | 71.7667 | 1 | 320 | Customer | 85769 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001586 | PD-02052020-00221 | SOUTHERN | SULPHUR | 5707:MILL CREEK | MILL CREEK 23 | 570723 | 2020-02-05 11:29 | 2020-02-05 17:10 | 341.17 | 1 | 1 | 341.1667 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | MILL CREEK | 2BLKS N OF MILL CREEK SCHOOL | CMI_NORMAL | NO | NO | NO | 861739 | 77647 | 6817 | 211 | 192 | 0.0003959 | 1.1604e-06 | 341.1667 | 1 | 310 | Customer | 22175 | Load | Tran1phOH | CHAD A DOTSON | 405-488-5658 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001588 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_822 | 870822 | 2020-02-05 11:32 | 2020-02-05 11:32 | 0 | 3825 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | NORMAN | 537 BRATCHER-MINER RD | CMI_MOMENTARY | YES | NO | NO | 861739 | 159220 | 57018 | 6776 | 1805 | 0 | 0.0044387 | 0 | 1 | 0 | Feeder | CEDAR LN_822 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001599 | PD-02052020-00232 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6024 | 836024 | 2020-02-05 11:34 | 2020-02-05 14:22 | 167.72 | 15 | 8 | 2380.75 | 5 | ELECTRICAL TRACKING | 27 | CUTOUT | BETHANY | 0.25M W NW 50 & COUNCIL | CMI_NORMAL | NO | NO | NO | 861739 | 128890 | 116115 | 5508 | 1342 | 0.0027627 | 1.7407e-05 | 158.7167 | 1 | 310 | Tap | 237737 | Fuse | FuseOH | JAMES CALDWELL | 405-973-6233 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001590 | PD-02052020-00239 | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_822 | 870822 | 2020-02-05 11:35 | 2020-02-05 12:49 | 74.38 | 1 | 1 | 7.8 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | CROWN RIDGE APTS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 57018 | 6776 | 1805 | 9.0515e-06 | 1.1604e-06 | 7.8 | 1 | 310 | Customer | 218664 | Load | Tran1phPad | MARK A PALMORE | 405-512-1933 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001593 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_822 | 870822 | 2020-02-05 11:42 | 2020-02-05 11:42 | 0.03 | 1264 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | NORMAN | 1401 CEDAR LN | CMI_MOMENTARY | YES | NO | NO | 861739 | 159220 | 57018 | 6776 | 1805 | 0 | 0.0014668 | 0 | 1 | 0 | Mainline | 332610 | Recloser | Rec3phElectronic | Crew | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001598 | PD-02052020-00234 | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1823 | 931823 | 2020-02-05 11:49 | 2020-02-05 13:44 | 114.75 | 1 | 1 | 111.7333 | 5 | ELECTRICAL TRACKING | 27 | CUTOUT | ALMA | 200.5S COLLUM ON WS HEATHER LN | CMI_NORMAL | NO | NO | NO | 861739 | 82281 | 61234 | 2848 | 1240 | 0.00012966 | 1.1604e-06 | 111.7333 | 1 | 310 | Secondary | 19987 | Load | Tran3phPadWye | MICHAEL L NEWMAN | 479-221-7071 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | Ark - Series 2
J2002.001600 |  | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-02-05 11:53 | 2020-02-05 14:06 | 133.33 | 1 | 1 | 133.3333 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | ARDMORE | .4 N SPRNDL RD ON MARY NIBLACK | CMI_NORMAL | NO | NO | NO | 861739 | 77647 | 23595 | 2208 | 1002 | 0.00015473 | 1.1604e-06 | 133.3333 | 1 | 310 | Load | 24752 | Load | TranOpenDelta | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001608 | PD-02052020-00247 | METRO EAST | SHAWNEE | 7407:REMINGTON | REMINGTON 22 | 740722 | 2020-02-05 12:05 | 2020-02-05 16:37 | 272.5 | 4 | 7 | 1066.4333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | SHAWNEE | 2 DUSTIN CI | CMI_NORMAL | NO | NO | NO | 861739 | 114447 | 22126 | 3667 | 1645 | 0.0012375 | 4.6418e-06 | 266.6083 | 1 | 310 | Load | 16898 | Load | Tran1phOH | JAMES CALDWELL | 405-973-6233 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | #N/A
J2002.001615 |  | METRO NORTH | NORTH | 8209:CLASSEN | CLASSEN_923 | 820923 | 2020-02-05 12:17 | 2020-02-05 12:17 | 0 | 1122 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 922 NW 4TH ST | CMI_MOMENTARY | YES | NO | NO | 861739 | 168282 | 148455 | 3888 | 1150 | 0 | 0.001302 | 0 | 1 | 0 | Feeder | CLASSEN_923 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001619 | PD-02052020-00250 | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9869 | 839869 | 2020-02-05 12:19 | 2020-02-05 12:50 | 30.57 | 1 | 1 | 30.5667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | Silver Hawk Sec 2 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 10663 | 3001 | 3.5471e-05 | 1.1604e-06 | 30.5667 | 1 | 310 | Customer | 257737 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001625 |  | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5024 | 865024 | 2020-02-05 12:27 | 2020-02-05 12:33 | 6.48 | 1 | 1 | 6.4833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 507 E.GRUMAN DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 114447 | 71230 | 8632 | 1076 | 7.5235e-06 | 1.1604e-06 | 6.4833 | 1 | 310 | Customer | 3401 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001624 | PD-02052020-00255 | METRO SOUTH | SOUTH | 8728:CHERRY CREEK | CHERRY_CREEK_2823 | 872823 | 2020-02-05 12:28 | 2020-02-05 13:48 | 80.25 | 1 | 1 | 44.8496 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 1414 BROAD ACRES DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 57018 | 7108 | 1302 | 5.2045e-05 | 1.1604e-06 | 44.8496 | 1 | 320 | Customer | 62656 | Load | Tran1phPad | SHANE DRAKE | 405-326-9052 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001637 | PD-02052020-00270 | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9864 | 839864 | 2020-02-05 12:56 | 2020-02-05 13:35 | 39 | 1 | 1 | 39 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 808 NW 189th CI | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 10663 | 3298 | 4.5257e-05 | 1.1604e-06 | 39 | 1 | 310 | Customer | 361580 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001640 | PD-02052020-00274 | SOUTHERN | DURANT | 5505:DURANT | DURANT 22 | 550522 | 2020-02-05 12:57 | 2020-02-05 14:26 | 89.25 | 1 | 1 | 89.25 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | BLUE | 3593 N Roberta Rd, Durant | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 77647 | 15498 | 1319 | 799 | 0.00010357 | 1.1604e-06 | 89.25 | 1 | 320 | Customer | 417742 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001647 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-05 13:02 | 2020-02-05 18:02 | 299.8 | 12 | 8 | 445.6 | 4 | DETERIORATION | 12 | POLE | LAMAR | ROBERTS AVE + CAZORT STR. | CMI_PLANNED | YES | NO | NO | 861739 | 82281 | 7548 | 730 | 0 | 0.00051709 | 1.3925e-05 | 37.1333 | 1 | 308 | Load | 15752 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | #N/A
J2002.001645 |  | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1422 | 911422 | 2020-02-05 13:15 | 2020-02-05 13:26 | 10.78 | 1 | 1 | 10.7833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 1101 N.45TH, 3 POLE S-N.J ST. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 82281 | 61234 | 4740 | 1954 | 1.2513e-05 | 1.1604e-06 | 10.7833 | 1 | 310 | Customer | 4056 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-05 | 2020 |  | Ark - Series 1
J2002.001644 | PD-02052020-00282 | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1621 | 581621 | 2020-02-05 13:15 | 2020-02-05 15:10 | 114.85 | 7 | 4 | 734.65 | 7 | ICE / SLEET / SNOW | 34 | CONDUCTOR SECONDARY - OH | ADA | 403 W.3 | CMI_NORMAL | NO | NO | NO | 861739 | 77647 | 11520 | 3462 | 1808 | 0.00085252 | 8.1231e-06 | 104.95 | 1 | 310 | Load | 11809 | Load | Tran1phOH | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001646 | PD-02052020-00288 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6924 | 846924 | 2020-02-05 13:17 | 2020-02-05 14:56 | 99.12 | 1 | 2 | 99.1167 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 13613 PIN-OAK | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 7727 | 1143 | 0.00011502 | 1.1604e-06 | 99.1167 | 1 | 320 | Customer | 59382 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001650 |  | SOUTHERN | SULPHUR | 5707:MILL CREEK | MILL CREEK 23 | 570723 | 2020-02-05 13:18 | 2020-02-05 14:08 | 50.37 | 2 | 2 | 100.7333 | 29 | TREES : GROW IN | 22 | FUSE - SECONDARY | MILL CREEK | MILL CRK OK | CMI_NORMAL | NO | NO | NO | 861739 | 77647 | 6817 | 211 | 192 | 0.0001169 | 2.3209e-06 | 50.3667 | 1 | 310 | Secondary | 4859 | Load | Tran1phOH | Ties | [6 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001652 |  | METRO SOUTH | SOUTH | 8728:CHERRY CREEK | CHERRY_CREEK_2831 | 872831 | 2020-02-05 13:32 | 2020-02-05 13:39 | 7.77 | 1 | 1 | 7.7667 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | CIMARRON CREEK 2 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 57018 | 7108 | 1643 | 9.0128e-06 | 1.1604e-06 | 7.7667 | 1 | 310 | Customer | 74696 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001655 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-02-05 13:42 | 2020-02-05 14:38 | 55.55 | 1 | 1 | 35.2333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | LAVACA | 300 MAIN | CMI_NORMAL | NO | NO | NO | 861739 | 82281 | 61234 | 2739 | 2127 | 4.0886e-05 | 1.1604e-06 | 35.2333 | 1 | 308 | Load | 13594 | Load | TranOpenDelta | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | Ark - Series 2
J2002.001659 |  | METRO SOUTH | SOUTH CENTRAL | 8717:TURNER | TURNER_1721 | 871721 | 2020-02-05 13:47 | 2020-02-05 13:54 | 7.37 | 1 | 1 | 7.3667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 505 SW.149 PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 102202 | 3083 | 1986 | 8.5486e-06 | 1.1604e-06 | 7.3667 | 1 | 320 | Customer | 74708 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001660 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-02-05 13:52 | 2020-02-05 14:22 | 29.67 | 12 | 6 | 282.4 | 4 | DETERIORATION | 12 | POLE | ARKOMA | 315 CECILIA | CMI_PLANNED | YES | NO | NO | 861739 | 82281 | 61234 | 2938 | 876 | 0.00032771 | 1.3925e-05 | 23.5333 | 1 | 308 | Load | 11259 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-05 | 2020 |  | Ark - Series 2
J2002.001662 |  | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-02-05 14:00 | 2020-02-05 14:06 | 5.58 | 1 | 1 | 5.5833 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | ARDMORE | LAKE MURRAY THOMPSONS BAY (HWY70/DOGWOOD RD 1S .3E | CMI_NORMAL | NO | NO | NO | 861739 | 77647 | 23595 | 2208 | 1002 | 6.4791e-06 | 1.1604e-06 | 5.5833 | 1 | 310 | Load | 238648 | Load | Tran1phPad | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001665 |  | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_724 | 510724 | 2020-02-05 14:10 | 2020-02-05 14:21 | 10.9 | 1 | 1 | 10.9 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ARDMORE | 130 G SW. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 77647 | 23595 | 4512 | 1625 | 1.2649e-05 | 1.1604e-06 | 10.9 | 1 | 310 | Customer | 11734 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | #N/A
J2002.001666 |  | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1621 | 581621 | 2020-02-05 14:13 | 2020-02-05 15:20 | 67.07 | 1 | 1 | 46.75 | 1 | CANCELLED | 57 | CANCELLED | ADA | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 0 | 0 | 0 | 0 | 5.4251e-05 | 1.1604e-06 | 46.75 | 1 | 310 | Customer |  | 0 | 0 | [6 empty] | 06/10/2020 note from burchamc. Reference J2002.001666 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001667 |  | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6523 | 836523 | 2020-02-05 14:17 | 2020-02-05 14:29 | 12.12 | 1 | 1 | 12.1167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7317 KNIGHT LAKE DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 128890 | 116115 | 7425 | 2257 | 1.4061e-05 | 1.1604e-06 | 12.1167 | 1 | 310 | Customer | 38611 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001669 | PD-02052020-00305 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-02-05 14:22 | 2020-02-05 14:58 | 36.15 | 1 | 1 | 36.15 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ARDMORE | LAKE MURRAY THOMPSONS BAY (HWY70/DOGWOOD RD 1S .3E | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 77647 | 23595 | 2208 | 1002 | 4.195e-05 | 1.1604e-06 | 36.15 | 1 | 310 | Load | 238648 | Load | Tran1phPad | GARRETT YOUNG | 580-276-6194 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001672 |  | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1621 | 581621 | 2020-02-05 14:28 | 2020-02-05 15:18 | 49.6 | 1 | 1 | 49.6 | 7 | ICE / SLEET / SNOW | 34 | CONDUCTOR SECONDARY - OH | ADA | 0 | CMI_NORMAL | NO | NO | NO | 861739 | 0 | 0 | 0 | 0 | 5.7558e-05 | 1.1604e-06 | 49.6 | 1 | 310 | Customer |  | 0 | 0 | [6 empty] | 06/10/2020 note from burchamc. Reference J2002.001672 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Manually completed blank Job Region, Job Area, etc. | Weather | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001675 |  | SOUTHERN | SULPHUR | 5707:MILL CREEK | MILL CREEK 23 | 570723 | 2020-02-05 14:31 | 2020-02-05 17:15 | 164.33 | 1 | 1 | 150.6333 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | MILL CREEK | MILL CRK OK | CMI_NORMAL | NO | NO | NO | 861739 | 77647 | 6817 | 211 | 192 | 0.0001748 | 1.1604e-06 | 150.6333 | 1 | 315 | Customer | 4859 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001678 | PD-02052020-00309 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2222 | 832222 | 2020-02-05 14:39 | 2020-02-05 15:04 | 24.87 | 1 | 1 | 24.8667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2209 NW.36 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 9178 | 1557 | 2.8856e-05 | 1.1604e-06 | 24.8667 | 1 | 310 | Customer | 18581 | Load | Tran1phOH | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001682 |  | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1621 | 581621 | 2020-02-05 15:00 | 2020-02-05 15:21 | 21.6 | 1 | 1 | 0.38333 | 7 | ICE / SLEET / SNOW | 34 | CONDUCTOR SECONDARY - OH | ADA | 828 N.OAK | CMI_NORMAL | NO | NO | NO | 861739 | 77647 | 11520 | 3462 | 1808 | 4.4484e-07 | 1.1604e-06 | 0.38333 | 1 | 310 | Customer | 3723 | Load | Tran1phOH | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001683 | PD-02052020-00318 | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4526 | 824526 | 2020-02-05 15:02 | 2020-02-05 16:47 | 104.67 | 1 | 2 | 23.9167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 3/16N NW.10 ON WS COUNTY LINE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 128890 | 116115 | 3411 | 824 | 2.7754e-05 | 1.1604e-06 | 23.9167 | 1 | 320 | Customer | 70773 | Load | Tran1phPad | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001684 |  | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3721 | 833721 | 2020-02-05 15:06 | 2020-02-05 15:12 | 5.35 | 1 | 1 | 5.35 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 332 NW.85 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 5767 | 725 | 6.2084e-06 | 1.1604e-06 | 5.35 | 1 | 310 | Customer | 28080 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001688 |  | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3721 | 833721 | 2020-02-05 15:20 | 2020-02-05 15:25 | 4.83 | 1 | 1 | 4.8333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 332 NW.85 | CMI_MOMENTARY | YES | NO | NO | 861739 | 168282 | 148455 | 5767 | 725 | 5.6088e-06 | 1.1604e-06 | 4.8333 | 1 | 320 | Customer | 28080 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001696 |  | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1523 | 811523 | 2020-02-05 15:44 | 2020-02-05 15:52 | 7.97 | 1 | 1 | 7.9667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1602 BIRCH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159220 | 102202 | 6066 | 805 | 9.2449e-06 | 1.1604e-06 | 7.9667 | 1 | 310 | Customer | 786 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001701 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7423 | 847423 | 2020-02-05 15:52 | 2020-02-05 15:58 | 6.15 | 1 | 1 | 6.15 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2118 N.KATE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 148455 | 6171 | 1295 | 7.1367e-06 | 1.1604e-06 | 6.15 | 1 | 320 | Customer | 409 | Load | TranOHDeltaSplitBank | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2022
J2002.001702 |  | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3723 | 913723 | 2020-02-05 15:58 | 2020-02-05 16:02 | 4 | 1 | 1 | 4 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 5900 KINKEAD AV 430 | CMI_MOMENTARY | YES | NO | NO | 861739 | 82281 | 61234 | 4573 | 734 | 4.6418e-06 | 1.1604e-06 | 4 | 1 | 310 | Customer | 66 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | Ark - Series 3
J2002.001704 | PD-02052020-00355 | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5822 | 845822 | 2020-02-05 16:02 | 2020-02-05 18:39 | 156.8 | 1 | 2 | 144.55 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 9601 NE.63 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 114447 | 71230 | 2985 | 935 | 0.00016774 | 1.1604e-06 | 144.55 | 1 | 310 | Load | 4392 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | #N/A
J2002.001708 |  | SOUTHERN | SULPHUR | 5707:MILL CREEK | MILL CREEK 23 | 570723 | 2020-02-05 16:14 | 2020-02-05 17:14 | 60.92 | 1 | 1 | 48.05 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | MILL CREEK | MILL CRK OK | CMI_NORMAL | NO | NO | NO | 861739 | 77647 | 6817 | 211 | 192 | 5.5759e-05 | 1.1604e-06 | 48.05 | 1 | 310 | Customer | 4859 | Load | Tran1phOH | [7 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001710 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-02-05 16:23 | 2020-02-05 18:45 | 141.57 | 2 | 2 | 279.5333 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 3735 W. HOSPITAL | CMI_PLANNED | YES | NO | NO | 861739 | 82281 | 61234 | 2739 | 2127 | 0.00032438 | 2.3209e-06 | 139.7667 | 1 | 308 | Tap | 100945 | Fuse | FuseOH | Contractor | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | Ark - Series 2
J2002.001714 | PD-02052020-00356 | ARKANSAS | POTEAU | 3505:POTEAU | POTEAU_529 | 350529 | 2020-02-05 16:28 | 2020-02-05 17:54 | 85.65 | 1 | 2 | 83.4667 | 12 | POOR CONNECTION | 50 | CONNECTOR | POTEAU | AIRPORT RD | CMI_NORMAL | NO | NO | NO | 861739 | 82281 | 13499 | 2303 | 441 | 9.6858e-05 | 1.1604e-06 | 83.4667 | 1 | 310 | Customer | 4393 | Load | Tran1phOH | JOHN MEEH | 918-413-0959 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | #N/A
J2002.001719 |  | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8123 | 838123 | 2020-02-05 16:58 | 2020-02-05 17:06 | 7.5 | 1 | 1 | 7.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 8301 N. COUNCIL, #2401 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 128890 | 116115 | 8958 | 1216 | 8.7033e-06 | 1.1604e-06 | 7.5 | 1 | 310 | Customer | 73565 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001720 |  | METRO NORTH | GUTHRIE | 8819:LIBERTY LAKE | LIBERTY_LAKE_1923 | 881923 | 2020-02-05 17:02 | 2020-02-05 17:10 | 7.93 | 1 | 1 | 7.9333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | EDMOND | 915 SUMMIT RIDGE DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 168282 | 19827 | 3354 | 1827 | 9.2062e-06 | 1.1604e-06 | 7.9333 | 1 | 310 | Customer | 342957 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001726 |  | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 21 | 570821 | 2020-02-05 17:36 | 2020-02-05 17:52 | 16.63 | 1 | 1 | 16.6333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DAVIS | N OF 7 BETWEEN GREER/LAKEWOOD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 77647 | 6817 | 1859 | 904 | 1.9302e-05 | 1.1604e-06 | 16.6333 | 1 | 310 | Customer | 21542 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | OK - 2021
J2002.001731 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3821 | 913821 | 2020-02-05 18:10 | 2020-02-05 19:56 | 105.7 | 2 | 2 | 195.9833 | 28 | OTHER (DESCRIBE) | 36 | CONDUCTOR PRIMARY - UG | FORT SMITH | RISER FOR 15513 TRAN | CMI_PLANNED | YES | NO | NO | 861739 | 82290 | 61238 | 2939 | 209 | 0.00022743 | 2.3209e-06 | 97.9917 | 1 | 308 | Mainline | 5529 | Fuse | FuseRiser | Contractor | [6 empty] | Other | N | DISTRIBUTION | 161kV | 2020-02-05 | 2020 |  | Ark - Series 2
J2002.001735 | PD-02052020-00378 | SOUTHERN | SULPHUR | 5706:LAKE ARBUCKLE | LAKE ARBUCKLE 46 | 570646 | 2020-02-05 18:29 | 2020-02-05 19:34 | 64.9 | 1 | 1 | 64.9 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SULPHUR | CABIN 1 AREA (GODDARD CAMP) | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 77671 | 6817 | 366 | 239 | 7.5313e-05 | 1.1604e-06 | 64.9 | 1 | 310 | Load | 13576 | Load | Tran1phOH | CHAD A DOTSON | 405-488-5658 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | #N/A
J2002.001740 | PD-02052020-00380 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1226 | 831226 | 2020-02-05 19:03 | 2020-02-05 19:52 | 49.18 | 49 | 49 | 7936.3667 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | NW.49 + MILITARY | CMI_NORMAL | NO | NO | NO | 861739 | 168299 | 148466 | 7754 | 1748 | 0.0092097 | 5.6862e-05 | 161.9667 | 1 | 310 | Tap | 26403 | Fuse | FuseOH | CORY J HUFFMAN | 870-668-0377 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | OK - 2021
J2002.001756 | PD-02052020-00392 | METRO EAST | SEMINOLE | 7505:WEWOKA | WEWOKA 21 | 750521 | 2020-02-05 20:54 | 2020-02-05 22:02 | 68.48 | 1 | 1 | 68.4833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | WEWOKA | 11/4MW BUTNER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 114473 | 13622 | 2477 | 1284 | 7.9471e-05 | 1.1604e-06 | 68.4833 | 1 | 310 | Load | 10676 | Load | Tran1phOH | BRADY A HUFF | 405-519-0701 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-05 | 2020 |  | OK - 2021
J2002.001766 | PD-02052020-00395 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7023 | 817023 | 2020-02-05 21:53 | 2020-02-06 08:40 | 647 | 1 | 1 | 646.9895 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | OG+E SERVICE CENTER S. HIGH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861739 | 159243 | 102215 | 9938 | 646 | 0.0007508 | 1.1604e-06 | 646.9895 | 1 | 320 | Load | 64568 | Load | Tran3phPadWye | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-05 | 2020 |  | #N/A
J2002.001800 | PD-02062020-00013 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1524 | 811524 | 2020-02-06 03:28 | 2020-02-06 08:02 | 274.47 | 13 | 16 | 3535.025 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 1336 SW.30 | CMI_NORMAL | NO | NO | NO | 861739 | 159243 | 102215 | 6068 | 2071 | 0.0041022 | 1.5086e-05 | 271.925 | 1 | 310 | Load | 6527 | Load | Tran1phOH | CHAD W GLEAVE | 405-250-7464 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | OK - 2022
J2002.001816 |  | SOUTHERN | HEALDTON | 5321:WILDHORSE | WILDHORSE_2122 | 532122 | 2020-02-06 05:51 | 2020-02-06 05:51 | 0.37 | 35 | 0 | 12.8333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | 0 | 0 | CMI_MOMENTARY | YES | NO | NO | 861794 | 77671 | 6804 | 155 | 35 | 1.4891e-05 | 4.0613e-05 | 0.36667 | 1 | 0 | Feeder | WILDHORSE_2122 | Breaker | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-06 | 2020 |  | #N/A
J2002.001822 | PD-02062020-00021 | METRO WEST | WEST | 8158:SARA | SARA_5871 | 815871 | 2020-02-06 06:56 | 2020-02-06 08:40 | 103.68 | 1 | 1 | 98.0194 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | SW 29th Terr and E of Fennel Rd | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 128932 | 116151 | 18275 | 5409 | 0.00011374 | 1.1604e-06 | 98.0194 | 1 | 320 | Customer | 243964 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | OK - 2022
J2002.001825 | PD-02062020-00023 | METRO NORTH | GUTHRIE | 8807:CRESCENT | CRESCENT_721 | 880721 | 2020-02-06 07:11 | 2020-02-06 10:28 | 197.17 | 1 | 1 | 193.05 | 4 | DETERIORATION | 2 | TRANSFORMER OH | CRESCENT | 2BE 74HY-1BS VANBUREN-CRESCENT | CMI_NORMAL | NO | NO | NO | 861794 | 168299 | 19833 | 1766 | 873 | 0.00022401 | 1.1604e-06 | 193.05 | 1 | 310 | Customer | 57647 | Load | Tran1phOH | BRIAN E WHITE | 405-642-7075 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001827 | PD-02062020-00026 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7423 | 847423 | 2020-02-06 07:19 | 2020-02-06 08:22 | 62.62 | 1 | 1 | 30.7095 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1425 NE.22 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 168299 | 148466 | 6171 | 1295 | 3.5634e-05 | 1.1604e-06 | 30.7095 | 1 | 310 | Customer | 368 | Load | TranOH3phDelta | REX R WILSON | 405-535-4507 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | OK - 2022
J2002.001834 | PD-02062020-00034 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-02-06 08:05 | 2020-02-06 09:19 | 73.55 | 1 | 1 | 35.1052 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4600 NW.19 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 168299 | 148466 | 9250 | 1940 | 4.0735e-05 | 1.1604e-06 | 35.1052 | 1 | 310 | Customer | 24599 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | OK - 2021
J2002.001836 | PD-02062020-00048 | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_924 | 910924 | 2020-02-06 08:10 | 2020-02-06 10:04 | 114.42 | 1 | 1 | 114.4167 | 12 | POOR CONNECTION | 50 | CONNECTOR | FORT SMITH | 1400 S.BOSTON | CMI_NORMAL | NO | NO | NO | 861794 | 82290 | 61238 | 5015 | 1724 | 0.00013277 | 1.1604e-06 | 114.4167 | 1 | 320 | Load | 13498 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | Ark - Series 3
J2002.001837 | PD-02062020-00035 | METRO EAST | SHAWNEE | 7411:DALE | DALE_1129 | 741129 | 2020-02-06 08:13 | 2020-02-06 09:34 | 80.87 | 1 | 1 | 72.9167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MCLOUD | 3MS 3MW OF MCLOUD SUB | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 114473 | 22129 | 972 | 971 | 8.461e-05 | 1.1604e-06 | 72.9167 | 1 | 310 | Customer | 19062 | Load | Tran1phOH | BRYAN K TATUM | 405-659-0746 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | OK - 2021
J2002.001838 | PD-02062020-00047 | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_822 | 870822 | 2020-02-06 08:22 | 2020-02-06 09:24 | 61.58 | 1 | 1 | 61.5833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 2632 Classen Blvd. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 159243 | 57028 | 6776 | 1805 | 7.1459e-05 | 1.1604e-06 | 61.5833 | 1 | 310 | Customer | 377830 | Load | Tran3phWye | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001840 | PD-02062020-00053 | SOUTHERN | PAULS VALLEY | 5611:MAYSVILLE | MAYSVILLE 22 | 561122 | 2020-02-06 08:30 | 2020-02-06 08:40 | 10.38 | 1 | 1 | 10.3833 | 23 | CUSTOMER EQUIPMENT | 31 | CONDUCTOR SERVICE - OH | MAYSVILLE | N EDGE OF MAYSVL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 77671 | 6220 | 946 | 452 | 1.2049e-05 | 1.1604e-06 | 10.3833 | 1 | 310 | Customer | 13965 | Load | Tran1phOH | BRUCE E BEAM | 405-626-0490 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | OK - 2021
J2002.001841 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-06 08:30 | 2020-02-06 13:23 | 292.42 | 1 | 1 | 118.5667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | LAMAR | HWY 64+JOHNSONVILLE LAMAR | CMI_PLANNED | YES | NO | NO | 861794 | 82290 | 7551 | 730 | 0 | 0.00013758 | 1.1604e-06 | 118.5667 | 1 | 308 | Load | 15812 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | #N/A
J2002.001844 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-06 08:38 | 2020-02-06 15:33 | 414.97 | 1 | 1 | 394.7667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | LAMAR | 1/2M N HWY 64 ON SEMINARY ST | CMI_PLANNED | YES | NO | NO | 861794 | 82290 | 7551 | 730 | 0 | 0.00045808 | 1.1604e-06 | 394.7667 | 1 | 308 | Load | 15940 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | #N/A
J2002.001848 | PD-02062020-00062 | NORTHEAST | SAPULPA | 7611:MORRISON TAP | MORRISON_TAP_1121 | 761121 | 2020-02-06 08:48 | 2020-02-06 10:43 | 115.13 | 1 | 1 | 115.1333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MORRISON | 848 MARY ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 74117 | 40805 | 895 | 466 | 0.0001336 | 1.1604e-06 | 115.1333 | 1 | 310 | Customer | 45621 | Load | Tran1phOH | BRAD WRIGHT | 918-629-1747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001850 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-06 08:52 | 2020-02-06 11:22 | 149.15 | 2 | 1 | 276.5 | 4 | DETERIORATION | 12 | POLE | POCOLA | LOT 7 WYNNWOOD | CMI_PLANNED | YES | NO | NO | 861794 | 82290 | 61238 | 1458 | 1240 | 0.00032084 | 2.3207e-06 | 138.25 | 1 | 308 | Load | 13749 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | Ark - Series 2
J2002.001852 | PD-02062020-00067 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-02-06 09:01 | 2020-02-06 10:10 | 69.45 | 1 | 1 | 69.45 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ARDMORE | 10 RANCH-ACRES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 77671 | 23604 | 2210 | 1003 | 8.0588e-05 | 1.1604e-06 | 69.45 | 1 | 310 | Customer | 17399 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001853 | PD-02062020-00069 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1521 | 811521 | 2020-02-06 09:02 | 2020-02-06 10:11 | 68.53 | 1 | 1 | 68.5333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1432 SW.11 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 159243 | 102215 | 6068 | 1247 | 7.9524e-05 | 1.1604e-06 | 68.5333 | 1 | 310 | Customer | 4186 | Load | Tran1phOH | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | OK - 2022
J2002.001854 | PD-02062020-00068 | METRO NORTH | GUTHRIE | 8819:LIBERTY LAKE | LIBERTY_LAKE_1921 | 881921 | 2020-02-06 09:09 | 2020-02-06 11:57 | 168.13 | 1 | 1 | 163.85 | 22 | WIND | 17 | JUMPER | GUTHRIE | L6B4 1000 OAKS | CMI_NORMAL | NO | NO | NO | 861794 | 168299 | 19833 | 3354 | 1527 | 0.00019013 | 1.1604e-06 | 163.85 | 1 | 310 | Customer | 61512 | Load | Tran1phOH | JOSEPH WAYNE POOL | 405-919-2253 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001857 | PD-02062020-00078 | NORTHWEST | ENID | 4220:CLYDE | CLYDE 21 | 422021 | 2020-02-06 09:11 | 2020-02-06 09:30 | 19.47 | 1 | 1 | 19.4667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | WAKITA | 2.5S1.5W CLYDE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 53575 | 37620 | 415 | 42 | 2.2589e-05 | 1.1604e-06 | 19.4667 | 1 | 320 | Customer | 2302 | Load | Tran1phOH | PATRICK LYONS | 580-395-4171 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | #N/A
J2002.001856 |  | ARKANSAS | FORT SMITH | 9512:ADABELL ROAD | ADABELL_ROAD_1222 | 951222 | 2020-02-06 09:12 | 2020-02-06 13:04 | 232.72 | 4 | 5 | 770.0397 | 4 | DETERIORATION | 1 | TRANSFORMER UG | VAN BUREN | 606 SPRUCE | CMI_PLANNED | YES | NO | NO | 861794 | 82290 | 61238 | 3123 | 1088 | 0.00089353 | 4.6415e-06 | 192.5099 | 1 | 310 | Load | 11932 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-06 | 2020 |  | Ark - Series 1, Ark - Series 2
J2002.001861 |  | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_924 | 910924 | 2020-02-06 09:15 | 2020-02-06 09:31 | 15.92 | 1 | 1 | 15.9167 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 1624 SOUTH FRESNO STREET | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 82290 | 61238 | 5015 | 1724 | 1.8469e-05 | 1.1604e-06 | 15.9167 | 1 | 310 | Customer | 15493 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | Ark - Series 3
J2002.001859 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4031 | 834031 | 2020-02-06 09:16 | 2020-02-06 13:21 | 245.77 | 3 | 2 | 171.9 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 9604 N.HORSESHOE RD | CMI_PLANNED | YES | NO | NO | 861794 | 128932 | 116151 | 10845 | 1642 | 0.00019947 | 3.4811e-06 | 57.3 | 1 | 310 | Load | 9600 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001860 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-02-06 09:16 | 2020-02-06 11:29 | 132.9 | 1 | 1 | 8.2507 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1104 N.GLADE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 128932 | 116151 | 3411 | 2041 | 9.5739e-06 | 1.1604e-06 | 8.2507 | 1 | 310 | Customer | 41109 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001864 |  | ARKANSAS | FORT SMITH | 9508:WHITESIDE | WHITESIDE_822 | 950822 | 2020-02-06 09:23 | 2020-02-06 10:15 | 52.77 | 6 | 6 | 291.6 | 4 | DETERIORATION | 28 | CROSSARM | VAN BUREN | 312 VINE | CMI_PLANNED | YES | NO | NO | 861794 | 82290 | 61238 | 1920 | 210 | 0.00033836 | 6.9622e-06 | 48.6 | 1 | 308 | Load | 12412 | Load | TranOpenDelta | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-06 | 2020 |  | Ark - Series 2
J2002.001867 | PD-02062020-00086 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_631 | 870631 | 2020-02-06 09:28 | 2020-02-06 09:56 | 27.88 | 1 | 1 | 27.8833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 1911 CHRY-STONE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 159243 | 57028 | 7374 | 1263 | 3.2355e-05 | 1.1604e-06 | 27.8833 | 1 | 320 | Customer | 33982 | Load | Tran1phOH | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001875 |  | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3721 | 833721 | 2020-02-06 09:30 | 2020-02-06 13:23 | 233.02 | 7 | 11 | 258.7667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 235 W.WILSHIRE | CMI_PLANNED | YES | NO | NO | 861794 | 168299 | 148466 | 5767 | 725 | 0.00030027 | 8.1226e-06 | 36.9667 | 1 | 310 | Load | 24956 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | OK - 2022
J2002.001866 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-02-06 09:30 | 2020-02-06 14:06 | 275.92 | 4 | 3 | 1099.0667 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 3401 STATELINE RD | CMI_PLANNED | YES | NO | NO | 861794 | 82290 | 61238 | 2939 | 877 | 0.0012753 | 4.6415e-06 | 274.7667 | 1 | 308 | Load | 8121 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-06 | 2020 |  | Ark - Series 2
J2002.001869 | PD-02062020-00090 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6331 | 816331 | 2020-02-06 09:31 | 2020-02-06 10:26 | 54.57 | 1 | 1 | 54.5667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MOORE | 769 SW 19TH ST, BLDG 20 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 159243 | 102215 | 11843 | 1367 | 6.3318e-05 | 1.1604e-06 | 54.5667 | 1 | 310 | Customer | 366078 | Load | Tran1phPad | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001870 | PD-02062020-00092 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6522 | 836522 | 2020-02-06 09:32 | 2020-02-06 10:14 | 41.67 | 1 | 1 | 20.3989 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6432 W.WILSHIRE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 128932 | 116151 | 7425 | 1863 | 2.367e-05 | 1.1604e-06 | 20.3989 | 1 | 310 | Customer | 42146 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | OK - 2021
J2002.001877 | PD-02062020-00112 | METRO EAST | EAST | 8411:ACORN | ACORN_1172 | 841172 | 2020-02-06 09:43 | 2020-02-06 10:53 | 69.83 | 1 | 1 | 69.8333 | 7 | ICE / SLEET / SNOW | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | .5MSNE122 WS COLTRAN | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861794 | 114473 | 71243 | 1796 | 704 | 8.1033e-05 | 1.1604e-06 | 69.8333 | 1 | 320 | Customer | 37795 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001880 |  | METRO NORTH | NORTH | 8209:CLASSEN | CLASSEN_923 | 820923 | 2020-02-06 09:46 | 2020-02-06 13:22 | 216.2 | 1 | 1 | 216.2 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 1312 NW.11 | CMI_PLANNED | YES | NO | NO | 861794 | 168299 | 148466 | 3889 | 1150 | 0.00025087 | 1.1604e-06 | 216.2 | 1 | 310 | Customer | 16324 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001883 | PD-02062020-00111 | METRO EAST | EAST | 8618:BARNES | BARNES_1821 | 861821 | 2020-02-06 09:51 | 2020-02-06 10:45 | 53.57 | 4 | 4 | 178.1667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 3/8 MW ANDERSON,N SE 59 | CMI_NORMAL | NO | NO | NO | 861794 | 114473 | 71243 | 953 | 533 | 0.00020674 | 4.6415e-06 | 44.5417 | 1 | 310 | Load | 72387 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001885 | PD-02062020-00122 | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1224 | 911224 | 2020-02-06 10:00 | 2020-02-06 11:22 | 82 | 1 | 1 | 82 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | BTWN ALBAMA + HARDIE-SO OF MAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 82290 | 61238 | 6605 | 1803 | 9.515e-05 | 1.1604e-06 | 82 | 1 | 320 | Customer | 14394 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | Ark - Series 1
J2002.001886 | PD-02062020-00118 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-02-06 10:08 | 2020-02-06 13:01 | 173.03 | 1 | 1 | 169.8833 | 12 | POOR CONNECTION | 50 | CONNECTOR | DEL CITY | 4608 SE.19 | CMI_NORMAL | NO | NO | NO | 861794 | 159243 | 102215 | 7422 | 2240 | 0.00019713 | 1.1604e-06 | 169.8833 | 1 | 320 | Customer | 22075 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | OK - 2022
J2002.001890 |  | ARKANSAS | FORT SMITH | 9512:ADABELL ROAD | ADABELL_ROAD_1222 | 951222 | 2020-02-06 10:14 | 2020-02-06 13:06 | 171.88 | 9 | 9 | 268.35 | 4 | DETERIORATION | 1 | TRANSFORMER UG | VAN BUREN | E OF HWY 59 ON POINTER TRAIL | CMI_PLANNED | YES | NO | NO | 861794 | 82290 | 61238 | 3123 | 1088 | 0.00031139 | 1.0443e-05 | 29.8167 | 1 | 310 | Load | 15911 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-06 | 2020 |  | Ark - Series 1, Ark - Series 2
J2002.001899 |  | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1122 | 511122 | 2020-02-06 10:33 | 2020-02-06 21:03 | 630.23 | 1 | 1 | 280.6333 | 4 | DETERIORATION | 1 | TRANSFORMER UG | DICKSON | 165 RIVER BOTTOM RD. | CMI_PLANNED | YES | NO | NO | 861794 | 77671 | 23604 | 2210 | 1207 | 0.00032564 | 1.1604e-06 | 280.6333 | 1 | 308 | Load | 377137 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001902 |  | ARKANSAS | FORT SMITH | 9512:ADABELL ROAD | ADABELL_ROAD_1222 | 951222 | 2020-02-06 10:37 | 2020-02-06 11:03 | 25.53 | 1 | 1 | 6.9667 | 4 | DETERIORATION | 1 | TRANSFORMER UG | VAN BUREN | 807 CARTWRIGHT | CMI_PLANNED | YES | NO | NO | 861794 | 82290 | 61238 | 3123 | 1088 | 8.0839e-06 | 1.1604e-06 | 6.9667 | 1 | 310 | Customer | 10298 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-06 | 2020 |  | Ark - Series 1, Ark - Series 2
J2002.001903 | PD-02062020-00138 | METRO WEST | WEST | 8323:RICHARDS | RICHARDS_2321 | 832321 | 2020-02-06 10:38 | 2020-02-06 14:56 | 258.28 | 2 | 2 | 488.8 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 8916 NW 115TH STREET | CMI_NORMAL | NO | NO | NO | 861794 | 128932 | 116151 | 5020 | 1409 | 0.00056719 | 2.3207e-06 | 244.4 | 1 | 310 | Secondary | 87400 | Load | Tran1phOH | BEAU S HUDSON | 405-306-8284 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001907 |  | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3722 | 833722 | 2020-02-06 10:40 | 2020-02-06 13:25 | 165.42 | 6 | 8 | 249.35 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 8614 GLENWOOD AV | CMI_PLANNED | YES | NO | NO | 861794 | 168299 | 148466 | 5767 | 1110 | 0.00028934 | 6.9622e-06 | 41.5583 | 1 | 310 | Load | 5826 | Load | TranOHDeltaSplitBank | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | OK - 2022
J2002.001905 |  | SOUTHERN | SULPHUR | 5709:PRICES FALLS | PRICES_FALLS_923 | 570923 | 2020-02-06 10:44 | 2020-02-06 10:44 | 0.03 | 183 | 0 | 6.1 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | DAVIS | 5175 KAY STARR TRAIL | CMI_MOMENTARY | YES | NO | NO | 861794 | 77671 | 6817 | 373 | 183 | 7.0783e-06 | 0.00021235 | 0.033333 | 1 | 0 | Feeder | PRICES_FALLS_923 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001909 |  | METRO SOUTH | SOUTH | 8728:CHERRY CREEK | CHERRY_CREEK_2823 | 872823 | 2020-02-06 10:51 | 2020-02-06 10:57 | 6.25 | 1 | 1 | 6.25 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | W.S. I-35 1/2 M N OF ROBINSON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 159243 | 57028 | 7109 | 1302 | 7.2523e-06 | 1.1604e-06 | 6.25 | 1 | 310 | Customer | 78114 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001908 |  | ARKANSAS | FORT SMITH | 9508:WHITESIDE | WHITESIDE_821 | 950821 | 2020-02-06 10:51 | 2020-02-06 13:20 | 149.53 | 4 | 3 | 585 | 4 | DETERIORATION | 12 | POLE | VAN BUREN | 201 S.25 | CMI_PLANNED | YES | NO | NO | 861794 | 82290 | 61238 | 1920 | 1281 | 0.00067882 | 4.6415e-06 | 146.25 | 1 | 310 | Load | 10720 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-06 | 2020 |  | Ark - Series 2
J2002.001911 | PD-02062020-00146 | METRO WEST | WEST | 8222:CZECH HALL | CZECH_HALL_2223 | 822223 | 2020-02-06 10:52 | 2020-02-06 11:16 | 23.7 | 1 | 1 | 7.426 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | YUKON | 204 REDBUD AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 128932 | 116151 | 8612 | 1176 | 8.6169e-06 | 1.1604e-06 | 7.426 | 1 | 310 | Customer | 47534 | Load | Tran1phPad | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001916 |  | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_521 | 530521 | 2020-02-06 11:03 | 2020-02-06 13:41 | 157.63 | 1 | 0 | 157.6447 | 4 | DETERIORATION | 2 | TRANSFORMER OH | HEALDTON | 40 FRANCES | CMI_PLANNED | YES | NO | NO | 861794 | 77671 | 6804 | 2129 | 1261 | 0.00018293 | 1.1604e-06 | 157.6447 | 1 | 0 | Load | 18800 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | OK - 2020
J2002.001917 |  | SOUTHERN | DURANT | 5504:BUTTERFIELD | BUTTERFIELD_429 | 550429 | 2020-02-06 11:03 | 2020-02-06 11:14 | 10.32 | 1 | 1 | 10.3167 | 1 | CANCELLED | 57 | CANCELLED | DURANT | 1330 N.5 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 77671 | 15505 | 3488 | 1274 | 1.1971e-05 | 1.1604e-06 | 10.3167 | 1 | 310 | Customer | 11492 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001918 |  | NORTHWEST | ENID | 4109:WAUKOMIS | WAUKOMIS 24 | 410924 | 2020-02-06 11:04 | 2020-02-06 13:54 | 170.37 | 1 | 1 | 152.2167 | 4 | DETERIORATION | 12 | POLE | DRUMMOND | 1E,1/2S-HWY 132,WAUKOMIS BLKTP | CMI_PLANNED | YES | NO | NO | 861794 | 53575 | 37620 | 1558 | 523 | 0.00017663 | 1.1604e-06 | 152.2167 | 1 | 308 | Load | 1071 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001927 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6324 | 816324 | 2020-02-06 11:31 | 2020-02-06 11:34 | 2.7 | 1 | 1 | 2.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MOORE | 806 NW.12 | CMI_MOMENTARY | YES | NO | NO | 861794 | 159243 | 102215 | 11843 | 2049 | 3.133e-06 | 1.1604e-06 | 2.7 | 1 | 310 | Customer | 48395 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | OK - 2021
J2002.001929 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-02-06 11:34 | 2020-02-06 12:26 | 51.33 | 2 | 2 | 98.6333 | 4 | DETERIORATION | 12 | POLE | ARKOMA | 705 OKLAHOMA | CMI_PLANNED | YES | NO | NO | 861794 | 82290 | 61238 | 2939 | 877 | 0.00011445 | 2.3207e-06 | 49.3167 | 1 | 308 | Load | 512 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-06 | 2020 |  | Ark - Series 2
J2002.001930 | PD-02062020-00177 | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5629 | 865629 | 2020-02-06 11:39 | 2020-02-06 14:59 | 200.17 | 1 | 1 | 200.1667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | VALLEY BROOK | 6212 ANDERSON DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 159243 | 102215 | 2761 | 736 | 0.00023227 | 1.1604e-06 | 200.1667 | 1 | 310 | Customer | 12152 | Load | Tran1phOH | GERARDO D SOTO | 405-758-6334 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001932 |  | METRO EAST | EAST | 8618:BARNES | BARNES_1822 | 861822 | 2020-02-06 11:45 | 2020-02-06 15:02 | 197.62 | 2 | 2 | 96.8833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 9317 SE 36TH | CMI_PLANNED | YES | NO | NO | 861794 | 114473 | 71243 | 953 | 420 | 0.00011242 | 2.3207e-06 | 48.4417 | 1 | 308 | Load | 32563 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001934 | PD-02062020-00182 | SOUTHERN | ARDMORE | 5108:WOLF CREEK | WOLF CREEK 22 | 510822 | 2020-02-06 11:46 | 2020-02-06 12:56 | 70.37 | 1 | 1 | 67.95 | 13 | PREMATURE FAILURE | 23 | FUSE - PRIMARY | LONE GROVE | .1 MS HWY 70 WS CHEEK RD | CMI_NORMAL | NO | NO | NO | 861794 | 77671 | 23604 | 449 | 237 | 7.8847e-05 | 1.1604e-06 | 67.95 | 1 | 310 | Customer | 27020 | Load | Tran1phOH | RANDAL G CALLAWAY | 580-220-8449 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001936 | PD-02062020-00183 | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1722 | 861722 | 2020-02-06 11:51 | 2020-02-06 13:17 | 85.82 | 1 | 1 | 72.8167 | 7 | ICE / SLEET / SNOW | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 4212 SE.46 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861794 | 114473 | 71243 | 6952 | 1788 | 8.4494e-05 | 1.1604e-06 | 72.8167 | 1 | 311 | Customer | 4780 | Load | Tran1phOH | GERARDO D SOTO | 405-758-6334 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | #N/A
J2002.001937 | PD-02062020-00189 | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8131 | 838131 | 2020-02-06 11:52 | 2020-02-06 13:33 | 101.25 | 1 | 1 | 11.7985 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7506 KNIGHTLAKE DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 128932 | 116151 | 8961 | 1832 | 1.3691e-05 | 1.1604e-06 | 11.7985 | 1 | 310 | Customer | 42803 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.002034 | PD-02062020-00185 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7022 | 817022 | 2020-02-06 11:52 | 2020-02-06 16:58 | 306.17 | 12 | 5 | 3508.4 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | MOORE | 608 NW.20 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861794 | 159243 | 102215 | 9938 | 2104 | 0.004071 | 1.3924e-05 | 292.3667 | 1 | 310 | Load | 48117 | Load | Tran1phPad | CAMERON L ALLEN | 405-517-2208 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001940 | PD-02062020-00187 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2627 | 862627 | 2020-02-06 11:56 | 2020-02-06 14:49 | 172.62 | 1 | 1 | 169.4833 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 5412 EVANBROOK TR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861794 | 159243 | 102215 | 7422 | 2004 | 0.00019666 | 1.1604e-06 | 169.4833 | 1 | 320 | Customer | 56596 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001948 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-02-06 12:10 | 2020-02-06 14:51 | 160.87 | 4 | 5 | 755.3333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | BIXBY | 20 E.DAWES BIXBY, OK | CMI_PLANNED | YES | NO | NO | 861794 | 74117 | 40805 | 2755 | 1443 | 0.00087647 | 4.6415e-06 | 188.8333 | 1 | 310 | Secondary | 41875 | Load | Tran3phWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | OK - 2021
J2002.001947 | PD-02062020-00267 | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1729 | 831729 | 2020-02-06 12:26 | 2020-02-06 14:14 | 108.32 | 1 | 1 | 108.3167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 13301 PLAZA TERR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 168299 | 148466 | 6648 | 649 | 0.00012569 | 1.1604e-06 | 108.3167 | 1 | 310 | Customer | 69572 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001949 |  | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6223 | 866223 | 2020-02-06 12:27 | 2020-02-06 13:43 | 76.08 | 1 | 1 | 66.55 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 1/4MS SE29 1/4W AND | CMI_PLANNED | YES | NO | NO | 861794 | 114473 | 71243 | 7214 | 2237 | 7.7223e-05 | 1.1604e-06 | 66.55 | 1 | 308 | Load | 26957 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001955 | PD-02062020-00222 | ARKANSAS | FORT SMITH | 9104:J STREET | J_STREET_431 | 910431 | 2020-02-06 12:40 | 2020-02-06 14:42 | 122.33 | 1 | 1 | 122.3333 | 11 | OVERLOAD | 21 | FUSE - TRANSFORMER | FORT SMITH | 1105 BALLMAN RD | CMI_NORMAL | NO | NO | NO | 861794 | 82290 | 61238 | 1999 | 836 | 0.00014195 | 1.1604e-06 | 122.3333 | 1 | 320 | Customer | 216000 | Load | Tran3phWye | ANTHONY SELF | 479-719-0734 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-06 | 2020 |  | Ark - Series 2
J2002.001957 | PD-02062020-00234 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1922 | 851922 | 2020-02-06 12:49 | 2020-02-06 13:16 | 27.08 | 1 | 1 | 27.0833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 7849 NE.10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 114473 | 71243 | 12464 | 1794 | 3.1427e-05 | 1.1604e-06 | 27.0833 | 1 | 310 | Customer | 51027 | Load | Tran1phPad | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001958 | PD-02062020-00235 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3022 | 743022 | 2020-02-06 12:51 | 2020-02-06 13:41 | 50.45 | 1 | 1 | 50.45 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SHAWNEE | 301 N.KENNEDY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 114473 | 22129 | 6651 | 2171 | 5.8541e-05 | 1.1604e-06 | 50.45 | 1 | 321 | Load | 12756 | Load | Tran3phPadWye | BRYAN K TATUM | 405-659-0746 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | OK - 2020
J2002.001961 | PD-02062020-00246 | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_624 | 410624 | 2020-02-06 12:57 | 2020-02-06 13:31 | 33.75 | 1 | 1 | 33.75 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ENID | 426 W.VINE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 53575 | 37620 | 6023 | 1861 | 3.9162e-05 | 1.1604e-06 | 33.75 | 1 | 310 | Customer | 3064 | Load | Tran1phOH | WILLIAM R PETHICK | 580-278-8129 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | #N/A
J2002.001960 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-02-06 12:58 | 2020-02-06 15:51 | 173.53 | 3 | 1 | 507.25 | 4 | DETERIORATION | 2 | TRANSFORMER OH | LAVACA | RIVER RD. N.-HWY. 96 | CMI_PLANNED | YES | NO | NO | 861794 | 82290 | 61238 | 2739 | 2127 | 0.0005886 | 3.4811e-06 | 169.0833 | 1 | 308 | Tap | 2699 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | Ark - Series 2
J2002.001963 |  | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_661 | 550661 | 2020-02-06 13:02 | 2020-02-06 17:09 | 246.55 | 6 | 1 | 1455.05 | 4 | DETERIORATION | 12 | POLE | DURANT | SW4 SEC4 6S 9E SHROYER MH PARK | CMI_PLANNED | YES | NO | NO | 861794 | 77671 | 15505 | 6741 | 447 | 0.0016884 | 6.9622e-06 | 242.5083 | 1 | 308 | Load | 23676 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001964 | PD-02062020-00245 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6121 | 836121 | 2020-02-06 13:06 | 2020-02-06 13:20 | 14.45 | 1 | 1 | 6.9869 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 909 NW.33 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 168299 | 148466 | 11121 | 1638 | 8.1074e-06 | 1.1604e-06 | 6.9869 | 1 | 310 | Customer | 13361 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | OK - 2021
J2002.001968 |  | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_631 | 870631 | 2020-02-06 13:08 | 2020-02-06 13:15 | 6.57 | 1 | 1 | 6.5667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 1911 CHRY-STONE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 159243 | 57028 | 7374 | 1263 | 7.6198e-06 | 1.1604e-06 | 6.5667 | 1 | 310 | Customer | 33982 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001973 |  | NORTHWEST | ENID | 4414:HENNESSEY | HENNESSEY_1423 | 441423 | 2020-02-06 13:14 | 2020-02-06 15:11 | 116.53 | 1 | 1 | 93.6333 | 3 | DAMAGED BY PUBLIC | 12 | POLE | HENNESSEY | HWY 51 & COLONY HOUSE 4ME 3MN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 53575 | 37620 | 1953 | 286 | 0.00010865 | 1.1604e-06 | 93.6333 | 1 | 308 | Tap | 251433 | Fuse | FuseOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001974 |  | NORTHWEST | ENID | 4414:HENNESSEY | HENNESSEY_1423 | 441423 | 2020-02-06 13:17 | 2020-02-06 15:10 | 112.9 | 1 | 1 | 88.6833 | 3 | DAMAGED BY PUBLIC | 12 | POLE | HENNESSEY | 2.5S 41/4E BISON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 53575 | 37620 | 1953 | 286 | 0.00010291 | 1.1604e-06 | 88.6833 | 1 | 308 | Load | 2027 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001980 | PD-02062020-00265 | METRO EAST | SEMINOLE | 7505:WEWOKA | WEWOKA 21 | 750521 | 2020-02-06 13:36 | 2020-02-06 19:46 | 369.93 | 1 | 1 | 7.0833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | WEWOKA | SW NW SW 12 8 7 | CMI_NORMAL | NO | NO | NO | 861794 | 114473 | 13622 | 2477 | 1284 | 8.2193e-06 | 1.1604e-06 | 7.0833 | 1 | 310 | Load | 9162 | Load | Tran3phWye | DAVID M CLEMMONS | 405-777-8355 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | OK - 2021
J2002.001979 |  | METRO EAST | EAST | 8542:RENO | RENO_4229 | 854229 | 2020-02-06 13:37 | 2020-02-06 13:44 | 6.18 | 1 | 1 | 6.1833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DEL CITY | 4625 TINKER EX | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 114473 | 71243 | 5214 | 1345 | 7.175e-06 | 1.1604e-06 | 6.1833 | 1 | 310 | Customer | 40583 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | OK - 2022
J2002.001978 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3831 | 913831 | 2020-02-06 13:38 | 2020-02-06 15:54 | 135.63 | 42 | 46 | 3699.5 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | FORT SMITH | JACKSON W.-S. 17 | CMI_PLANNED | YES | NO | NO | 861794 | 82290 | 61238 | 2939 | 485 | 0.0042928 | 4.8736e-05 | 88.0833 | 1 | 310 | Mainline | 2584 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-06 | 2020 |  | Ark - Series 2
J2002.001982 |  | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1421 | 911421 | 2020-02-06 13:46 | 2020-02-06 13:55 | 9.87 | 1 | 1 | 9.8667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 3222 JOHNSON, 3 POLE E-N.32ND | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 82290 | 61238 | 4741 | 1751 | 1.1449e-05 | 1.1604e-06 | 9.8667 | 1 | 310 | Customer | 3791 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-06 | 2020 |  | Ark - Series 1
J2002.001990 | PD-02062020-00295 | NORTHEAST | SAPULPA | 7604:PAYNE | PAYNE 51 | 760451 | 2020-02-06 14:00 | 2020-02-06 15:03 | 63.33 | 1 | 1 | 63.3333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | RIPLEY | RIPLEY OK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 74117 | 40805 | 365 | 365 | 7.349e-05 | 1.1604e-06 | 63.3333 | 1 | 310 | Customer | 45270 | Load | Tran1phOH | NICHOLAS MANION | 918-290-1327 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.001995 |  | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1423 | 311423 | 2020-02-06 14:10 | 2020-02-06 15:26 | 75.33 | 9 | 5 | 442.65 | 4 | DETERIORATION | 1 | TRANSFORMER UG | MUSKOGEE | 0 | CMI_PLANNED | YES | NO | NO | 861794 | 74117 | 33312 | 4574 | 1499 | 0.00051364 | 1.0443e-05 | 49.1833 | 1 | 308 | Mainline | 11485-2 | Switch | SwitchDefault | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | OK - 2020
J2002.001997 | PD-02062020-00305 | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6221 | 866221 | 2020-02-06 14:20 | 2020-02-06 15:18 | 58.12 | 1 | 1 | 58.1167 | 1 | CANCELLED | 57 | CANCELLED | MIDWEST CITY | 9113 STONEGATE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 114473 | 71243 | 7214 | 1294 | 6.7437e-05 | 1.1604e-06 | 58.1167 | 1 | 310 | Customer | 68666 | Load | Tran1phPad | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.002000 | PD-02062020-00307 | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_724 | 510724 | 2020-02-06 14:25 | 2020-02-06 15:09 | 44.33 | 1 | 1 | 44.3333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ARDMORE | 802 W.BROADWAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 77671 | 23604 | 4517 | 1630 | 5.1443e-05 | 1.1604e-06 | 44.3333 | 1 | 320 | Customer | 139 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | #N/A
J2002.002001 |  | ARKANSAS | POTEAU | 3516:TARBY | TARBY_1625 | 351625 | 2020-02-06 14:30 | 2020-02-06 14:55 | 25.38 | 1 | 1 | 25.3833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | POTEAU | 1/4 MI.WOF 271 ON COGGINS RD. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 82290 | 13501 | 1677 | 1197 | 2.9454e-05 | 1.1604e-06 | 25.3833 | 1 | 310 | Customer | 1962 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-06 | 2020 |  | #N/A
J2002.002003 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_629 | 460629 | 2020-02-06 14:32 | 2020-02-06 16:45 | 133.4 | 1 | 1 | 133.4 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | WOODWARD | 1719 BROADMOOR-WOODWARD | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861794 | 53575 | 10432 | 5686 | 933 | 0.00015479 | 1.1604e-06 | 133.4 | 1 | 310 | Customer | 10698 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | #N/A
J2002.002005 | PD-02062020-00329 | NORTHEAST | SAPULPA | 3207:HILL TOP | HILL TOP 23 | 320723 | 2020-02-06 14:32 | 2020-02-06 19:43 | 310.87 | 3 | 4 | 922.55 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | GLENPOOL | 583 E.140TH ST | CMI_NORMAL | NO | NO | NO | 861794 | 74117 | 40805 | 993 | 412 | 0.0010705 | 3.4811e-06 | 307.5167 | 1 | 320 | Secondary | 40996 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | #N/A
J2002.002004 | PD-02062020-00332 | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_622 | 770622 | 2020-02-06 14:34 | 2020-02-06 16:43 | 129.43 | 1 | 1 | 129.4333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | BRISTOW | 409 E 3RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 74117 | 40805 | 3784 | 2011 | 0.00015019 | 1.1604e-06 | 129.4333 | 1 | 310 | Customer | 41940 | Load | Tran1phOH | GREGORY R HOOVER | 918-261-6803 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | #N/A
J2002.002007 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-06 14:35 | 2020-02-06 16:58 | 143.57 | 1 | 0 | 143.5494 | 4 | DETERIORATION | 12 | POLE | POCOLA | NW OF 112-271 | CMI_PLANNED | YES | NO | NO | 861794 | 82290 | 61238 | 1458 | 1240 | 0.00016657 | 1.1604e-06 | 143.5494 | 1 | 0 | Tap | 2405 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | Ark - Series 2
J2002.002011 | PD-02062020-00326 | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2223 | 882223 | 2020-02-06 14:41 | 2020-02-06 16:15 | 93.62 | 1 | 1 | 90.9333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | EDMOND | BN NE 206 BE BRYANT | CMI_NORMAL | NO | NO | NO | 861794 | 168299 | 19833 | 5388 | 1202 | 0.00010552 | 1.1604e-06 | 90.9333 | 1 | 310 | Load | 26312 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.002015 | PD-02062020-00322 | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2823 | 312823 | 2020-02-06 14:46 | 2020-02-06 16:09 | 82.65 | 1 | 1 | 82.65 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MUSKOGEE | 117 N.N | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 74117 | 33312 | 5285 | 1396 | 9.5905e-05 | 1.1604e-06 | 82.65 | 1 | 310 | Customer | 3503 | Load | Tran1phOH | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-06 | 2020 |  | #N/A
J2002.002014 |  | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5624 | 865624 | 2020-02-06 14:47 | 2020-02-06 14:48 | 0.28 | 112 | 0 | 28 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 2739 SE 59TH ST | CMI_MOMENTARY | YES | NO | NO | 861794 | 159243 | 102215 | 2761 | 112 | 3.249e-05 | 0.00012996 | 0.25 | 1 | 0 | Feeder | FOSTER_5624 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.002017 |  | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5624 | 865624 | 2020-02-06 14:52 | 2020-02-06 15:24 | 32.62 | 1 | 1 | 32.6167 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 3350 E I-240 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 159243 | 102215 | 2761 | 112 | 3.7847e-05 | 1.1604e-06 | 32.6167 | 1 | 310 | Customer | 78040 | Load | Tran3phWye | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.002022 |  | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1523 | 811523 | 2020-02-06 15:11 | 2020-02-06 15:40 | 28.22 | 1 | 1 | 28.2167 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1927 SW.11 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 159243 | 102215 | 6068 | 806 | 3.2742e-05 | 1.1604e-06 | 28.2167 | 1 | 310 | Customer | 1325 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | OK - 2022
J2002.002025 |  | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2021 | 822021 | 2020-02-06 15:20 | 2020-02-06 15:24 | 4.12 | 1 | 1 | 4.1167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3014 NORTH PL | CMI_MOMENTARY | YES | NO | NO | 861794 | 168299 | 148466 | 6036 | 1113 | 4.7769e-06 | 1.1604e-06 | 4.1167 | 1 | 310 | Customer | 15644 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | OK - 2020
J2002.002030 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-02-06 15:40 | 2020-02-06 17:49 | 128.75 | 4 | 0 | 514.9853 | 4 | DETERIORATION | 12 | POLE | ARKOMA | 524 SHERMAN | CMI_PLANNED | YES | NO | NO | 861794 | 82290 | 61238 | 2939 | 877 | 0.00059757 | 4.6415e-06 | 128.7463 | 1 | 0 | Load | 3650 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-06 | 2020 |  | Ark - Series 2
J2002.002033 | PD-02062020-00366 | NORTHEAST | MUSKOGEE | 3326:JAMESVILLE | JAMESVILLE_2642 | 332642 | 2020-02-06 15:51 | 2020-02-06 17:24 | 93.25 | 1 | 1 | 93.25 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | HASKELL | HASKELL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 74117 | 33312 | 1554 | 728 | 0.0001082 | 1.1604e-06 | 93.25 | 1 | 320 | Customer | 14011 | Load | Tran1phOH | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | #N/A
J2002.002036 | PD-02062020-00368 | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_423 | 710423 | 2020-02-06 16:00 | 2020-02-06 19:02 | 181.58 | 1 | 1 | 181.5833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | DAVENPORT | 11/4MW DAVENPORT NS HWY 66 | CMI_NORMAL | NO | NO | NO | 861794 | 114473 | 7479 | 2828 | 980 | 0.0002107 | 1.1604e-06 | 181.5833 | 1 | 320 | Load | 17477 | Load | TranOpenDelta | CAMERON L ALLEN | 405-517-2208 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.002040 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2525 | 912525 | 2020-02-06 16:14 | 2020-02-06 18:19 | 124.92 | 3 | 3 | 314.9 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | FORT SMITH | 4314 S.PHOENIX | CMI_PLANNED | YES | NO | NO | 861794 | 82290 | 61238 | 2739 | 198 | 0.0003654 | 3.4811e-06 | 104.9667 | 1 | 308 | Load | 9792 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | Ark - Series 2
J2002.002042 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_822 | 870822 | 2020-02-06 16:19 | 2020-02-06 16:38 | 19.58 | 1 | 1 | 19.5833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 2608 S. Classen Blvd. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 159243 | 57028 | 6776 | 1805 | 2.2724e-05 | 1.1604e-06 | 19.5833 | 1 | 310 | Customer | 376284 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.002045 | PD-02062020-00382 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5021 | 865021 | 2020-02-06 16:28 | 2020-02-06 22:24 | 355.63 | 1 | 1 | 349.9667 | 13 | PREMATURE FAILURE | 2 | TRANSFORMER OH | MIDWEST CITY | 1110-2 S AIR DEPOT | CMI_NORMAL | NO | NO | NO | 861794 | 114473 | 71243 | 8633 | 1293 | 0.00040609 | 1.1604e-06 | 349.9667 | 1 | 310 | Customer | 72790 | Load | Tran3phWye | DAVID M CLEMMONS | 405-777-8355 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.002049 | PD-02062020-00383 | METRO EAST | SEMINOLE | 7208:CYPRESS | CYPRESS_822 | 720822 | 2020-02-06 16:43 | 2020-02-06 17:45 | 61.8 | 1 | 1 | 35.7667 | 12 | POOR CONNECTION | 50 | CONNECTOR | HOLDENVILLE | 619 E POPLAR | CMI_NORMAL | NO | NO | NO | 861794 | 114473 | 13622 | 2522 | 1432 | 4.1503e-05 | 1.1604e-06 | 35.7667 | 1 | 320 | Customer | 12693 | Load | Tran1phOH | DELBERT HISAW | 405-683-1721 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | OK - 2020
J2002.002052 | PD-02062020-00385 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2222 | 832222 | 2020-02-06 16:47 | 2020-02-06 17:12 | 24.78 | 1 | 1 | 24.7833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2263 NW.37 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 168299 | 148466 | 9178 | 1557 | 2.8758e-05 | 1.1604e-06 | 24.7833 | 1 | 310 | Customer | 13375 | Load | Tran1phOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | OK - 2022
J2002.002056 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7429 | 847429 | 2020-02-06 17:03 | 2020-02-06 17:10 | 7.28 | 1 | 1 | 7.2833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2024 HARDEN DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 168299 | 148466 | 6171 | 681 | 8.4514e-06 | 1.1604e-06 | 7.2833 | 1 | 310 | Customer | 6364 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | OK - 2022
J2002.002058 | PD-02062020-00388 | NORTHWEST | ENID | 4112:CHESTNUT | CHESTNUT_1222 | 411222 | 2020-02-06 17:09 | 2020-02-06 18:09 | 60.45 | 1 | 1 | 60.45 | 22 | WIND | 31 | CONDUCTOR SERVICE - OH | ENID | 2111 E WALNUT AV | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861794 | 53575 | 37620 | 2868 | 1753 | 7.0144e-05 | 1.1604e-06 | 60.45 | 1 | 320 | Customer | 7160 | Load | Tran1phOH | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | #N/A
J2002.002060 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3821 | 913821 | 2020-02-06 17:28 | 2020-02-06 21:36 | 248.02 | 1 | 1 | 236.0667 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | FORT SMITH | ROGERS + 7TH ST | CMI_PLANNED | YES | NO | NO | 861794 | 82290 | 61238 | 2939 | 209 | 0.00027392 | 1.1604e-06 | 236.0667 | 1 | 308 | Mainline | 5179 | Fuse | FuseRiser | Contractor | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-06 | 2020 |  | Ark - Series 2
J2002.002063 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7021 | 817021 | 2020-02-06 17:37 | 2020-02-06 18:09 | 32.05 | 1 | 1 | 32.05 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 7000 S.WALKER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 159243 | 102215 | 9938 | 1789 | 3.719e-05 | 1.1604e-06 | 32.05 | 1 | 310 | Customer | 52784 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.002064 | PD-02062020-00389 | NORTHEAST | SAPULPA | 7604:PAYNE | PAYNE 51 | 760451 | 2020-02-06 17:44 | 2020-02-06 19:05 | 81.17 | 1 | 1 | 77.0167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | RIPLEY | RIPLEY OK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 74117 | 40805 | 365 | 365 | 8.9368e-05 | 1.1604e-06 | 77.0167 | 1 | 310 | Customer | 45270 | Load | Tran1phOH | NICHOLAS MANION | 918-290-1327 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.002067 | PD-02062020-00391 | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1373 | 831373 | 2020-02-06 18:14 | 2020-02-06 19:23 | 69.42 | 1 | 1 | 65.0833 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 13401 N MORGAN RD | CMI_NORMAL | NO | NO | NO | 861794 | 128944 | 116160 | 7911 | 4121 | 7.5521e-05 | 1.1604e-06 | 65.0833 | 1 | 310 | Customer | 224348 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.002070 |  | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5421 | 865421 | 2020-02-06 18:23 | 2020-02-06 18:36 | 13.27 | 1 | 1 | 13.2667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MOORE | 213 nw 12th | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 159251 | 102221 | 9810 | 1880 | 1.5394e-05 | 1.1604e-06 | 13.2667 | 1 | 310 | Customer | 371030 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.002075 | PD-02062020-00396 | NORTHEAST | SAPULPA | 3218:BEGGS | BEGGS_1829 | 321829 | 2020-02-06 18:25 | 2020-02-06 21:02 | 157.03 | 3 | 4 | 456.9 | 4 | DETERIORATION | 50 | CONNECTOR | BEGGS | 5/8N 251ST ON HWY 75A WS | CMI_NORMAL | NO | NO | NO | 861794 | 74122 | 40808 | 1844 | 904 | 0.00053017 | 3.4811e-06 | 152.3 | 1 | 310 | Load | 46575 | Load | Tran1phOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | OK - 2020
J2002.002072 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5132 | 815132 | 2020-02-06 18:31 | 2020-02-06 18:36 | 4.25 | 1 | 1 | 4.25 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2755 SW.74 | CMI_MOMENTARY | YES | NO | NO | 861794 | 159251 | 102221 | 13940 | 2002 | 4.9316e-06 | 1.1604e-06 | 4.25 | 1 | 310 | Customer | 46786 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.002081 | PD-02062020-00394 | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5822 | 845822 | 2020-02-06 18:51 | 2020-02-06 20:30 | 99.25 | 1 | 1 | 99.25 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | SPENCER | 8717 NE.53 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 114484 | 71251 | 2983 | 934 | 0.00011517 | 1.1604e-06 | 99.25 | 1 | 320 | Customer | 29195 | Load | Tran1phOH | KYLE L GOODIN | 405-426-9802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | #N/A
J2002.002090 |  | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9864 | 839864 | 2020-02-06 19:40 | 2020-02-06 19:47 | 7.2 | 1 | 1 | 7.2 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 19116 Rush Springs Ln | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 168306 | 148470 | 10667 | 3302 | 8.3547e-06 | 1.1604e-06 | 7.2 | 1 | 310 | Customer | 361575 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.002089 | PD-02062020-00398 | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2224 | 882224 | 2020-02-06 19:40 | 2020-02-06 20:50 | 70.32 | 1 | 1 | 70.3167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | EDMOND | 4/10S CO LN ES AIR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 168306 | 19836 | 5388 | 1852 | 8.1593e-05 | 1.1604e-06 | 70.3167 | 1 | 310 | Load | 66613 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.002096 |  | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5229 | 835229 | 2020-02-06 19:59 | 2020-02-06 20:17 | 17.82 | 1 | 1 | 17.8167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 11427 SPRINGHOLLOW RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 168306 | 148470 | 6518 | 1290 | 2.0674e-05 | 1.1604e-06 | 17.8167 | 1 | 310 | Customer | 69452 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.002101 | PD-02062020-00403 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_866 | 830866 | 2020-02-06 20:13 | 2020-02-06 21:28 | 74.62 | 3 | 4 | 910.45 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 1405 NW 147TH ST | CMI_NORMAL | NO | NO | NO | 861794 | 168306 | 148470 | 19403 | 4304 | 0.0010565 | 3.4811e-06 | 303.4833 | 1 | 310 | Secondary | 85177 | Load | Tran1phPad | BRIAN E WHITE | 405-642-7075 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.002105 | PD-02062020-00409 | ARKANSAS | FORT SMITH | 9340:TWIN BRIDGES | TWIN_BRIDGES_4021 | 934021 | 2020-02-06 20:31 | 2020-02-06 21:39 | 68.07 | 3 | 4 | 200.75 | 5 | ELECTRICAL TRACKING | 21 | FUSE - TRANSFORMER | VAN BUREN | 1M E-VAN BUREN @ HL10/7 | CMI_NORMAL | NO | NO | NO | 861794 | 82303 | 61245 | 1039 | 1039 | 0.00023294 | 3.4811e-06 | 66.9167 | 1 | 310 | Load | 4495 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-06 | 2020 |  | Ark - Series 1
J2002.002106 | PD-02062020-00412 | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1373 | 831373 | 2020-02-06 20:36 | 2020-02-06 23:40 | 183.75 | 1 | 2 | 179.9 | 13 | PREMATURE FAILURE | 2 | TRANSFORMER OH | OKLAHOMA CITY | 13401 N MORGAN RD | CMI_NORMAL | NO | NO | NO | 861794 | 128944 | 116160 | 7911 | 4121 | 0.00020875 | 1.1604e-06 | 179.9 | 1 | 310 | Customer | 224348 | Load | Tran1phOH | BEAU S HUDSON | 405-306-8284 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.002104 |  | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5229 | 835229 | 2020-02-06 20:38 | 2020-02-06 20:45 | 7.03 | 1 | 1 | 7.0333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 11427 SPRINGHOLLOW RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 168306 | 148470 | 6518 | 1290 | 8.1613e-06 | 1.1604e-06 | 7.0333 | 1 | 315 | Customer | 69452 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | #N/A
J2002.002113 |  | NORTHEAST | MUSKOGEE | 3111:FIVE TRIBES | FIVE_TRIBES_1131 | 311131 | 2020-02-06 21:42 | 2020-02-06 22:08 | 26.22 | 1 | 1 | 26.2167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 1024 SOUTH "C" | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 74122 | 33314 | 1682 | 816 | 3.0421e-05 | 1.1604e-06 | 26.2167 | 1 | 310 | Customer | 4502 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-06 | 2020 |  | #N/A
J2002.002117 | PD-02062020-00416 | METRO SOUTH | SOUTH | 8714:LITTLE AXE | LITTLE_AXE_1421 | 871421 | 2020-02-06 22:22 | 2020-02-07 01:34 | 191.5 | 12 | 9 | 2195.8 | 4 | DETERIORATION | 27 | CUTOUT | NORMAN | DOBBS ON TECUMSEH | CMI_NORMAL | NO | NO | NO | 861794 | 159251 | 57030 | 616 | 616 | 0.0025479 | 1.3924e-05 | 182.9833 | 1 | 310 | Mainline | 16862 | Fuse | FuseOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-06 | 2020 |  | #N/A
J2002.002118 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-02-06 22:25 | 2020-02-06 22:41 | 16.08 | 1 | 1 | 16.0833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 9017 N UNIVERSITY AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861794 | 168306 | 148470 | 8789 | 1953 | 1.8663e-05 | 1.1604e-06 | 16.0833 | 1 | 310 | Customer | 372820 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-06 | 2020 |  | OK - 2021
J2002.002151 | PD-02072020-00010 | NORTHEAST | SAPULPA | 3213:BOWDEN | BOWDEN_1329 | 321329 | 2020-02-07 07:08 | 2020-02-07 08:19 | 70.92 | 1 | 1 | 70.9167 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 23 | FUSE - PRIMARY | SAPULPA | 7757 S. 145th W. Ave. | CMI_NORMAL | NO | NO | NO | 861829 | 74122 | 40808 | 3378 | 1516 | 8.2286e-05 | 1.1603e-06 | 70.9167 | 1 | 310 | Load | 335193 | Load | Tran3phWye | CGI ADMIN | 918-261-6802 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | OK - 2020
J2002.002158 | PD-02072020-00017 | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_622 | 880622 | 2020-02-07 07:36 | 2020-02-07 08:49 | 72.62 | 7 | 6 | 486.15 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | GUTHRIE | 1208 E.SPRINGER | CMI_NORMAL | NO | NO | NO | 861829 | 168306 | 19836 | 5172 | 1166 | 0.00056409 | 8.1223e-06 | 69.45 | 1 | 310 | Load | 40078 | Load | Tran1phOH | JOSEPH WAYNE POOL | 405-919-2253 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002155 |  | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_622 | 880622 | 2020-02-07 07:36 | 2020-02-07 07:36 | 0 | 1166 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | GUTHRIE | 800 W INDUSTRIAL RD | CMI_MOMENTARY | YES | NO | NO | 861829 | 168306 | 19836 | 5172 | 1166 | 0 | 0.0013529 | 0 | 1 | 0 | Feeder | COTWD CK_622 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002161 | PD-02072020-00020 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5132 | 815132 | 2020-02-07 07:49 | 2020-02-07 09:19 | 90.08 | 1 | 1 | 90.0833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 7604 S.VILLA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 159251 | 102221 | 13940 | 2002 | 0.00010453 | 1.1603e-06 | 90.0833 | 1 | 310 | Customer | 31182 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002169 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-07 08:17 | 2020-02-07 14:24 | 366.7 | 4 | 4 | 1365.1 | 4 | DETERIORATION | 2 | TRANSFORMER OH | LAMAR | 150 ASH | CMI_PLANNED | YES | NO | NO | 861829 | 82303 | 7551 | 730 | 0 | 0.001584 | 4.6413e-06 | 341.275 | 1 | 308 | Load | 765 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | #N/A
J2002.002170 | PD-02072020-00048 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5134 | 815134 | 2020-02-07 08:33 | 2020-02-07 09:37 | 64.22 | 1 | 1 | 64.2167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 9701 S.SHARTEL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 159251 | 102221 | 13940 | 2469 | 7.4512e-05 | 1.1603e-06 | 64.2167 | 1 | 310 | Customer | 48913 | Load | Tran1phPad | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002171 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-07 08:38 | 2020-02-07 10:00 | 82.62 | 1 | 1 | 79.4833 | 4 | DETERIORATION | 12 | POLE | POCOLA | NW OF 112-271 | CMI_PLANNED | YES | NO | NO | 861829 | 82303 | 61245 | 1458 | 1240 | 9.2226e-05 | 1.1603e-06 | 79.4833 | 1 | 308 | Tap | 2405 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | Ark - Series 2
J2002.002175 | PD-02072020-00069 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-02-07 08:39 | 2020-02-07 11:00 | 140.82 | 1 | 2 | 145.4833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | WINSLOW | 1M N-MT GAYLOR + 600 E-HL22/8 | CMI_NORMAL | NO | NO | NO | 861829 | 82303 | 61245 | 3790 | 2585 | 0.00016881 | 1.1603e-06 | 145.4833 | 1 | 310 | Load | 5081 | Load | Tran1phOH | KRIS L HALMES | 479-430-9447 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-02-07 | 2020 |  | Ark - Series 2
J2002.002178 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-02-07 08:42 | 2020-02-07 14:26 | 343.87 | 4 | 3 | 681.8333 | 4 | DETERIORATION | 12 | POLE | ARKOMA | 524 SHERMAN | CMI_PLANNED | YES | NO | NO | 861829 | 82303 | 61245 | 2940 | 877 | 0.00079115 | 4.6413e-06 | 170.4583 | 1 | 308 | Load | 3650 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-07 | 2020 |  | Ark - Series 2
J2002.002177 | PD-02072020-00055 | SOUTHERN | PAULS VALLEY | 5611:MAYSVILLE | MAYSVILLE 21 | 561121 | 2020-02-07 08:48 | 2020-02-07 10:48 | 120.07 | 1 | 2 | 115.85 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | MAYSVILLE | BETWEEN ELM,OAK NS 6TH(MAYSVL) | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861829 | 77681 | 6221 | 946 | 494 | 0.00013442 | 1.1603e-06 | 115.85 | 1 | 310 | Customer | 468 | Load | TranOHDeltaSplitBank | BRUCE E BEAM | 405-626-0490 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | OK - 2021
J2002.002176 | PD-02072020-00049 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1924 | 851924 | 2020-02-07 08:50 | 2020-02-07 10:15 | 84.93 | 1 | 1 | 84.9333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 1406 N.DOUGLAS BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 114484 | 71251 | 12467 | 1608 | 9.855e-05 | 1.1603e-06 | 84.9333 | 1 | 310 | Customer | 10732 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002182 |  | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2524 | 512524 | 2020-02-07 09:02 | 2020-02-07 19:34 | 631.4 | 1 | 1 | 631.3753 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | LONE GROVE | CORNER HWY 70 & W. CASE ST, LONE GROVE | CMI_PLANNED | YES | NO | NO | 861829 | 77681 | 23604 | 3307 | 1001 | 0.0007326 | 1.1603e-06 | 631.3753 | 1 | 308 | Load | 223296 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002193 | PD-02072020-00065 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-02-07 09:13 | 2020-02-07 10:11 | 58.05 | 1 | 2 | 55.4167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ARDMORE | 2501 SPRINGDALE RD | CMI_NORMAL | NO | NO | NO | 861829 | 77681 | 23604 | 2209 | 1003 | 6.4301e-05 | 1.1603e-06 | 55.4167 | 1 | 310 | Load | 19569 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002185 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-07 09:19 | 2020-02-07 10:29 | 70.7 | 7 | 2 | 353.2667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | LAMAR | JOHNSONVILLE ST,N-HWY 64,LAMAR | CMI_PLANNED | YES | NO | NO | 861829 | 82303 | 7551 | 730 | 0 | 0.0004099 | 8.1223e-06 | 50.4667 | 1 | 308 | Load | 17403 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | #N/A
J2002.002190 |  | SOUTHERN | SULPHUR | 5705:SULPHUR | SULPHUR_529 | 570529 | 2020-02-07 09:22 | 2020-02-07 09:35 | 12.95 | 1 | 1 | 12.95 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SULPHUR | BL SUL SPR COM STA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 77681 | 6817 | 3635 | 1187 | 1.5026e-05 | 1.1603e-06 | 12.95 | 1 | 310 | Customer | 13231 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | OK - 2021
J2002.002191 |  | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_623 | 410623 | 2020-02-07 09:24 | 2020-02-07 12:24 | 180.72 | 14 | 11 | 2443 | 4 | DETERIORATION | 12 | POLE | ENID | 206 E.COLUMBIA | CMI_PLANNED | YES | NO | NO | 861829 | 53583 | 37623 | 6025 | 1546 | 0.0028347 | 1.6245e-05 | 174.5 | 1 | 308 | Load | 598 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | #N/A
J2002.002202 | PD-02072020-00073 | ARKANSAS | FORT SMITH | 9508:WHITESIDE | WHITESIDE_821 | 950821 | 2020-02-07 09:42 | 2020-02-07 10:41 | 58.57 | 1 | 2 | 58.5667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | VAN BUREN | 2012 CHESTNUT (HOSPITAL DR) | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 82303 | 61245 | 1920 | 1281 | 6.7956e-05 | 1.1603e-06 | 58.5667 | 1 | 320 | Customer | 17491 | Load | Tran3phPadWye | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-07 | 2020 |  | Ark - Series 2
J2002.002206 | PD-02072020-00082 | NORTHEAST | MUSKOGEE | 3312:CHECOTAH | CHECOTAH 21 | 331221 | 2020-02-07 09:53 | 2020-02-07 10:40 | 46.77 | 1 | 1 | 45.1 | 12 | POOR CONNECTION | 50 | CONNECTOR | CHECOTAH | R.CHEC.1/4M.E.OF SEWER ON 266 | CMI_NORMAL | NO | NO | NO | 861829 | 74122 | 33314 | 2892 | 1360 | 5.2331e-05 | 1.1603e-06 | 45.1 | 1 | 320 | Load | 20931 | Load | Tran1phOH | NICHOLAS SELVIDGE | 918-652-1986 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | OK - 2020
J2002.002209 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-07 09:58 | 2020-02-07 10:07 | 9.5 | 1 | 1 | 9.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 7102 HWY-271 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 82303 | 61245 | 1458 | 1240 | 1.1023e-05 | 1.1603e-06 | 9.5 | 1 | 310 | Customer | 1629 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | Ark - Series 2
J2002.002211 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_823 | 870823 | 2020-02-07 09:58 | 2020-02-07 10:02 | 4.25 | 1 | 1 | 4.25 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 2825 S.DEWEY AV | CMI_MOMENTARY | YES | NO | NO | 861829 | 159251 | 57030 | 6776 | 2379 | 4.9314e-06 | 1.1603e-06 | 4.25 | 1 | 310 | Customer | 17090 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002212 |  | METRO WEST | WEST | 8157:MACARTHUR | MACARTHUR_5722 | 815722 | 2020-02-07 10:00 | 2020-02-07 10:28 | 27.92 | 3 | 1 | 50.2644 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 4100 NEWCASTLE BL | CMI_PLANNED | YES | NO | NO | 861829 | 128944 | 116160 | 1854 | 347 | 5.8323e-05 | 3.481e-06 | 16.7548 | 1 | 310 | Load | 36173 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | #N/A
J2002.002218 | PD-02072020-00095 | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5629 | 865629 | 2020-02-07 10:12 | 2020-02-07 10:58 | 46.43 | 1 | 1 | 46.4333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | I-240 + S.EASTERN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 159251 | 102221 | 2761 | 736 | 5.3878e-05 | 1.1603e-06 | 46.4333 | 1 | 310 | Load | 67473 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002220 |  | NORTHWEST | ENID | 4109:WAUKOMIS | WAUKOMIS 23 | 410923 | 2020-02-07 10:18 | 2020-02-07 13:13 | 175.57 | 1 | 1 | 173.4667 | 4 | DETERIORATION | 12 | POLE | FAIRMONT | 1N 1E PION SCH | CMI_PLANNED | YES | NO | NO | 861829 | 53583 | 37623 | 1558 | 572 | 0.00020128 | 1.1603e-06 | 173.4667 | 1 | 308 | Tap | 378224 | Fuse | FuseOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002228 | PD-02072020-00134 | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1222 | 911222 | 2020-02-07 10:34 | 2020-02-07 12:04 | 90.27 | 1 | 1 | 90.2667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 502.5 S.18 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 82303 | 61245 | 6607 | 1292 | 0.00010474 | 1.1603e-06 | 90.2667 | 1 | 320 | Customer | 12505 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | Ark - Series 1
J2002.002229 |  | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_423 | 710423 | 2020-02-07 10:35 | 2020-02-07 11:10 | 35.28 | 2 | 1 | 69.9 | 4 | DETERIORATION | 2 | TRANSFORMER OH | DAVENPORT | 43/4MI E 1/2MI N HWY66 | CMI_PLANNED | YES | NO | NO | 861829 | 114484 | 7480 | 2828 | 980 | 8.1107e-05 | 2.3206e-06 | 34.95 | 1 | 308 | Tap | 5992 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002243 |  | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_922 | 910922 | 2020-02-07 10:38 | 2020-02-07 14:00 | 201.67 | 4 | 4 | 274.0333 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | FORT SMITH | HEATHER RIDGE AND GARY STREET | CMI_PLANNED | YES | NO | NO | 861829 | 82303 | 61245 | 5015 | 960 | 0.00031797 | 4.6413e-06 | 68.5083 | 1 | 308 | Secondary | 15693 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | Ark - Series 3
J2002.002235 |  | ARKANSAS | FORT SMITH | 9508:WHITESIDE | WHITESIDE_821 | 950821 | 2020-02-07 10:40 | 2020-02-07 11:09 | 28.28 | 1 | 1 | 28.2833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | VAN BUREN | lot 16 Park Heights | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 82303 | 61245 | 1920 | 1281 | 3.2818e-05 | 1.1603e-06 | 28.2833 | 1 | 310 | Customer | 308339 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-07 | 2020 |  | Ark - Series 2
J2002.002234 | PD-02072020-00115 | METRO WEST | WEST | 8359:YUKON | YUKON_5923 | 835923 | 2020-02-07 10:41 | 2020-02-07 13:09 | 148.02 | 1 | 1 | 148.0167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | YUKON | S.6TH + ELM | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 128944 | 116160 | 6433 | 1152 | 0.00017175 | 1.1603e-06 | 148.0167 | 1 | 320 | Load | 76770 | Load | TranOH3phDelta | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | #N/A
J2002.002236 | PD-02072020-00119 | METRO WEST | EL RENO | 8908:ROMAN NOSE | ROMAN_NOSE_852 | 890852 | 2020-02-07 10:41 | 2020-02-07 13:05 | 143.53 | 1 | 2 | 143.5333 | 13 | PREMATURE FAILURE | 2 | TRANSFORMER OH | LOYAL | N2730 RD and E0730 Rd | CMI_NORMAL | NO | NO | NO | 861829 | 128944 | 12784 | 525 | 257 | 0.00016655 | 1.1603e-06 | 143.5333 | 1 | 310 | Load | 379388 | Load | Tran3phWye | ERIC S KAPPUS | 405-642-1454 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002245 | PD-02072020-00135 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4121 | 814121 | 2020-02-07 10:54 | 2020-02-07 14:58 | 243.6 | 14 | 19 | 3389.4 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 5109 S.FRANCIS | CMI_NORMAL | NO | NO | NO | 861829 | 159251 | 102221 | 5809 | 1200 | 0.0039328 | 1.6245e-05 | 242.1 | 1 | 310 | Load | 7703 | Load | Tran1phOH | JACOB SHANDY | 918-623-6369 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | #N/A
J2002.002246 |  | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2022 | 862022 | 2020-02-07 11:03 | 2020-02-07 11:24 | 21.23 | 4 | 0 | 39.1333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 14 SE.30 | CMI_PLANNED | YES | NO | NO | 861829 | 159251 | 102221 | 4757 | 1554 | 4.5407e-05 | 4.6413e-06 | 9.7833 | 1 | 0 | Load | 1270 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002255 | PD-02072020-00144 | SOUTHERN | PAULS VALLEY | 5619:RUSH CREEK | RUSH_CREEK_1922 | 561922 | 2020-02-07 11:11 | 2020-02-07 11:41 | 30.1 | 11 | 9 | 303.7833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | PAULS VALLEY | N OF LESLIE E OF ELIZABETH | CMI_NORMAL | NO | NO | NO | 861829 | 77681 | 6221 | 2074 | 1193 | 0.00035249 | 1.2764e-05 | 27.6167 | 1 | 310 | Load | 10155 | Load | Tran1phOH | BRUCE E BEAM | 405-626-0490 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | OK - 2021
J2002.002248 | PD-02072020-00137 | METRO EAST | SEMINOLE | 7208:CYPRESS | CYPRESS_822 | 720822 | 2020-02-07 11:11 | 2020-02-07 13:24 | 133 | 1 | 2 | 100.7667 | 4 | DETERIORATION | 50 | CONNECTOR | HOLDENVILLE | 1O5 HUGHES | CMI_NORMAL | NO | NO | NO | 861829 | 114484 | 13624 | 2522 | 1432 | 0.00011692 | 1.1603e-06 | 100.7667 | 1 | 320 | Customer | 5457 | Load | Tran1phOH | DELBERT HISAW | 405-683-1721 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | OK - 2020
J2002.002253 | PD-02072020-00141 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9922 | 829922 | 2020-02-07 11:14 | 2020-02-07 12:29 | 74.67 | 1 | 1 | 18.2995 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 6647 NW 10 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 128944 | 116160 | 9241 | 842 | 2.1233e-05 | 1.1603e-06 | 18.2995 | 1 | 310 | Customer | 34525 | Load | Tran1phPad | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002259 | PD-02072020-00151 | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1022 | 311022 | 2020-02-07 11:23 | 2020-02-07 15:10 | 227.45 | 67 | 30 | 15061.6 | 29 | TREES : GROW IN | 37 | CONDUCTOR PRIMARY - OH | MUSKOGEE | C.CLUB DR + C.CLUB RD | CMI_NORMAL | NO | NO | NO | 861829 | 74122 | 33314 | 2906 | 1093 | 0.017476 | 7.7742e-05 | 224.8 | 1 | 310 | Mainline | 3107 | Fuse | FuseOH | GARY MICHAEL KNUPP | 918-577-8564 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | #N/A
J2002.002270 | PD-02072020-00161 | NORTHEAST | MUSKOGEE | 3332:EUFAULA SPA | EUFAULA SPA 23 | 333223 | 2020-02-07 11:33 | 2020-02-07 12:55 | 82.25 | 3 | 3 | 226.35 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | EUFAULA | 1.5N.ON COON CREEK | CMI_NORMAL | NO | NO | NO | 861829 | 74122 | 33314 | 263 | 165 | 0.00026264 | 3.481e-06 | 75.45 | 1 | 310 | Load | 19468 | Load | Tran1phOH | NICHOLAS SELVIDGE | 918-652-1986 | [5 empty] | Animals | N | DISTRIBUTION | 24.9kV | 2020-02-07 | 2020 |  | #N/A
J2002.002273 | PD-02072020-00176 | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8123 | 838123 | 2020-02-07 11:56 | 2020-02-07 13:56 | 120.07 | 1 | 1 | 120.0667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 8301 N. COUNCIL, #1203 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 128944 | 116160 | 8961 | 1217 | 0.00013932 | 1.1603e-06 | 120.0667 | 1 | 310 | Customer | 73560 | Load | Tran1phPad | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002283 |  | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1926 | 851926 | 2020-02-07 12:01 | 2020-02-07 12:20 | 18.78 | 1 | 1 | 18.7833 | 1 | CANCELLED | 57 | CANCELLED | MIDWEST CITY | 1204 MCDONALD DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 114484 | 71251 | 12467 | 2128 | 2.1795e-05 | 1.1603e-06 | 18.7833 | 1 | 308 | Customer | 21590 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | OK - 2021
J2002.002279 | PD-02072020-00186 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2222 | 852222 | 2020-02-07 12:11 | 2020-02-07 13:53 | 101.62 | 1 | 2 | 101.6167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | HARRAH | 935 N DOBBS RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 114484 | 71251 | 11646 | 2221 | 0.00011791 | 1.1603e-06 | 101.6167 | 1 | 310 | Load | 77437 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002281 | PD-02072020-00178 | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-02-07 12:13 | 2020-02-07 12:59 | 45.95 | 1 | 1 | 45.95 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ARKOMA | 700 YOUNG | CMI_NORMAL | NO | NO | NO | 861829 | 82303 | 61245 | 2940 | 877 | 5.3317e-05 | 1.1603e-06 | 45.95 | 1 | 310 | Customer | 8001 | Load | Tran1phOH | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-02-07 | 2020 |  | Ark - Series 2
J2002.002287 | PD-02072020-00182 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2224 | 832224 | 2020-02-07 12:28 | 2020-02-07 13:36 | 67.62 | 1 | 1 | 67.6167 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 3816 N.DREXEL | CMI_NORMAL | NO | NO | NO | 861829 | 168306 | 148470 | 9178 | 1431 | 7.8457e-05 | 1.1603e-06 | 67.6167 | 1 | 310 | Customer | 15407 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | #N/A
J2002.002290 |  | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3721 | 913721 | 2020-02-07 12:36 | 2020-02-07 13:39 | 62.82 | 4 | 4 | 198.6667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 4720 S.Q | CMI_PLANNED | YES | NO | NO | 861829 | 82303 | 61245 | 4573 | 1500 | 0.00023052 | 4.6413e-06 | 49.6667 | 1 | 310 | Load | 13041 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | Ark - Series 3
J2002.002292 |  | METRO SOUTH | SOUTH CENTRAL | 8717:TURNER | TURNER_1723 | 871723 | 2020-02-07 12:41 | 2020-02-07 12:51 | 10.53 | 1 | 1 | 10.5333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 6475 36TH AV NW | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 159251 | 102221 | 3083 | 1097 | 1.2222e-05 | 1.1603e-06 | 10.5333 | 1 | 310 | Customer | 358009 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002305 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1229 | 831229 | 2020-02-07 13:16 | 2020-02-07 13:16 | 0.02 | 787 | 0 | 13.1167 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 5529 CLASSEN BLVD | CMI_MOMENTARY | YES | NO | NO | 861829 | 168306 | 148470 | 7754 | 787 | 1.522e-05 | 0.00091317 | 0.016667 | 1 | 0 | Feeder | BEL ISLE_1229 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-07 | 2020 |  | OK - 2022
J2002.002307 | PD-02072020-00217 | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6222 | 866222 | 2020-02-07 13:25 | 2020-02-07 16:12 | 166.9 | 1 | 1 | 166.9 | 22 | WIND | 12 | POLE | OKLAHOMA CITY | 13600 SE.35 | CMI_NORMAL | NO | NO | NO | 861829 | 114484 | 71251 | 7214 | 1901 | 0.00019366 | 1.1603e-06 | 166.9 | 1 | 310 | Customer | 51464 | Load | Tran1phOH | DAVID M CLEMMONS | 405-777-8355 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002315 | PD-02072020-00237 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9931 | 829931 | 2020-02-07 13:43 | 2020-02-07 15:10 | 86.57 | 1 | 1 | 86.5667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 6025 NW 10TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 128944 | 116160 | 9241 | 2198 | 0.00010045 | 1.1603e-06 | 86.5667 | 1 | 310 | Customer | 34742 | Load | Tran1phPad | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002314 |  | SOUTHERN | PAULS VALLEY | 5611:MAYSVILLE | MAYSVILLE 21 | 561121 | 2020-02-07 13:44 | 2020-02-07 15:49 | 125.28 | 1 | 1 | 125.2833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MAYSVILLE | BETWEEN ELM,OAK NS 6TH(MAYSVL) | CMI_NORMAL | NO | NO | NO | 861829 | 77681 | 6221 | 946 | 494 | 0.00014537 | 1.1603e-06 | 125.2833 | 1 | 310 | Customer | 468 | Load | TranOHDeltaSplitBank | [7 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | OK - 2021
J2002.002316 | PD-02072020-00236 | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8122 | 838122 | 2020-02-07 13:44 | 2020-02-07 15:48 | 124.02 | 1 | 3 | 118.05 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 9900 PHEASANT LN | CMI_NORMAL | NO | NO | NO | 861829 | 128944 | 116160 | 8961 | 971 | 0.00013698 | 1.1603e-06 | 118.05 | 1 | 310 | Customer | 53484 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002320 | PD-02072020-00256 | NORTHEAST | MUSKOGEE | 3111:FIVE TRIBES | FIVE_TRIBES_1131 | 311131 | 2020-02-07 13:57 | 2020-02-07 17:20 | 203.08 | 49 | 31 | 9167.0833 | 12 | POOR CONNECTION | 50 | CONNECTOR | MUSKOGEE | 1/2 MS BORDER ON 69 . | CMI_NORMAL | NO | NO | NO | 861829 | 74122 | 33314 | 1682 | 816 | 0.010637 | 5.6856e-05 | 187.0833 | 1 | 310 | Mainline | 28031 | Fuse | FuseOH | GARY MICHAEL KNUPP | 918-577-8564 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-07 | 2020 |  | #N/A
J2002.002323 |  | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1823 | 931823 | 2020-02-07 14:05 | 2020-02-07 14:27 | 21.58 | 5 | 5 | 123.7304 | 4 | DETERIORATION | 39 | BUSHING | ALMA | KINGS POINT CIR | CMI_PLANNED | YES | NO | NO | 861829 | 82303 | 61245 | 2850 | 1240 | 0.00014357 | 5.8016e-06 | 24.7461 | 1 | 310 | Load | 16785 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | Ark - Series 2
J2002.002324 |  | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-02-07 14:07 | 2020-02-07 14:07 | 0.08 | 41 | 0 | 2.6964 | 1 | CANCELLED | 57 | CANCELLED | 0 | 0 | CMI_MOMENTARY | YES | NO | NO | 861829 | 77681 | 7201 | 2191 | 1672 | 3.1287e-06 | 4.7573e-05 | 0.065767 | 1 | 0 | Mainline |  | 0 | 0 | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002327 | PD-02072020-00279 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1221 | 831221 | 2020-02-07 14:25 | 2020-02-07 17:00 | 154.87 | 1 | 1 | 87.7434 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 2625 NW 65TH | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861829 | 168306 | 148470 | 7754 | 995 | 0.00010181 | 1.1603e-06 | 87.7434 | 1 | 310 | Customer | 23274 | Load | TranOpenDelta | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | OK - 2022
J2002.002328 | PD-02072020-00284 | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1724 | 831724 | 2020-02-07 14:28 | 2020-02-07 15:05 | 37.18 | 1 | 1 | 37.1833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 12601 N.PENN BLDG 21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 168306 | 148470 | 6648 | 2778 | 4.3145e-05 | 1.1603e-06 | 37.1833 | 1 | 310 | Customer | 75139 | Load | Tran1phPad | CAMERON PITTS | 405-537-6633 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002339 |  | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-02-07 14:43 | 2020-02-07 14:44 | 0.22 | 10 | 0 | 2.175 | 1 | CANCELLED | 57 | CANCELLED | 0 | 0 | CMI_MOMENTARY | YES | NO | NO | 861829 | 77681 | 7201 | 2191 | 1672 | 2.5237e-06 | 1.1603e-05 | 0.2175 | 1 | 0 | Mainline |  | 0 | 0 | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002348 |  | ARKANSAS | POTEAU | 3607:ROLAND ROAD | ROLAND_RD_721 | 360721 | 2020-02-07 14:59 | 2020-02-07 15:10 | 11.58 | 1 | 1 | 8 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ROLAND | 12 SHADY LANE, ROLAND | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 82303 | 13507 | 1141 | 1141 | 9.2826e-06 | 1.1603e-06 | 8 | 1 | 310 | Customer | 16484 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | #N/A
J2002.002353 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-02-07 15:10 | 2020-02-07 15:18 | 7.8 | 1 | 1 | 7.8 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7235 JANET | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 159251 | 57030 | 4239 | 1005 | 9.0505e-06 | 1.1603e-06 | 7.8 | 1 | 310 | Customer | 71243 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002352 | PD-02072020-00315 | NORTHWEST | ENID | 4261:WHITE EAGLE | WHITE_EAGLE_6121 | 426121 | 2020-02-07 15:12 | 2020-02-07 18:19 | 186.98 | 1 | 1 | 182.4833 | 22 | WIND | 17 | JUMPER | PONCA CITY | 1.5S RANCH ELV | CMI_NORMAL | NO | NO | NO | 861829 | 53583 | 37623 | 216 | 216 | 0.00021174 | 1.1603e-06 | 182.4833 | 1 | 310 | Load | 7051 | Load | Tran3phWye | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002356 | PD-02072020-00319 | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2522 | 512522 | 2020-02-07 15:16 | 2020-02-07 15:54 | 37.87 | 1 | 1 | 37.8667 | 4 | DETERIORATION | 20 | FUSE BARREL | LONE GROVE | 3N ON NWPRT RD (LG WATER WELL) | CMI_NORMAL | NO | NO | NO | 861829 | 77681 | 23604 | 3307 | 562 | 4.3938e-05 | 1.1603e-06 | 37.8667 | 1 | 320 | Load | 16781 | Load | Tran3phWye | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | OK - 2021
J2002.002355 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6961 | 846961 | 2020-02-07 15:17 | 2020-02-07 15:17 | 0.07 | 1215 | 0 | 81 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | W MEMORIAL RD & SANTA FE AV | CMI_MOMENTARY | YES | NO | NO | 861829 | 168306 | 148470 | 7729 | 1388 | 9.3986e-05 | 0.0014098 | 0.066667 | 1 | 0 | Mainline | 252370 | Recloser | Rec3phElectronic | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002358 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6921 | 846921 | 2020-02-07 15:28 | 2020-02-07 15:37 | 8.47 | 1 | 1 | 8.4667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 14613 N KELLEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 168306 | 148470 | 7729 | 1358 | 9.8241e-06 | 1.1603e-06 | 8.4667 | 1 | 310 | Load | 81816 | Load | Tran3phPadWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002360 | PD-02072020-00325 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4821 | 824821 | 2020-02-07 15:35 | 2020-02-07 17:44 | 128.95 | 1 | 1 | 123.9167 | 3 | DAMAGED BY PUBLIC | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 2109 W. SHERIDAN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 168306 | 148470 | 4200 | 242 | 0.00014378 | 1.1603e-06 | 123.9167 | 1 | 310 | Customer | 1037 | Load | TranOpenDelta | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | OK - 2022
J2002.002364 | PD-02072020-00334 | ARKANSAS | POTEAU | 3516:TARBY | TARBY_1625 | 351625 | 2020-02-07 15:51 | 2020-02-07 16:39 | 47.9 | 1 | 2 | 47.5 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | POTEAU | .5ME ABM DR NS RD | CMI_NORMAL | NO | NO | NO | 861829 | 82303 | 13507 | 1677 | 1197 | 5.5115e-05 | 1.1603e-06 | 47.5 | 1 | 310 | Load | 15281 | Load | Tran1phOH | TOBY C MEAD | 918-658-5596 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-02-07 | 2020 |  | #N/A
J2002.002366 |  | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1022 | 311022 | 2020-02-07 16:02 | 2020-02-07 16:10 | 8.32 | 1 | 1 | 8.3167 | 1 | CANCELLED | 57 | CANCELLED | MUSKOGEE | CLUBVIEW ESTATES | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 74122 | 33314 | 2906 | 1093 | 9.65e-06 | 1.1603e-06 | 8.3167 | 1 | 310 | Customer | 195910 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | #N/A
J2002.002368 | PD-02072020-00340 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2122 | 822122 | 2020-02-07 16:09 | 2020-02-07 21:03 | 294.08 | 1 | 5 | 9.8833 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 4212 NW.22 | CMI_NORMAL | NO | NO | NO | 861829 | 168306 | 148470 | 9250 | 1837 | 1.1468e-05 | 1.1603e-06 | 9.8833 | 1 | 310 | Customer | 27119 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | OK - 2020
J2002.002370 | PD-02072020-00341 | METRO NORTH | NORTH | 8347:WILSHIRE | WILSHIRE_4721 | 834721 | 2020-02-07 16:13 | 2020-02-07 17:30 | 77.4 | 1 | 1 | 77.4 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 6101 N.MAY AV | CMI_NORMAL | NO | NO | NO | 861829 | 168306 | 148470 | 4624 | 927 | 8.9809e-05 | 1.1603e-06 | 77.4 | 1 | 320 | Customer | 21262 | Load | TranOpenDelta | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | OK - 2022
J2002.002372 |  | METRO WEST | WEST | 8222:CZECH HALL | CZECH_HALL_2222 | 822222 | 2020-02-07 16:27 | 2020-02-07 16:36 | 8.95 | 1 | 1 | 8.95 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 11501 LOCHWOOD DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 128944 | 116160 | 8612 | 2029 | 1.0385e-05 | 1.1603e-06 | 8.95 | 1 | 310 | Customer | 76443 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002383 | PD-02072020-00351 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3629 | 833629 | 2020-02-07 16:48 | 2020-02-07 17:39 | 50.6 | 6 | 6 | 270.35 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | THE VILLAGE | 2837 HUNTLEIGH DR | CMI_NORMAL | NO | NO | NO | 861829 | 168306 | 148470 | 8789 | 1397 | 0.00031369 | 6.9619e-06 | 45.0583 | 1 | 310 | Load | 14365 | Load | Tran1phOH | BRADLEY SUDBECK | 405-999-6850 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002380 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3629 | 833629 | 2020-02-07 16:48 | 2020-02-07 16:48 | 0 | 1397 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 2204 HEFNER RD | CMI_MOMENTARY | YES | NO | NO | 861829 | 168306 | 148470 | 8789 | 1397 | 0 | 0.001621 | 0 | 1 | 0 | Feeder | TENNESSE_3629 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002381 | PD-02072020-00353 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-02-07 16:50 | 2020-02-07 18:45 | 115.38 | 1 | 1 | 118.7333 | 5 | ELECTRICAL TRACKING | 20 | FUSE BARREL | ALMA | NEWBERRY CHAPPLE RD,ALMA RURAL | CMI_NORMAL | NO | NO | NO | 861829 | 82303 | 61245 | 3790 | 2585 | 0.00013777 | 1.1603e-06 | 118.7333 | 1 | 310 | Customer | 16433 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-07 | 2020 |  | Ark - Series 2
J2002.002386 | PD-02072020-00356 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3622 | 853622 | 2020-02-07 16:59 | 2020-02-07 17:41 | 41.62 | 1 | 1 | 41.6167 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1315 S.EASTERN | CMI_NORMAL | NO | NO | NO | 861829 | 168306 | 148470 | 5933 | 965 | 4.8289e-05 | 1.1603e-06 | 41.6167 | 1 | 320 | Load | 52380 | Load | Tran3phWye | ROBERT HALL | 405-757-9640 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002385 | PD-02072020-00355 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-02-07 17:00 | 2020-02-07 18:36 | 96.33 | 1 | 1 | 92.2333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 318 NW.20 | CMI_NORMAL | NO | NO | NO | 861829 | 168306 | 148470 | 11122 | 2333 | 0.00010702 | 1.1603e-06 | 92.2333 | 1 | 310 | Customer | 35186 | Load | TranOpenDelta | MONTY WISELEY | 405-471-2592 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | OK - 2020
J2002.002387 | PD-02072020-00357 | METRO WEST | WEST | 8158:SARA | SARA_5871 | 815871 | 2020-02-07 17:04 | 2020-02-07 18:41 | 97.43 | 1 | 1 | 89.9167 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | BELLFLOWER SEC. 3 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861829 | 128944 | 116160 | 18280 | 5413 | 0.00010433 | 1.1603e-06 | 89.9167 | 1 | 320 | Customer | 200403 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | OK - 2022
J2002.002392 | PD-02072020-00358 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2222 | 852222 | 2020-02-07 17:11 | 2020-02-07 17:58 | 47.15 | 1 | 1 | 44.8167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | HARRAH | 935 N DOBBS RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 114484 | 71251 | 11646 | 2221 | 5.2002e-05 | 1.1603e-06 | 44.8167 | 1 | 310 | Load | 77437 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002391 |  | NORTHEAST | SAPULPA | 7632:OAK GROVE | OAK_GROVE_3221 | 763221 | 2020-02-07 17:12 | 2020-02-07 17:31 | 19.17 | 1 | 1 | 19.1667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | CUSHING | 2323 N oakgrove rd | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 74122 | 40808 | 1020 | 1020 | 2.224e-05 | 1.1603e-06 | 19.1667 | 1 | 310 | Load | 370859 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | OK - 2021
J2002.002393 | PD-02072020-00360 | ARKANSAS | FORT SMITH | 9126:OAK PARK | OAK_PARK_2621 | 912621 | 2020-02-07 17:16 | 2020-02-07 18:42 | 85.7 | 1 | 1 | 85.7 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 3817 MARY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 82303 | 61245 | 2286 | 113 | 9.944e-05 | 1.1603e-06 | 85.7 | 1 | 320 | Customer | 6633 | Load | Tran1phOH | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-07 | 2020 |  | #N/A
J2002.002394 | PD-02072020-00359 | NORTHEAST | MUSKOGEE | 3111:FIVE TRIBES | FIVE_TRIBES_1131 | 311131 | 2020-02-07 17:21 | 2020-02-07 18:13 | 51.22 | 1 | 1 | 51.2104 | 12 | POOR CONNECTION | 50 | CONNECTOR | MUSKOGEE | 2912 WAUHILLA DR | CMI_NORMAL | NO | NO | NO | 861829 | 74122 | 33314 | 1682 | 816 | 5.9421e-05 | 1.1603e-06 | 51.2104 | 1 | 310 | Customer | 6658 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-07 | 2020 |  | #N/A
J2002.002402 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-02-07 17:51 | 2020-02-07 18:40 | 49.32 | 1 | 1 | 41.1667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 304 NW.20 | CMI_NORMAL | NO | NO | NO | 861829 | 168306 | 148470 | 11122 | 2333 | 4.7767e-05 | 1.1603e-06 | 41.1667 | 1 | 310 | Customer | 2642 | Load | Tran1phOH | Ties | [6 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | OK - 2020
J2002.002405 | PD-02072020-00365 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1523 | 811523 | 2020-02-07 18:25 | 2020-02-07 19:58 | 92.55 | 1 | 1 | 92.55 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2217 SW.19 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 159258 | 102225 | 6070 | 807 | 0.00010739 | 1.1603e-06 | 92.55 | 1 | 320 | Customer | 5738 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | OK - 2022
J2002.002408 |  | METRO WEST | WEST | 8323:RICHARDS | RICHARDS_2321 | 832321 | 2020-02-07 18:39 | 2020-02-07 19:14 | 34.5 | 1 | 1 | 34.5 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 13304 MACKINAC ISLAND DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 128953 | 116166 | 5020 | 1409 | 4.0031e-05 | 1.1603e-06 | 34.5 | 1 | 310 | Customer | 339323 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002411 |  | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1724 | 831724 | 2020-02-07 19:04 | 2020-02-07 19:12 | 8.17 | 1 | 1 | 8.1667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 2301 NW.122 BLDG 16A | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 168321 | 148484 | 6648 | 2778 | 9.476e-06 | 1.1603e-06 | 8.1667 | 1 | 310 | Customer | 75029 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002416 | PD-02072020-00369 | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9869 | 839869 | 2020-02-07 19:36 | 2020-02-07 22:17 | 161 | 1 | 1 | 161 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2312 Pueblos Rd | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 168321 | 148484 | 10667 | 3002 | 0.00018681 | 1.1603e-06 | 161 | 1 | 320 | Customer | 393567 | Load | Tran1phPad | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | OK - 2022
J2002.002424 | PD-02072020-00368 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_871 | 830871 | 2020-02-07 19:48 | 2020-02-07 21:26 | 98.72 | 551 | 277 | 51968.4833 | 13 | PREMATURE FAILURE | 23 | FUSE - PRIMARY | OKLAHOMA CITY | 20032 N PENNSYLVANIA AV | CMI_NORMAL | NO | NO | NO | 861829 | 168321 | 148484 | 19409 | 4254 | 0.0603 | 0.00063934 | 94.3167 | 1 | 310 | Mainline | 316262 | Fuse | FuseOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | OK - 2021
J2002.002422 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_869 | 830869 | 2020-02-07 19:50 | 2020-02-07 20:04 | 13.85 | 1 | 1 | 13.85 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4216 NW 146TH TERRACE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 168321 | 148484 | 19409 | 2470 | 1.607e-05 | 1.1603e-06 | 13.85 | 1 | 310 | Customer | 4926 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002432 | PD-02072020-00371 | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-02-07 19:52 | 2020-02-08 00:26 | 273.88 | 15 | 10 | 2090.65 | 4 | DETERIORATION | 1 | TRANSFORMER UG | LAVACA | BERRY RIDGE ADDITION | CMI_NORMAL | NO | NO | NO | 861829 | 82310 | 61250 | 2740 | 2128 | 0.0024258 | 1.7405e-05 | 139.3767 | 1 | 310 | Mainline | 101226 | Fuse | FuseRiser | TRAVIS EARNHART | 479-719-2561 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | Ark - Series 2
J2002.002430 | PD-02072020-00372 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4122 | 814122 | 2020-02-07 19:57 | 2020-02-07 21:43 | 105.73 | 1 | 2 | 100.3333 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 338 SE.48 | CMI_NORMAL | NO | NO | NO | 861829 | 159258 | 102225 | 5810 | 1273 | 0.00011642 | 1.1603e-06 | 100.3333 | 1 | 310 | Customer | 9591 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | #N/A
J2002.002433 | PD-02072020-00373 | METRO NORTH | NORTH | 8347:WILSHIRE | WILSHIRE_4722 | 834722 | 2020-02-07 20:02 | 2020-02-07 20:49 | 47.08 | 1 | 1 | 17.45 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2501 CLERMONT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 168321 | 148484 | 4624 | 1590 | 2.0248e-05 | 1.1603e-06 | 17.45 | 1 | 310 | Customer | 21650 | Load | TranOpenDelta | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | OK - 2021
J2002.002447 | PD-02072020-00386 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7021 | 817021 | 2020-02-07 21:13 | 2020-02-07 22:15 | 61.78 | 1 | 1 | 61.7833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 801 SW 89th St. | CMI_NORMAL | NO | NO | NO | 861829 | 159258 | 102225 | 9938 | 1789 | 7.1689e-05 | 1.1603e-06 | 61.7833 | 1 | 310 | Customer | 78180 | Load | Tran1phOH | CAMERON L ALLEN | 405-517-2208 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002448 | PD-02072020-00388 | NORTHEAST | SAPULPA | 3210:HICKORY HILL | HICKORY_HILL_1024 | 321024 | 2020-02-07 21:16 | 2020-02-07 23:10 | 113.58 | 1 | 1 | 46.6167 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | SAPULPA | 1110 E.TERESA | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861829 | 74141 | 40825 | 2684 | 1247 | 5.409e-05 | 1.1603e-06 | 46.6167 | 1 | 310 | Customer | 44759 | Load | Tran1phOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | OK - 2022
J2002.002449 | PD-02072020-00389 | ARKANSAS | POTEAU | 3608:MULDROW | MULDROW 21 | 360821 | 2020-02-07 21:20 | 2020-02-07 23:56 | 156.1 | 1 | 1 | 156.1 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MULDROW | 310 E.BROADWAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861829 | 82310 | 13509 | 2274 | 1227 | 0.00018113 | 1.1603e-06 | 156.1 | 1 | 310 | Customer | 11085 | Load | Tran1phPad | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-07 | 2020 |  | #N/A
J2002.002452 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_871 | 830871 | 2020-02-07 21:54 | 2020-02-07 21:58 | 4.25 | 1 | 1 | 4.25 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 2216 NW 195TH ST | CMI_MOMENTARY | YES | NO | NO | 861829 | 168321 | 148484 | 19409 | 4254 | 4.9314e-06 | 1.1603e-06 | 4.25 | 1 | 310 | Customer | 302524 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | OK - 2021
J2002.002454 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7021 | 817021 | 2020-02-07 22:08 | 2020-02-08 00:29 | 140.3 | 9 | 8 | 1203.15 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 815 SW 89 | CMI_NORMAL | NO | NO | NO | 861829 | 159258 | 102225 | 9938 | 1789 | 0.001396 | 1.0443e-05 | 133.6833 | 1 | 310 | Load | 78267 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002463 | PD-02072020-00394 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2122 | 822122 | 2020-02-07 23:02 | 2020-02-08 01:56 | 173.57 | 1 | 1 | 173.5667 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 2208 N.SAPULPA | CMI_NORMAL | NO | NO | NO | 861829 | 168321 | 148484 | 9250 | 1837 | 0.00020139 | 1.1603e-06 | 173.5667 | 1 | 320 | Customer | 15524 | Load | Tran1phOH | BRADLEY SUDBECK | 405-999-6850 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | OK - 2020
J2002.002464 |  | SOUTHERN | MADILL | 5410:GLASSES | GLASSES_1023 | 541023 | 2020-02-07 23:08 | 2020-02-08 00:13 | 65.12 | 7 | 5 | 344.75 | 28 | OTHER (DESCRIBE) | 19 | GROUNDING | MADILL | 108 SQUARE | CMI_PLANNED | YES | NO | NO | 861829 | 77689 | 7202 | 2380 | 844 | 0.00040002 | 8.1223e-06 | 49.25 | 1 | 308 | Load | 308 | Load | TranOH3phDelta | Contractor | [6 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-07 | 2020 |  | #N/A
J2002.002507 |  | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_722 | 510722 | 2020-02-08 07:17 | 2020-02-08 12:27 | 309.87 | 7 | 2 | 2014.6 | 4 | DETERIORATION | 12 | POLE | ARDMORE | 518 R SW. | CMI_PLANNED | YES | NO | NO | 861858 | 77689 | 23604 | 4517 | 985 | 0.0023375 | 8.122e-06 | 287.8 | 1 | 308 | Load | 3981 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | #N/A
J2002.002512 | PD-02082020-00009 | METRO NORTH | NORTH | 8347:WILSHIRE | WILSHIRE_4722 | 834722 | 2020-02-08 07:53 | 2020-02-08 09:17 | 83.77 | 9 | 12 | 716.85 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2800 PEMBROKE TR | CMI_NORMAL | NO | NO | NO | 861858 | 168321 | 148484 | 4624 | 1590 | 0.00083175 | 1.0443e-05 | 79.65 | 1 | 310 | Load | 24357 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | OK - 2021
J2002.002511 |  | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5621 | 865621 | 2020-02-08 07:57 | 2020-02-08 13:16 | 318.5 | 1 | 0 | 314.4167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | N, PROSPECT/SE 59TH | CMI_PLANNED | YES | NO | NO | 861858 | 159258 | 102225 | 2761 | 541 | 0.00036481 | 1.1603e-06 | 314.4167 | 1 | 0 | Tap | 13153 | Fuse | FuseRiser | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002520 | PD-02082020-00012 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-02-08 08:25 | 2020-02-08 10:04 | 98.68 | 4 | 6 | 383.0667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 316 NW.22 | CMI_NORMAL | NO | NO | NO | 861858 | 168321 | 148484 | 11122 | 2333 | 0.00044447 | 4.6411e-06 | 95.7667 | 1 | 310 | Load | 24227 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | OK - 2020
J2002.002523 | PD-02082020-00014 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4022 | 834022 | 2020-02-08 08:41 | 2020-02-08 09:53 | 72.32 | 3 | 2 | 202.95 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 9816 N.HORSESHOE RD | CMI_NORMAL | NO | NO | NO | 861858 | 128953 | 116166 | 10845 | 1369 | 0.00023548 | 3.4809e-06 | 67.65 | 1 | 310 | Load | 47701 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002524 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2525 | 912525 | 2020-02-08 08:43 | 2020-02-08 14:14 | 330.62 | 1 | 1 | 326.0333 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 4401 SAVANNAH | CMI_PLANNED | YES | NO | NO | 861858 | 82310 | 61250 | 2740 | 198 | 0.00037829 | 1.1603e-06 | 326.0333 | 1 | 308 | Mainline | 4537 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | Ark - Series 2
J2002.002525 |  | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3024 | 743024 | 2020-02-08 08:47 | 2020-02-08 10:10 | 83.55 | 7 | 4 | 520.3333 | 4 | DETERIORATION | 12 | POLE | SHAWNEE | 211 E.MAIN | CMI_PLANNED | YES | NO | NO | 861858 | 114489 | 22132 | 6652 | 1641 | 0.00060373 | 8.122e-06 | 74.3333 | 1 | 308 | Load | 2074 | Load | Tran3phWye | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002528 | PD-02082020-00016 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5031 | 865031 | 2020-02-08 08:51 | 2020-02-08 09:24 | 32.87 | 1597 | 904 | 52488.0667 | 13 | PREMATURE FAILURE | 56 | SCADA - LOCKOUT | MIDWEST CITY | 8346 SE 15TH | CMI_NORMAL | NO | NO | NO | 861858 | 114489 | 71254 | 8633 | 1597 | 0.060901 | 0.001853 | 32.8667 | 1 | 310 | Feeder | GLENDALE_5031 | Recloser | SubRecloser | [7 empty] | Equipment | N | SUBSTATION | 138kV | 2020-02-08 | 2020 |  | OK - 2022
J2002.002530 | PD-02082020-00018 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3922 | 833922 | 2020-02-08 09:01 | 2020-02-08 10:44 | 103.17 | 12 | 10 | 981.8 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 4200 NW.54 | CMI_NORMAL | NO | NO | NO | 861858 | 168321 | 148484 | 7853 | 1636 | 0.0011392 | 1.3923e-05 | 81.8167 | 1 | 310 | Load | 21070 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | OK - 2022
J2002.002531 | PD-02082020-00020 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2122 | 822122 | 2020-02-08 09:03 | 2020-02-08 12:36 | 212.85 | 2 | 4 | 79.75 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 4212 NW.22 | CMI_NORMAL | NO | NO | NO | 861858 | 168321 | 148484 | 9250 | 1837 | 9.2533e-05 | 2.3206e-06 | 39.875 | 1 | 310 | Secondary | 27119 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | OK - 2020
J2002.002532 | PD-02082020-00021 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-02-08 09:03 | 2020-02-08 10:21 | 77.75 | 1 | 1 | 77.75 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DEL CITY | 4213 SE.25 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159258 | 102225 | 7422 | 2240 | 9.0212e-05 | 1.1603e-06 | 77.75 | 1 | 310 | Customer | 4647 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | OK - 2022
J2002.002545 | PD-02082020-00028 | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-02-08 09:11 | 2020-02-08 10:34 | 82.9 | 2 | 2 | 160.4333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | TISHOMINGO | 1.7W WEST INN - RAVIA | CMI_NORMAL | NO | NO | NO | 861858 | 77689 | 7202 | 2191 | 1672 | 0.00018615 | 2.3206e-06 | 80.2167 | 1 | 310 | Load | 19329 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002538 | PD-02082020-00025 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3624 | 853624 | 2020-02-08 09:13 | 2020-02-08 10:13 | 59.82 | 1 | 1 | 11.0667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1501 E RENO | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168321 | 148484 | 5933 | 932 | 1.284e-05 | 1.1603e-06 | 11.0667 | 1 | 310 | Load | 25250 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002539 | PD-02082020-00024 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6125 | 836125 | 2020-02-08 09:18 | 2020-02-08 10:07 | 49.33 | 1 | 1 | 43.4333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 312 NW.21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168321 | 148484 | 11122 | 2333 | 5.0395e-05 | 1.1603e-06 | 43.4333 | 1 | 310 | Customer | 3641 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | OK - 2020
J2002.002541 |  | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3729 | 833729 | 2020-02-08 09:22 | 2020-02-08 09:22 | 0 | 1588 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 8423 N CLASSEN BLVD | CMI_MOMENTARY | YES | NO | NO | 861858 | 168321 | 148484 | 5768 | 1401 | 0 | 0.0018425 | 0 | 1 | 0 | Feeder | 84th ST_3729 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-08 | 2020 |  | OK - 2021
J2002.002542 | PD-02082020-00026 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5134 | 815134 | 2020-02-08 09:22 | 2020-02-08 10:58 | 95.73 | 1 | 1 | 95.7333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 9300 S. Western | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159258 | 102225 | 13940 | 2469 | 0.00011108 | 1.1603e-06 | 95.7333 | 1 | 310 | Load | 379621 | Load | Tran3phWye | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002543 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4524 | 824524 | 2020-02-08 09:24 | 2020-02-08 09:24 | 0.02 | 290 | 0 | 4.8333 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 202 N COUNCIL RD | CMI_MOMENTARY | YES | NO | NO | 861858 | 128953 | 116166 | 3411 | 290 | 5.608e-06 | 0.00033648 | 0.016667 | 1 | 0 | Feeder | COUNCIL_4524 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002544 |  | METRO EAST | SHAWNEE | 7432:ST GREGORY | ST_GREGORY_3224 | 743224 | 2020-02-08 09:25 | 2020-02-08 09:38 | 13.4 | 1 | 1 | 13.4 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SHAWNEE | 3908 N.AYDELOTTE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 114489 | 22132 | 4095 | 1374 | 1.5548e-05 | 1.1603e-06 | 13.4 | 1 | 310 | Customer | 6955 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002547 |  | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2225 | 832225 | 2020-02-08 09:32 | 2020-02-08 09:32 | 0 | 2040 | 0 | 0 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 2800 NW 38TH ST | CMI_MOMENTARY | YES | NO | NO | 861858 | 168321 | 148484 | 9179 | 2040 | 0 | 0.002367 | 0 | 1 | 0 | Feeder | 38TH ST_2225 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | OK - 2021
J2002.002553 | PD-02082020-00030 | NORTHEAST | SAPULPA | 7632:OAK GROVE | OAK_GROVE_3221 | 763221 | 2020-02-08 09:32 | 2020-02-08 10:22 | 49.5 | 1 | 1 | 46.2667 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | DRUMRIGHT | W OF TOWN | CMI_NORMAL | NO | NO | NO | 861858 | 74141 | 40825 | 1020 | 1020 | 5.3682e-05 | 1.1603e-06 | 46.2667 | 1 | 310 | Load | 40010 | Load | Tran3phWye | NICHOLAS MANION | 918-290-1327 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | OK - 2021
J2002.002552 | PD-02082020-00031 | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-02-08 09:34 | 2020-02-08 11:25 | 111.47 | 1 | 1 | 104.0333 | 4 | DETERIORATION | 50 | CONNECTOR | EL RENO | 117 N.M | CMI_NORMAL | NO | NO | NO | 861858 | 128953 | 12787 | 6965 | 1830 | 0.00012071 | 1.1603e-06 | 104.0333 | 1 | 310 | Customer | 41597 | Load | Tran1phOH | ERIC S KAPPUS | 405-642-1454 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002554 |  | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2225 | 832225 | 2020-02-08 09:35 | 2020-02-08 09:36 | 0.32 | 2040 | 0 | 646 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 2800 NW 38TH ST | CMI_MOMENTARY | YES | NO | NO | 861858 | 168321 | 148484 | 9179 | 2040 | 0.00074954 | 0.002367 | 0.31667 | 1 | 0 | Feeder | 38TH ST_2225 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | OK - 2021
J2002.002561 |  | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4823 | 824823 | 2020-02-08 10:10 | 2020-02-08 11:37 | 87.13 | 6 | 1 | 483.5 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 3001 SW.25 | CMI_NORMAL | NO | NO | NO | 861858 | 168321 | 148484 | 4202 | 1797 | 0.000561 | 6.9617e-06 | 80.5833 | 1 | 308 | Load | 17693 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | OK - 2021
J2002.002565 |  | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4121 | 814121 | 2020-02-08 10:28 | 2020-02-08 10:31 | 3.65 | 1 | 1 | 3.65 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 707 SW.50 | CMI_MOMENTARY | YES | NO | NO | 861858 | 159258 | 102225 | 5810 | 1200 | 4.235e-06 | 1.1603e-06 | 3.65 | 1 | 310 | Customer | 7151 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | #N/A
J2002.002569 |  | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5031 | 865031 | 2020-02-08 10:34 | 2020-02-08 10:41 | 7.08 | 1 | 1 | 7.0833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 463 HARR DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 114489 | 71254 | 8633 | 1597 | 8.2187e-06 | 1.1603e-06 | 7.0833 | 1 | 310 | Customer | 45385 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | OK - 2022
J2002.002570 |  | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2625 | 862625 | 2020-02-08 10:36 | 2020-02-08 19:45 | 549.57 | 1 | 0 | 522.1833 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | 2524 SE.15 | CMI_PLANNED | YES | NO | NO | 861858 | 159258 | 102225 | 7422 | 1269 | 0.00060588 | 1.1603e-06 | 522.1833 | 1 | 0 | Load | 56981 | Load | TranOH3phDelta | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | OK - 2022
J2002.002574 |  | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_823 | 870823 | 2020-02-08 10:42 | 2020-02-08 10:49 | 6.88 | 1 | 1 | 6.8833 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 2813 DEWEY AVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159258 | 57033 | 6776 | 2379 | 7.9866e-06 | 1.1603e-06 | 6.8833 | 1 | 310 | Customer | 89415 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002581 | PD-02082020-00038 | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-02-08 10:57 | 2020-02-08 14:13 | 196.03 | 1 | 3 | 170.8833 | 13 | PREMATURE FAILURE | 15 | METER - SECONDARY | BIXBY | PECAN PARK BETWEEN L37+38 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861858 | 74141 | 40825 | 2755 | 1443 | 0.00019827 | 1.1603e-06 | 170.8833 | 1 | 310 | Customer | 43105 | Load | Tran1phOH | JOSHUA N MCKINNEY | 918-863-6313 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | OK - 2021
J2002.002585 | PD-02082020-00040 | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2129 | 332129 | 2020-02-08 11:16 | 2020-02-08 15:24 | 248.33 | 1 | 1 | 248.3333 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | FORT GIBSON | ELEMENTARY SCHOOL | CMI_NORMAL | NO | NO | NO | 861858 | 74141 | 33316 | 3337 | 942 | 0.00028814 | 1.1603e-06 | 248.3333 | 1 | 320 | Load | 21188 | Load | Tran3phPadWye | NORTHEAST BOUG | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-08 | 2020 |  | #N/A
J2002.002588 | PD-02082020-00041 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9924 | 829924 | 2020-02-08 11:23 | 2020-02-08 13:36 | 133.03 | 6 | 6 | 779.8 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | BETHANY | 1900 ROLLING-RIDGE | CMI_NORMAL | NO | NO | NO | 861858 | 128953 | 116166 | 9243 | 1485 | 0.00090479 | 6.9617e-06 | 129.9667 | 1 | 310 | Load | 38481 | Load | Tran1phOH | CONTRACTOR C-BHI15 DAVID ELLIOT INC | 580-614-1404 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002587 | PD-02082020-00042 | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1022 | 311022 | 2020-02-08 11:26 | 2020-02-08 16:05 | 278.7 | 3 | 4 | 728 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | MUSKOGEE | L 6 BLK 1 RIVEROAKS II | CMI_NORMAL | NO | NO | NO | 861858 | 74141 | 33316 | 2906 | 1093 | 0.00084469 | 3.4809e-06 | 242.6667 | 1 | 310 | Mainline | 25840 | Fuse | FuseRiser | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | #N/A
J2002.002590 | PD-02082020-00043 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_861 | 830861 | 2020-02-08 11:31 | 2020-02-08 16:03 | 272.07 | 1 | 1 | 263.0167 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 5209 NW 161st Te | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861858 | 168321 | 148484 | 19409 | 3948 | 0.00030517 | 1.1603e-06 | 263.0167 | 1 | 320 | Customer | 357249 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002593 |  | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3622 | 853622 | 2020-02-08 11:43 | 2020-02-08 11:48 | 5.33 | 1 | 1 | 5.3333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 409 TINKER-DIAG | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168321 | 148484 | 5933 | 965 | 6.1882e-06 | 1.1603e-06 | 5.3333 | 1 | 310 | Customer | 45247 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002599 | PD-02082020-00046 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-02-08 11:53 | 2020-02-08 13:12 | 79.15 | 1 | 2 | 79.15 | 3 | DAMAGED BY PUBLIC | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 2213 SW.50 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159258 | 102225 | 7610 | 2463 | 9.1836e-05 | 1.1603e-06 | 79.15 | 1 | 311 | Customer | 36540 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | #N/A
J2002.002600 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3821 | 913821 | 2020-02-08 12:08 | 2020-02-08 12:08 | 0 | 209 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | FT SMITH | 1904 SOUTH 7TH ST | CMI_MOMENTARY | YES | NO | NO | 861858 | 82310 | 61250 | 2941 | 209 | 0 | 0.0002425 | 0 | 1 | 0 | Feeder | ARKOMA_3821 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-02-08 | 2020 |  | Ark - Series 2
J2002.002602 | PD-02082020-00047 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6961 | 846961 | 2020-02-08 12:11 | 2020-02-08 16:28 | 256.58 | 1 | 1 | 244.8667 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | WALKER + NW.142 BLK.1 LOT B | CMI_NORMAL | NO | NO | NO | 861858 | 168321 | 148484 | 7731 | 1389 | 0.00028411 | 1.1603e-06 | 244.8667 | 1 | 320 | Customer | 69416 | Load | Tran1phPad | BRIAN E WHITE | 405-642-7075 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002604 | PD-02082020-00049 | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3821 | 913821 | 2020-02-08 12:15 | 2020-02-08 13:11 | 55.58 | 1 | 1 | 55.5833 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 23 | FUSE - PRIMARY | FORT SMITH | POST OFFICE PADMOUNT | CMI_NORMAL | NO | NO | NO | 861858 | 82310 | 61250 | 2941 | 209 | 6.4492e-05 | 1.1603e-06 | 55.5833 | 1 | 310 | Customer | 18198 | Load | Tran3phPadWye | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-02-08 | 2020 |  | Ark - Series 2
J2002.002606 | PD-02082020-00051 | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_628 | 550628 | 2020-02-08 12:28 | 2020-02-08 13:40 | 72.38 | 1 | 1 | 72.3833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DURANT | BRIARWOOD APTS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 77689 | 15514 | 6747 | 962 | 8.3985e-05 | 1.1603e-06 | 72.3833 | 1 | 310 | Customer | 16544 | Load | Tran1phPad | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002608 |  | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3622 | 853622 | 2020-02-08 12:33 | 2020-02-08 12:36 | 3.9 | 1 | 1 | 3.9 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 409 TINKER-DIAG | CMI_MOMENTARY | YES | NO | NO | 861858 | 168321 | 148484 | 5933 | 965 | 4.5251e-06 | 1.1603e-06 | 3.9 | 1 | 310 | Customer | 45247 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002611 |  | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2625 | 862625 | 2020-02-08 13:01 | 2020-02-08 19:43 | 402.82 | 25 | 12 | 9431.0417 | 28 | OTHER (DESCRIBE) | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | GENESEE / .1MS SE.15TH | CMI_PLANNED | YES | NO | NO | 861858 | 159258 | 102225 | 7422 | 1269 | 0.010943 | 2.9007e-05 | 377.2417 | 1 | 310 | Mainline | 18260 | Fuse | FuseOH | [7 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | OK - 2022
J2002.002612 |  | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4121 | 814121 | 2020-02-08 13:04 | 2020-02-08 13:04 | 0 | 252 | 0 | 0 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 824 SW 51ST ST | CMI_MOMENTARY | YES | NO | NO | 861858 | 159258 | 102225 | 5810 | 1200 | 0 | 0.00029239 | 0 | 1 | 0 | Mainline | 337540 | Recloser | Rec3phElectronic | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | #N/A
J2002.002613 |  | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4121 | 814121 | 2020-02-08 13:04 | 2020-02-08 13:04 | 0 | 175 | 0 | 0 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 824 SW 51ST ST | CMI_MOMENTARY | YES | NO | NO | 861858 | 159258 | 102225 | 5810 | 1200 | 0 | 0.00020305 | 0 | 1 | 0 | Mainline | 337540 | Recloser | Rec3phElectronic | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | #N/A
J2002.002614 | PD-02082020-00057 | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_521 | 530521 | 2020-02-08 13:10 | 2020-02-08 14:15 | 64.52 | 1 | 1 | 81.5167 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | HEALDTON | HICKORY + LAKEVIEW | CMI_NORMAL | NO | NO | NO | 861858 | 77689 | 6808 | 2130 | 1261 | 9.4582e-05 | 1.1603e-06 | 81.5167 | 1 | 320 | Load | 26459 | Load | Tran1phPad | JOE LOFTIS | 918-884-5349 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | OK - 2020
J2002.002615 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-08 13:13 | 2020-02-08 17:03 | 230.15 | 7 | 3 | 899.5583 | 4 | DETERIORATION | 12 | POLE | LAMAR | LAMAR AR 72846 | CMI_PLANNED | YES | NO | NO | 861858 | 82310 | 7551 | 730 | 0 | 0.0010437 | 8.122e-06 | 128.5083 | 1 | 308 | Load | 7003 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | #N/A
J2002.002620 | PD-02082020-00061 | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2821 | 312821 | 2020-02-08 13:30 | 2020-02-08 17:34 | 244.2 | 1 | 1 | 244.2 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 1207 FOXCROFT CI 6 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 74141 | 33316 | 5286 | 1153 | 0.00028334 | 1.1603e-06 | 244.2 | 1 | 310 | Customer | 2419 | Load | Tran1phOH | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-08 | 2020 |  | #N/A
J2002.002623 | PD-02082020-00062 | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2129 | 332129 | 2020-02-08 13:35 | 2020-02-08 15:33 | 117.57 | 1 | 1 | 117.5667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT GIBSON | FT GIBSON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 74141 | 33316 | 3337 | 942 | 0.00013641 | 1.1603e-06 | 117.5667 | 1 | 310 | Customer | 14496 | Load | Tran1phOH | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-08 | 2020 |  | #N/A
J2002.002624 | PD-02082020-00059 | SOUTHERN | HEALDTON | 5322:DUNDEE | DUNDEE 22 | 532222 | 2020-02-08 13:39 | 2020-02-08 14:00 | 21.17 | 1 | 1 | 21.1667 | 4 | DETERIORATION | 27 | CUTOUT | HEALDTON | 8-TX 1N 6W 4N .1W SS | CMI_NORMAL | NO | NO | NO | 861858 | 77689 | 6808 | 1015 | 1004 | 2.4559e-05 | 1.1603e-06 | 21.1667 | 1 | 310 | Load | 11026 | Load | Tran3phWye | ROBERT J BEARDSLEE | 580-618-2506 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002625 | PD-02082020-00060 | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1623 | 581623 | 2020-02-08 13:43 | 2020-02-08 17:42 | 238.98 | 1 | 2 | 207.1167 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | ADA | 1308 S.JOHNSTON | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861858 | 77689 | 11523 | 3463 | 1654 | 0.00024031 | 1.1603e-06 | 207.1167 | 1 | 310 | Customer | 13345 | Load | Tran1phOH | CAMERON BRADY | 580-307-7052 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002627 |  | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_724 | 510724 | 2020-02-08 13:46 | 2020-02-08 16:05 | 138.38 | 9 | 7 | 947.55 | 4 | DETERIORATION | 12 | POLE | ARDMORE | 1024 BIXBY | CMI_PLANNED | YES | NO | NO | 861858 | 77689 | 23604 | 4517 | 1630 | 0.0010994 | 1.0443e-05 | 105.2833 | 1 | 308 | Load | 898 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | #N/A
J2002.002628 |  | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3622 | 853622 | 2020-02-08 13:48 | 2020-02-08 13:59 | 11.5 | 1 | 1 | 11.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 411 TINKER-DIAG | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168321 | 148484 | 5933 | 965 | 1.3343e-05 | 1.1603e-06 | 11.5 | 1 | 310 | Customer | 45242 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002638 | PD-02082020-00067 | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1224 | 911224 | 2020-02-08 14:41 | 2020-02-08 15:45 | 63.67 | 1 | 1 | 63.6667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 1125 N.34 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 82310 | 61250 | 6608 | 1804 | 7.3871e-05 | 1.1603e-06 | 63.6667 | 1 | 310 | Customer | 6234 | Load | Tran1phOH | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | Ark - Series 1
J2002.002642 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2525 | 912525 | 2020-02-08 15:16 | 2020-02-08 17:41 | 144.67 | 2 | 2 | 289.3526 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 5021 OLD GREENWOOD RD | CMI_PLANNED | YES | NO | NO | 861858 | 82310 | 61250 | 2740 | 198 | 0.00033573 | 2.3206e-06 | 144.6763 | 1 | 308 | Load | 8385 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | Ark - Series 2
J2002.002651 | PD-02082020-00069 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2122 | 822122 | 2020-02-08 15:26 | 2020-02-08 20:46 | 320.45 | 6 | 7 | 1751.1 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 2865 N.ANN DR | CMI_NORMAL | NO | NO | NO | 861858 | 168321 | 148484 | 9250 | 1837 | 0.0020318 | 6.9617e-06 | 291.85 | 1 | 310 | Load | 24139 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | OK - 2020
J2002.002648 |  | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3622 | 853622 | 2020-02-08 15:28 | 2020-02-08 15:33 | 4.38 | 1 | 1 | 4.3833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 409 TINKER-DIAG | CMI_MOMENTARY | YES | NO | NO | 861858 | 168321 | 148484 | 5933 | 965 | 5.0859e-06 | 1.1603e-06 | 4.3833 | 1 | 310 | Customer | 45247 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002653 | PD-02082020-00071 | SOUTHERN | ADA | 5813:BYNG SPA | BYNG_SPA_1322 | 581322 | 2020-02-08 15:44 | 2020-02-08 18:46 | 181.98 | 1 | 1 | 124.725 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | BYNG | 611 S MAIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 77689 | 11523 | 546 | 546 | 0.00014472 | 1.1603e-06 | 124.725 | 1 | 320 | Customer | 418276 | Load | Tran1phOH | CAMERON BRADY | 580-307-7052 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | #N/A
J2002.002658 | PD-02082020-00072 | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9869 | 839869 | 2020-02-08 16:43 | 2020-02-08 17:55 | 72.18 | 1 | 1 | 72.1833 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 2312 Pueblos Rd | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861858 | 168321 | 148484 | 10667 | 3002 | 8.3753e-05 | 1.1603e-06 | 72.1833 | 1 | 320 | Customer | 393567 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | OK - 2022
J2002.002664 | PD-02082020-00073 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1222 | 831222 | 2020-02-08 17:16 | 2020-02-08 18:55 | 99.07 | 50 | 50 | 4442.5 | 28 | OTHER (DESCRIBE) | 23 | FUSE - PRIMARY | OKLAHOMA CITY | NW.59 + WS-VILLA | CMI_NORMAL | NO | NO | NO | 861858 | 168321 | 148484 | 7754 | 1009 | 0.0051546 | 5.8014e-05 | 88.85 | 1 | 310 | Tap | 19208 | Fuse | FuseOH | ROBERT HALL | 405-757-9640 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | OK - 2021
J2002.002661 |  | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1724 | 831724 | 2020-02-08 17:17 | 2020-02-08 17:26 | 8.43 | 1 | 1 | 8.4333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2301 NW.122 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168321 | 148484 | 6648 | 2778 | 9.7851e-06 | 1.1603e-06 | 8.4333 | 1 | 310 | Customer | 75067 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002669 |  | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-02-08 17:39 | 2020-02-08 17:39 | 0 | 1 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | 0 | SS Russett Sub | CMI_MOMENTARY | YES | NO | NO | 861858 | 77689 | 7202 | 2191 | 1672 | 0 | 1.1603e-06 | 0 | 1 | 0 | Mainline | 366150 | Recloser | Rec3phElectronic | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002671 | PD-02082020-00076 | SOUTHERN | DURANT | 5512:COLBERT | COLBERT_1221 | 551221 | 2020-02-08 17:47 | 2020-02-08 19:48 | 120.92 | 1 | 1 | 107.5667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | COLBERT | SOUTH OF CALERA | CMI_NORMAL | NO | NO | NO | 861858 | 77689 | 15514 | 2173 | 897 | 0.00012481 | 1.1603e-06 | 107.5667 | 1 | 310 | Load | 25844 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002670 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6961 | 846961 | 2020-02-08 17:47 | 2020-02-08 20:08 | 140.98 | 722 | 483 | 100502.4 | 3 | DAMAGED BY PUBLIC | 12 | POLE | OKLAHOMA CITY | N WALKER AVE & W MEMORIAL RD | CMI_PLANNED | YES | NO | NO | 861858 | 168321 | 148484 | 7731 | 1389 | 0.11661 | 0.00083773 | 139.2 | 1 | 310 | Mainline | 406600 | Recloser | Rec3phElectronic | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002676 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_866 | 830866 | 2020-02-08 17:47 | 2020-02-08 22:44 | 297.07 | 1 | 3 | 139.1833 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1/2BS-NW.148 + LONGFORD WAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168321 | 148484 | 19409 | 4304 | 0.00016149 | 1.1603e-06 | 139.1833 | 1 | 310 | Customer | 85398 | Load | Tran1phPad | Crew | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002672 | PD-02082020-00075 | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3722 | 913722 | 2020-02-08 17:48 | 2020-02-08 18:42 | 53.8 | 1 | 1 | 53.8 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 5801 KINKEAD AV HLD1 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 82310 | 61250 | 4573 | 1442 | 6.2423e-05 | 1.1603e-06 | 53.8 | 1 | 310 | Customer | 20 | Load | Tran1phPad | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | Ark - Series 3
J2002.002679 |  | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2224 | 832224 | 2020-02-08 18:01 | 2020-02-08 18:12 | 10.87 | 1 | 1 | 10.8667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3741 NW.29 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168321 | 148484 | 9179 | 1431 | 1.2608e-05 | 1.1603e-06 | 10.8667 | 1 | 310 | Customer | 28207 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | #N/A
J2002.002684 |  | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_523 | 320523 | 2020-02-08 18:11 | 2020-02-08 18:26 | 15.48 | 1 | 1 | 15.4833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SAPULPA | SHADY GROVE M/H PK:BLK A.LOT32 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 74149 | 40830 | 3856 | 1730 | 1.7965e-05 | 1.1603e-06 | 15.4833 | 1 | 310 | Customer | 43857 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-08 | 2020 |  | OK - 2022
J2002.002686 | PD-02082020-00080 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1928 | 851928 | 2020-02-08 18:22 | 2020-02-08 19:04 | 41.55 | 1 | 1 | 41.55 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 9704 NE.4 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 114496 | 71251 | 12468 | 2020 | 4.821e-05 | 1.1603e-06 | 41.55 | 1 | 310 | Customer | 45285 | Load | Tran1phPad | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002689 | PD-02082020-00083 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5132 | 815132 | 2020-02-08 19:03 | 2020-02-08 20:57 | 114.32 | 90 | 117 | 9223.5 | 4 | DETERIORATION | 17 | JUMPER | OKLAHOMA CITY | SS SW 74 WS LINN | CMI_NORMAL | NO | NO | NO | 861858 | 159261 | 102225 | 13940 | 2002 | 0.010702 | 0.00010443 | 102.4833 | 1 | 310 | Mainline | 13091 | Fuse | FuseOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002692 | PD-02082020-00084 | SOUTHERN | SULPHUR | 5705:SULPHUR | SULPHUR_523 | 570523 | 2020-02-08 19:09 | 2020-02-08 21:24 | 134.9 | 44 | 16 | 5513.2 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 23 | FUSE - PRIMARY | SULPHUR | 4TH + MUSKOGEE N SIDE | CMI_NORMAL | NO | NO | NO | 861858 | 77688 | 6817 | 3635 | 1089 | 0.0063969 | 5.1052e-05 | 125.3 | 1 | 310 | Mainline | 10192 | Fuse | FuseOH | BRUCE E BEAM | 405-626-0490 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | OK - 2021
J2002.002704 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6961 | 846961 | 2020-02-08 20:18 | 2020-02-08 20:32 | 13.92 | 3 | 3 | 35.5833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 413 NW.140 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168321 | 148484 | 7731 | 1389 | 4.1287e-05 | 3.4809e-06 | 11.8611 | 1 | 310 | Customer | 87931 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002707 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6961 | 846961 | 2020-02-08 20:32 | 2020-02-08 20:36 | 4.25 | 1 | 1 | 4.25 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | BEHIND 600 NW 143RD ST | CMI_MOMENTARY | YES | NO | NO | 861858 | 168321 | 148484 | 7731 | 1389 | 4.9312e-06 | 1.1603e-06 | 4.25 | 1 | 310 | Customer | 69415 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002708 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6961 | 846961 | 2020-02-08 20:36 | 2020-02-08 20:42 | 5.87 | 1 | 1 | 5.8667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | L10,B2-OAKMOND ADDN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168321 | 148484 | 7731 | 1389 | 6.807e-06 | 1.1603e-06 | 5.8667 | 1 | 310 | Customer | 85942 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002711 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6961 | 846961 | 2020-02-08 20:55 | 2020-02-08 20:59 | 3.93 | 1 | 1 | 3.9333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | L7,B3-OAKMOND ADDN | CMI_MOMENTARY | YES | NO | NO | 861858 | 168321 | 148484 | 7731 | 1389 | 4.5638e-06 | 1.1603e-06 | 3.9333 | 1 | 310 | Customer | 88093 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002717 | PD-02082020-00100 | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1724 | 831724 | 2020-02-08 21:40 | 2020-02-08 22:46 | 65.52 | 1 | 1 | 65.5167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2301 NW.122 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168321 | 148484 | 6649 | 2779 | 7.6018e-05 | 1.1603e-06 | 65.5167 | 1 | 310 | Customer | 75067 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002718 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5132 | 815132 | 2020-02-08 21:47 | 2020-02-08 22:22 | 34.98 | 1 | 1 | 34.9833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 7900 S.SHERWOOD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159261 | 102225 | 13940 | 2002 | 4.0591e-05 | 1.1603e-06 | 34.9833 | 1 | 310 | Customer | 17689 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002734 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6961 | 846961 | 2020-02-08 23:02 | 2020-02-08 23:12 | 9.28 | 1 | 1 | 9.2833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | IN ALLEY BEHIND | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168321 | 148484 | 7731 | 1389 | 1.0771e-05 | 1.1603e-06 | 9.2833 | 1 | 310 | Customer | 69408 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-08 | 2020 |  | #N/A
J2002.002738 |  | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_523 | 320523 | 2020-02-09 01:08 | 2020-02-09 01:22 | 13.8 | 1 | 1 | 13.8 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SAPULPA | 1109 S.MAIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 74149 | 40830 | 3856 | 1730 | 1.6012e-05 | 1.1603e-06 | 13.8 | 1 | 310 | Customer | 40037 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-09 | 2020 |  | OK - 2022
J2002.002748 |  | ARKANSAS | OZARK | 9412:ALTUS | ALTUS_1229 | 941229 | 2020-02-09 03:19 | 2020-02-09 03:19 | 0 | 866 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OZARK | 6007 GRAVEL RD | CMI_MOMENTARY | YES | NO | NO | 861858 | 82318 | 7555 | 866 | 866 | 0 | 0.0010048 | 0 | 1 | 0 | Feeder | ALTUS_1229 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-02-09 | 2020 |  | Ark - Series 2
J2002.002749 |  | NORTHWEST | ENID | 4220:CLYDE | CLYDE 23 | 422023 | 2020-02-09 03:26 | 2020-02-09 03:35 | 8.97 | 1 | 1 | 8.9667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | WAKITA | N-SPRUCE,BTWN PINE+COTTONWOOD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 53588 | 37628 | 417 | 375 | 1.0404e-05 | 1.1603e-06 | 8.9667 | 1 | 310 | Customer | 7637 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-09 | 2020 |  | #N/A
J2002.002753 | PD-02092020-00004 | ARKANSAS | OZARK | 9412:ALTUS | ALTUS_1229 | 941229 | 2020-02-09 04:19 | 2020-02-09 05:40 | 80.9 | 1 | 1 | 80.9 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OZARK | W-ALTUS, N-CENTER CROSS SCHOOL | CMI_NORMAL | NO | NO | NO | 861858 | 82318 | 7555 | 866 | 866 | 9.3867e-05 | 1.1603e-06 | 80.9 | 1 | 310 | Load | 17604 | Load | Tran1phOH | TRAVIS EARNHART | 479-719-2561 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-09 | 2020 |  | Ark - Series 2
J2002.002759 |  | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_523 | 320523 | 2020-02-09 05:03 | 2020-02-09 05:10 | 6.98 | 1 | 1 | 6.9833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SAPULPA | 1109 S.MAIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 74149 | 40830 | 3856 | 1730 | 8.1026e-06 | 1.1603e-06 | 6.9833 | 1 | 310 | Customer | 40037 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-09 | 2020 |  | OK - 2022
J2002.002762 | PD-02092020-00007 | METRO WEST | WEST | 8321:PIEDMONT | PIEDMONT_2169 | 832169 | 2020-02-09 06:14 | 2020-02-09 11:25 | 311.22 | 5 | 6 | 1544.6667 | 22 | WIND | 17 | JUMPER | PIEDMONT | 1/2 BN ADAMS + PIEDMONT RD | CMI_NORMAL | NO | NO | NO | 861858 | 128953 | 116167 | 6308 | 1664 | 0.0017923 | 5.8014e-06 | 308.9333 | 1 | 310 | Secondary | 53984 | Load | Tran1phOH | BRADLEY SUDBECK | 405-999-6850 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002775 |  | METRO NORTH | NORTH | 8493:KELLEY AVE | KELLEY_AVENUE_9331 | 849331 | 2020-02-09 08:16 | 2020-02-09 15:08 | 411.73 | 3 | 2 | 1222.6 | 28 | OTHER (DESCRIBE) | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | .25 MN of Britton & Kelly on ES of Kelly | CMI_PLANNED | YES | NO | NO | 861858 | 168321 | 148484 | 1482 | 1060 | 0.0014186 | 3.4809e-06 | 407.5333 | 1 | 308 | Tap | 307882 | Fuse | FuseRiser | [7 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002783 | PD-02092020-00013 | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5822 | 845822 | 2020-02-09 08:17 | 2020-02-09 11:46 | 209.07 | 4 | 6 | 807.9333 | 22 | WIND | 17 | JUMPER | SPENCER | .4MWDOUGLAS + NE.50 | CMI_NORMAL | NO | NO | NO | 861858 | 114496 | 71251 | 2984 | 935 | 0.00093743 | 4.6411e-06 | 201.9833 | 1 | 310 | Tap | 21096 | Fuse | FuseOH | DAVID M CLEMMONS | 405-777-8355 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-09 | 2020 |  | #N/A
J2002.002776 |  | METRO NORTH | NORTH | 8493:KELLEY AVE | KELLEY_AVENUE_9331 | 849331 | 2020-02-09 08:17 | 2020-02-09 15:08 | 410.48 | 1 | 1 | 276.85 | 28 | OTHER (DESCRIBE) | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | 9801 N KELLEY | CMI_PLANNED | YES | NO | NO | 861858 | 168321 | 148484 | 1482 | 1060 | 0.00032122 | 1.1603e-06 | 276.85 | 1 | 308 | Tap | 226658 | Fuse | FuseRiser | [7 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002778 | PD-02092020-00011 | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1373 | 831373 | 2020-02-09 08:19 | 2020-02-09 10:21 | 121.92 | 1 | 1 | 99.7833 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 10528 NW 35th St | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861858 | 128953 | 116167 | 7913 | 4122 | 0.00011578 | 1.1603e-06 | 99.7833 | 1 | 320 | Customer | 360012 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002777 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2525 | 912525 | 2020-02-09 08:20 | 2020-02-09 10:30 | 130.12 | 2 | 2 | 252.6 | 4 | DETERIORATION | 28 | CROSSARM | FORT SMITH | 4520 S.PHOENIX | CMI_PLANNED | YES | NO | NO | 861858 | 82318 | 61253 | 2740 | 198 | 0.00029309 | 2.3206e-06 | 126.3 | 1 | 308 | Load | 9828 | Load | Tran3phWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-09 | 2020 |  | Ark - Series 2
J2002.002779 |  | METRO NORTH | NORTH | 8535:OU MED CENTER | OU_MEDICAL_CEN_3572 | 853572 | 2020-02-09 08:27 | 2020-02-09 10:15 | 108.25 | 1 | 0 | 99.0333 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | 111 N HARRISON | CMI_NORMAL | NO | NO | NO | 861858 | 168321 | 148484 | 525 | 499 | 0.00011491 | 1.1603e-06 | 99.0333 | 1 | 0 | Load | 257347 | Load | Tran3phPadWye | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002781 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3829 | 913829 | 2020-02-09 08:30 | 2020-02-09 09:37 | 67.42 | 1 | 0 | 52.2333 | 4 | DETERIORATION | 4 | SWITCH - OIL | FORT SMITH | 1011 S. Y ST | CMI_PLANNED | YES | NO | NO | 861858 | 82318 | 61253 | 2941 | 1188 | 6.0605e-05 | 1.1603e-06 | 52.2333 | 1 | 0 | Load | 331923 | Load | Tran3phWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-09 | 2020 |  | Ark - Series 2
J2002.002785 | PD-02092020-00014 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2222 | 832222 | 2020-02-09 08:31 | 2020-02-09 10:58 | 147.12 | 9 | 9 | 1309.05 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2333 NW.38 | CMI_NORMAL | NO | NO | NO | 861858 | 168321 | 148484 | 9179 | 1557 | 0.0015189 | 1.0443e-05 | 145.45 | 1 | 310 | Load | 4341 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Other | N | DISTRIBUTION | 69kV | 2020-02-09 | 2020 |  | OK - 2022
J2002.002789 | PD-02092020-00015 | METRO SOUTH | SOUTH | 8726:NOBLE | NOBLE_2621 | 872621 | 2020-02-09 09:02 | 2020-02-09 14:23 | 321.05 | 1 | 3 | 2.4333 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | NOBLE | 604 CONDOR CT | CMI_NORMAL | NO | NO | NO | 861858 | 159261 | 57036 | 2967 | 1446 | 2.8234e-06 | 1.1603e-06 | 2.4333 | 1 | 320 | Customer | 67032 | Load | Tran1phOH | DAVID M CLEMMONS | 405-777-8355 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002794 | PD-02092020-00017 | NORTHEAST | MUSKOGEE | 3326:JAMESVILLE | JAMESVILLE_2621 | 332621 | 2020-02-09 09:13 | 2020-02-09 11:02 | 109.1 | 1 | 1 | 102.7333 | 4 | DETERIORATION | 21 | FUSE - TRANSFORMER | BALD HILL | 1/2 MILE WEST JAMESVILLE "Y" | CMI_NORMAL | NO | NO | NO | 861858 | 74149 | 33319 | 1555 | 273 | 0.0001192 | 1.1603e-06 | 102.7333 | 1 | 310 | Load | 16559 | Load | Tran1phOH | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-09 | 2020 |  | OK - 2020
J2002.002802 | PD-02092020-00020 | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_422 | 510422 | 2020-02-09 09:50 | 2020-02-09 11:00 | 70.1 | 1 | 1 | 68.9833 | 4 | DETERIORATION | 1 | TRANSFORMER UG | ARDMORE | HWY 70 1.9 E SS | CMI_NORMAL | NO | NO | NO | 861858 | 77688 | 23603 | 2319 | 1058 | 8.004e-05 | 1.1603e-06 | 68.9833 | 1 | 310 | Customer | 10986 | Load | Tran1phPad | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002805 | PD-02092020-00021 | SOUTHERN | DURANT | 5511:BOKCHITO | BOKCHITO 21 | 551121 | 2020-02-09 10:00 | 2020-02-09 13:54 | 234.08 | 1 | 1 | 167.3 | 11 | OVERLOAD | 2 | TRANSFORMER OH | BENNINGTON | .5W BENNINGTON ON HWY 70 | CMI_NORMAL | NO | NO | NO | 861858 | 77688 | 15515 | 674 | 674 | 0.00019412 | 1.1603e-06 | 167.3 | 1 | 320 | Customer | 28254 | Load | TranOpenDelta | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kv | 2020-02-09 | 2020 |  | #N/A
J2002.002809 | PD-02092020-00024 | METRO NORTH | GUTHRIE | 8813:FITZGERALD CR | FITZGERALD_CR_1342 | 881342 | 2020-02-09 10:18 | 2020-02-09 12:16 | 118.22 | 1 | 1 | 118.2167 | 22 | WIND | 21 | FUSE - TRANSFORMER | LANGSTON | 200 FT S OF W HALE ST AND 200 FT W OF N TOLSON AV | CMI_NORMAL | NO | NO | NO | 861858 | 168321 | 19837 | 1045 | 808 | 0.00013716 | 1.1603e-06 | 118.2167 | 1 | 310 | Customer | 229693 | Load | Tran3phPadWye | JOSEPH WAYNE POOL | 405-919-2253 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002811 |  | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_422 | 510422 | 2020-02-09 10:30 | 2020-02-09 10:30 | 0 | 1057 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 2510 SAM NOBLE PARKWAY | CMI_MOMENTARY | YES | NO | NO | 861858 | 77688 | 23603 | 2319 | 1058 | 0 | 0.0012264 | 0 | 1 | 0 | Feeder | FOUNDATION_422 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002814 | PD-02092020-00026 | SOUTHERN | PAULS VALLEY | 5620:PRAIRIE POINT | PRAIRIE_POINT_2021 | 562021 | 2020-02-09 10:36 | 2020-02-09 11:45 | 68.77 | 1 | 1 | 68.7667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ELMORE CITY | 24534 E CR1655 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 77688 | 6221 | 611 | 572 | 7.9789e-05 | 1.1603e-06 | 68.7667 | 1 | 310 | Load | 411425 | Load | Tran1phOH | BRUCE E BEAM | 405-626-0490 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | OK - 2021
J2002.002817 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2525 | 912525 | 2020-02-09 10:59 | 2020-02-09 13:35 | 156.32 | 1 | 1 | 138.6 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 4304 PHOENIX | CMI_PLANNED | YES | NO | NO | 861858 | 82318 | 61253 | 2740 | 198 | 0.00016082 | 1.1603e-06 | 138.6 | 1 | 308 | Mainline | 2455 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-09 | 2020 |  | Ark - Series 2
J2002.002829 | PD-02092020-00028 | SOUTHERN | SULPHUR | 5705:SULPHUR | SULPHUR_521 | 570521 | 2020-02-09 11:48 | 2020-02-09 12:54 | 65.63 | 3 | 5 | 190.9 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | SULPHUR | 302 E OKLA | CMI_NORMAL | NO | NO | NO | 861858 | 77688 | 6817 | 3635 | 757 | 0.0002215 | 3.4809e-06 | 63.6333 | 1 | 310 | Secondary | 5267 | Load | Tran1phOH | BRUCE E BEAM | 405-626-0490 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002828 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9922 | 829922 | 2020-02-09 11:58 | 2020-02-09 12:03 | 5 | 7 | 0 | 35 | 28 | OTHER (DESCRIBE) | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | 6002 NW 2ND | CMI_MOMENTARY | YES | NO | NO | 861858 | 128953 | 116167 | 9242 | 842 | 4.061e-05 | 8.122e-06 | 5 | 1 | 0 | Mainline | 32991 | Fuse | FuseRiser | [7 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002832 | PD-02092020-00029 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4823 | 824823 | 2020-02-09 12:05 | 2020-02-09 13:10 | 64.98 | 14 | 14 | 875.1167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 3024 SW.20 | CMI_NORMAL | NO | NO | NO | 861858 | 168321 | 148484 | 4202 | 1797 | 0.0010154 | 1.6244e-05 | 62.5083 | 1 | 310 | Load | 6947 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | OK - 2021
J2002.002833 | PD-02092020-00030 | NORTHWEST | ENID | 4112:CHESTNUT | CHESTNUT_1222 | 411222 | 2020-02-09 12:13 | 2020-02-09 13:14 | 61 | 1 | 1 | 61 | 3 | DAMAGED BY PUBLIC | 34 | CONDUCTOR SECONDARY - OH | ENID | 2209 E PINE AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 53588 | 37628 | 2868 | 1753 | 7.0777e-05 | 1.1603e-06 | 61 | 1 | 310 | Customer | 4187 | Load | Tran1phOH | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-09 | 2020 |  | #N/A
J2002.002838 | PD-02092020-00032 | METRO WEST | WEST | 8157:MACARTHUR | MACARTHUR_5722 | 815722 | 2020-02-09 12:21 | 2020-02-09 13:27 | 66.17 | 12 | 9 | 782.5 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 4228 SW.32 | CMI_NORMAL | NO | NO | NO | 861858 | 128953 | 116167 | 1854 | 347 | 0.00090792 | 1.3923e-05 | 65.2083 | 1 | 310 | Load | 4572 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-09 | 2020 |  | #N/A
J2002.002836 |  | METRO WEST | WEST | 8157:MACARTHUR | MACARTHUR_5722 | 815722 | 2020-02-09 12:21 | 2020-02-09 12:21 | 0 | 347 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 3710 N MACARTHUR | CMI_MOMENTARY | YES | NO | NO | 861858 | 128953 | 116167 | 1854 | 347 | 0 | 0.00040262 | 0 | 1 | 0 | Feeder | MACARTHR_5722 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-09 | 2020 |  | #N/A
J2002.002840 | PD-02092020-00035 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2263 | 852263 | 2020-02-09 12:31 | 2020-02-09 14:07 | 96.07 | 1 | 1 | 96.0667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 12924 NE 46TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 114496 | 71251 | 11645 | 1535 | 0.00011146 | 1.1603e-06 | 96.0667 | 1 | 310 | Load | 415171 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | OK - 2021
J2002.002843 | PD-02092020-00033 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1122 | 511122 | 2020-02-09 12:40 | 2020-02-09 13:42 | 62.25 | 1 | 1 | 58.4333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ARDMORE | HOLMAN ADDITION | CMI_NORMAL | NO | NO | NO | 861858 | 77688 | 23603 | 2209 | 1206 | 6.7799e-05 | 1.1603e-06 | 58.4333 | 1 | 310 | Load | 3226 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002848 |  | METRO EAST | EAST | 8411:ACORN | ACORN_1170 | 841170 | 2020-02-09 13:06 | 2020-02-09 13:06 | 0.1 | 1092 | 0 | 109.2 | 16 | SUBSTATION OPERATION | 55 | SCADA - CIRCUIT TRIP | OKLAHOMA CITY | 8700 N AIR DEPOT BLVD | CMI_MOMENTARY | YES | NO | NO | 861858 | 114496 | 71251 | 1796 | 1092 | 0.0001267 | 0.001267 | 0.1 | 1 | 0 | Feeder | ACORN_1170 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002854 | PD-02092020-00037 | METRO EAST | EAST | 8411:ACORN | ACORN_1170 | 841170 | 2020-02-09 13:09 | 2020-02-09 16:00 | 171.13 | 19 | 11 | 1837.3 | 28 | OTHER (DESCRIBE) | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | L5 B1 APPLE VALLEY II | CMI_NORMAL | NO | NO | NO | 861858 | 114496 | 71251 | 1796 | 1092 | 0.0021318 | 2.2045e-05 | 96.7 | 1 | 310 | Mainline | 28344 | Fuse | FuseRiser | BAD ORDER PRIMARY RES COORD | [6 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002853 | PD-02092020-00038 | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1221 | 911221 | 2020-02-09 13:14 | 2020-02-09 14:02 | 48.48 | 1 | 1 | 48.4833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 609.5 S.21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 82318 | 61253 | 6608 | 1742 | 5.6254e-05 | 1.1603e-06 | 48.4833 | 1 | 320 | Customer | 11775 | Load | Tran1phOH | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-09 | 2020 |  | Ark - Series 1
J2002.002857 |  | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2729 | 872729 | 2020-02-09 13:30 | 2020-02-09 18:26 | 296.13 | 2 | 0 | 67.2 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | NORMAN | 3516 WELLSITE DR | CMI_PLANNED | YES | NO | NO | 861858 | 159261 | 57036 | 6494 | 1267 | 7.7971e-05 | 2.3206e-06 | 33.6 | 1 | 0 | Load | 82943 | Load | Tran3phWye | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002860 | PD-02092020-00040 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_771 | 870771 | 2020-02-09 13:33 | 2020-02-09 15:50 | 136.63 | 1 | 1 | 119.7167 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | NOBLE | 4461 NORTHRIDGE LN | CMI_NORMAL | NO | NO | NO | 861858 | 159261 | 57036 | 11844 | 1816 | 0.00013891 | 1.1603e-06 | 119.7167 | 1 | 320 | Customer | 56774 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002861 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5138 | 815138 | 2020-02-09 13:41 | 2020-02-09 13:56 | 15.48 | 1 | 1 | 15.4833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1514 SW 77TH PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159261 | 102225 | 13940 | 1416 | 1.7965e-05 | 1.1603e-06 | 15.4833 | 1 | 320 | Customer | 25868 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002862 | PD-02092020-00042 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3024 | 743024 | 2020-02-09 13:56 | 2020-02-09 15:13 | 76.9 | 1 | 1 | 76.9 | 4 | DETERIORATION | 50 | CONNECTOR | SHAWNEE | 525 S.KICKAPOO | CMI_NORMAL | NO | NO | NO | 861858 | 114496 | 22140 | 6654 | 1641 | 8.9226e-05 | 1.1603e-06 | 76.9 | 1 | 321 | Customer | 2057 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002867 |  | ARKANSAS | FORT SMITH | 9508:WHITESIDE | WHITESIDE_821 | 950821 | 2020-02-09 14:07 | 2020-02-09 15:50 | 102.7 | 1 | 1 | 67.65 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | VAN BUREN | S 14 + VIRGINIA | CMI_PLANNED | YES | NO | NO | 861858 | 82318 | 61253 | 1920 | 1281 | 7.8493e-05 | 1.1603e-06 | 67.65 | 1 | 308 | Mainline | 4316 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-09 | 2020 |  | Ark - Series 2
J2002.002872 | PD-02092020-00045 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_621 | 870621 | 2020-02-09 14:52 | 2020-02-09 16:22 | 89.95 | 1 | 1 | 89.95 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 401 N.MERCEDES DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159261 | 57036 | 7375 | 928 | 0.00010437 | 1.1603e-06 | 89.95 | 1 | 310 | Customer | 36696 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002874 | PD-02092020-00046 | NORTHEAST | MUSKOGEE | 3117:THREE RIVERS | THREE_RIVERS_1721 | 311721 | 2020-02-09 15:11 | 2020-02-09 16:09 | 57.73 | 1 | 1 | 57.7333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 2341 MANILA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 74149 | 33319 | 2835 | 1048 | 6.6987e-05 | 1.1603e-06 | 57.7333 | 1 | 320 | Customer | 8833 | Load | Tran1phOH | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-09 | 2020 |  | #N/A
J2002.002880 | PD-02092020-00048 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5125 | 815125 | 2020-02-09 15:44 | 2020-02-09 16:46 | 61.53 | 1 | 1 | 40.3593 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 7100 S.INDIANA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159261 | 102225 | 13940 | 1432 | 4.6828e-05 | 1.1603e-06 | 40.3593 | 1 | 310 | Customer | 22038 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002892 | PD-02092020-00052 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2029 | 862029 | 2020-02-09 17:23 | 2020-02-09 17:50 | 27.23 | 1 | 1 | 27.2333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 714 SE.21 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159261 | 102225 | 4755 | 985 | 3.1598e-05 | 1.1603e-06 | 27.2333 | 1 | 310 | Customer | 7110 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002893 | PD-02092020-00053 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3731 | 833731 | 2020-02-09 17:30 | 2020-02-09 17:58 | 27.77 | 1 | 1 | 8.0147 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | THE VILLAGE | 1820 CHURCHILL WY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168321 | 148484 | 5768 | 1903 | 9.2993e-06 | 1.1603e-06 | 8.0147 | 1 | 310 | Customer | 7883 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | OK - 2020
J2002.002895 | PD-02092020-00054 | NORTHEAST | MUSKOGEE | 3326:JAMESVILLE | JAMESVILLE_2621 | 332621 | 2020-02-09 17:35 | 2020-02-09 19:02 | 86.75 | 1 | 1 | 76.1167 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | BALD HILL | 1/2 MILE WEST JAMESVILLE "Y" | CMI_NORMAL | NO | NO | NO | 861858 | 74149 | 33319 | 1555 | 273 | 8.8317e-05 | 1.1603e-06 | 76.1167 | 1 | 310 | Load | 16559 | Load | Tran1phOH | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-02-09 | 2020 |  | OK - 2020
J2002.002896 |  | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2521 | 512521 | 2020-02-09 17:36 | 2020-02-09 17:36 | 0 | 784 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | LONE GROVE | 113 S NEWPORT RD | CMI_MOMENTARY | YES | NO | NO | 861858 | 77688 | 23603 | 3307 | 784 | 0 | 0.00090966 | 0 | 1 | 0 | Feeder | LONE_GROVE_2521 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002897 | PD-02092020-00055 | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2521 | 512521 | 2020-02-09 17:44 | 2020-02-09 18:35 | 50.75 | 1 | 1 | 49.9833 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | LONE GROVE | 5W ON HWY 70 1/8S | CMI_NORMAL | NO | NO | NO | 861858 | 77688 | 23603 | 3307 | 784 | 5.7995e-05 | 1.1603e-06 | 49.9833 | 1 | 310 | Customer | 20085 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002898 |  | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1924 | 851924 | 2020-02-09 17:45 | 2020-02-09 17:50 | 5.23 | 1 | 1 | 5.2333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 8822 MISTY HOLLOW DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 114496 | 71251 | 12468 | 1608 | 6.0722e-06 | 1.1603e-06 | 5.2333 | 1 | 310 | Customer | 81996 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002900 | PD-02092020-00056 | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_621 | 880621 | 2020-02-09 17:46 | 2020-02-09 18:19 | 32.9 | 1 | 1 | 32.9 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | GUTHRIE | N-ROLLER COASTER,E-HWY 77 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168321 | 19837 | 5172 | 1880 | 3.8173e-05 | 1.1603e-06 | 32.9 | 1 | 320 | Load | 82613 | Load | Tran3phPadWye | JOSEPH WAYNE POOL | 405-919-2253 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002907 | PD-02092020-00058 | METRO EAST | SEMINOLE | 7505:WEWOKA | WEWOKA 21 | 750521 | 2020-02-09 18:35 | 2020-02-09 19:54 | 79.22 | 1 | 1 | 66.2167 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | WEWOKA | 1MW | CMI_NORMAL | NO | NO | NO | 861858 | 114496 | 13623 | 2477 | 1284 | 7.683e-05 | 1.1603e-06 | 66.2167 | 1 | 311 | Customer | 494 | Load | Tran1phOH | DELBERT HISAW | 405-683-1721 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-02-09 | 2020 |  | OK - 2021
J2002.002909 | PD-02092020-00059 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5125 | 815125 | 2020-02-09 19:31 | 2020-02-09 21:28 | 117.23 | 1 | 2 | 74.969 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7100 S.INDIANA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159261 | 102225 | 13940 | 1432 | 8.6985e-05 | 1.1603e-06 | 74.969 | 1 | 310 | Customer | 22038 | Load | Tran1phOH | GERARDO D SOTO | 405-758-6334 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002910 |  | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1724 | 831724 | 2020-02-09 20:00 | 2020-02-09 20:19 | 19.4 | 1 | 1 | 19.4 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2301 NW.122 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168324 | 148486 | 6649 | 2779 | 2.251e-05 | 1.1603e-06 | 19.4 | 1 | 310 | Customer | 75067 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002916 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-02-09 20:18 | 2020-02-09 20:39 | 20.62 | 1 | 1 | 20.6167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 5720 NW.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168324 | 148486 | 9250 | 1940 | 2.3921e-05 | 1.1603e-06 | 20.6167 | 1 | 310 | Customer | 30951 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | OK - 2021
J2002.002923 | PD-02092020-00061 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-02-09 20:44 | 2020-02-09 23:28 | 163.82 | 1 | 2 | 154.4333 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 1401 NW.103 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861858 | 168324 | 148486 | 8788 | 1953 | 0.00017919 | 1.1603e-06 | 154.4333 | 1 | 320 | Customer | 19172 | Load | Tran1phOH | BRADLEY SUDBECK | 405-999-6850 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | OK - 2021
J2002.002924 | PD-02092020-00062 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4121 | 814121 | 2020-02-09 21:09 | 2020-02-09 22:18 | 69.05 | 1 | 1 | 31.5792 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1209 SW.46 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159261 | 102225 | 5809 | 1200 | 3.6641e-05 | 1.1603e-06 | 31.5792 | 1 | 310 | Customer | 17586 | Load | Tran1phOH | GERARDO D SOTO | 405-758-6334 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-09 | 2020 |  | #N/A
J2002.002927 |  | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_423 | 710423 | 2020-02-09 21:23 | 2020-02-09 21:37 | 14.02 | 856 | 0 | 0.13333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | CHANDLER | N 3450 RD AND HWY 66 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 114496 | 7482 | 2829 | 980 | 1.5471e-07 | 0.0009932 | 0.00015576 | 1 | 0 | Feeder | BELLCOW_423 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002928 | PD-02092020-00063 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-02-09 21:25 | 2020-02-09 22:34 | 68.75 | 1 | 1 | 68.75 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 5720 NW.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168324 | 148486 | 9250 | 1940 | 7.977e-05 | 1.1603e-06 | 68.75 | 1 | 310 | Customer | 30951 | Load | Tran1phPad | BRADLEY SUDBECK | 405-999-6850 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | OK - 2021
J2002.002938 | PD-02092020-00065 | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_922 | 910922 | 2020-02-09 22:41 | 2020-02-10 03:45 | 303.87 | 54 | 58 | 16329.6 | 25 | LIGHTNING | 37 | CONDUCTOR PRIMARY - OH | FORT SMITH | SOVIEW SUBD 70 WOGRNW | CMI_NORMAL | NO | NO | NO | 861858 | 82319 | 61254 | 5015 | 960 | 0.018947 | 6.2655e-05 | 302.4 | 1 | 310 | Mainline | 2655 | Fuse | FuseOH | TRAVIS EARNHART | 479-719-2561 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-09 | 2020 |  | Ark - Series 3
J2002.002936 | PD-02092020-00066 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1924 | 851924 | 2020-02-09 22:43 | 2020-02-10 00:11 | 88.38 | 1 | 1 | 88.3833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MIDWEST CITY | 8822 MISTY HOLLOW DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 114496 | 71251 | 12468 | 1608 | 0.00010255 | 1.1603e-06 | 88.3833 | 1 | 310 | Customer | 81996 | Load | Tran1phPad | BRADLEY SUDBECK | 405-999-6850 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-09 | 2020 |  | #N/A
J2002.002961 |  | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6522 | 836522 | 2020-02-10 03:43 | 2020-02-10 03:48 | 4.68 | 1 | 1 | 4.6833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6454 W.WILSHIRE | CMI_MOMENTARY | YES | NO | NO | 861858 | 128953 | 116167 | 7425 | 1863 | 5.434e-06 | 1.1603e-06 | 4.6833 | 1 | 310 | Customer | 42126 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | OK - 2021
J2002.002973 | PD-02102020-01507 | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_621 | 880621 | 2020-02-10 07:20 | 2020-02-10 10:43 | 203 | 1 | 2 | 203 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | GUTHRIE | N-ROLLER COASTER,E-HWY 77 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168324 | 19838 | 5172 | 1880 | 0.00023554 | 1.1603e-06 | 203 | 1 | 320 | Load | 82613 | Load | Tran3phPadWye | KELLEY D WATSON | 405-763-8148 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.002974 | PD-02102020-01809 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2229 | 852229 | 2020-02-10 07:23 | 2020-02-10 09:37 | 134.48 | 1 | 1 | 130.75 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | HARRAH | 2229 MAXEY DR | CMI_NORMAL | NO | NO | NO | 861858 | 114496 | 71251 | 11645 | 1392 | 0.00015171 | 1.1603e-06 | 130.75 | 1 | 310 | Customer | 51359 | Load | Tran1phOH | STEPHEN R MEADOWS | 405-641-5657 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.002982 | PD-02102020-01855 | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_423 | 710423 | 2020-02-10 08:11 | 2020-02-10 10:00 | 109.22 | 1 | 1 | 106.1167 | 3 | DAMAGED BY PUBLIC | 21 | FUSE - TRANSFORMER | CHANDLER | 11/4M E CHANDLER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 114496 | 7482 | 2829 | 980 | 0.00012313 | 1.1603e-06 | 106.1167 | 1 | 310 | Load | 11209 | Load | TranOpenDelta | SCOTT C PERRY | 405-258-6044 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.002983 | PD-02102020-01862 | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_861 | 550861 | 2020-02-10 08:19 | 2020-02-10 11:02 | 162.72 | 1 | 1 | 162.7167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DURANT | E2030 Rd and Pecan Ridge .1N | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 77690 | 15516 | 1105 | 482 | 0.0001888 | 1.1603e-06 | 162.7167 | 1 | 320 | Customer | 403304 | Load | Tran1phPad | CONTRACTOR BHI3 DAVID ELLIOT INC | 918-282-1005 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.002988 |  | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_621 | 880621 | 2020-02-10 08:29 | 2020-02-10 10:46 | 136.45 | 1 | 1 | 136.45 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | GUTHRIE | N END OF MOOSE CIRCLE GTH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168324 | 19838 | 5172 | 1880 | 0.00015832 | 1.1603e-06 | 136.45 | 1 | 320 | Customer | 68715 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.002995 | PD-02102020-01882 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-02-10 08:48 | 2020-02-10 09:34 | 46.82 | 1 | 1 | 46.8167 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | DEL CITY | 3313 SE.22 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159261 | 102225 | 7422 | 2240 | 5.4321e-05 | 1.1603e-06 | 46.8167 | 1 | 310 | Customer | 5725 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | OK - 2022
J2002.002996 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-02-10 08:50 | 2020-02-10 14:52 | 361.53 | 1 | 1 | 342.4333 | 4 | DETERIORATION | 12 | POLE | BARLING | 3RD STR. | CMI_PLANNED | YES | NO | NO | 861858 | 82319 | 61254 | 2740 | 2128 | 0.00039732 | 1.1603e-06 | 342.4333 | 1 | 308 | Tap | 100958 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | Ark - Series 2
J2002.002997 | PD-02102020-01895 | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5624 | 865624 | 2020-02-10 08:52 | 2020-02-10 09:46 | 54.03 | 1 | 1 | 54.0333 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 6306 S. BRYANT AVE | CMI_NORMAL | NO | NO | NO | 861858 | 159261 | 102225 | 2761 | 112 | 6.2694e-05 | 1.1603e-06 | 54.0333 | 1 | 310 | Load | 182433 | Load | Tran1phOH | MARK A PALMORE | 405-512-1933 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003001 | PD-02102020-01898 | NORTHWEST | ENID | 4240:DEER CREEK | DEER CREEK 48 | 424048 | 2020-02-10 08:59 | 2020-02-10 10:10 | 71.45 | 1 | 1 | 71.45 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | LAMONT | BN-JEFFERSON, .5BW-MAIN | CMI_NORMAL | NO | NO | NO | 861858 | 53589 | 37628 | 623 | 478 | 8.2902e-05 | 1.1603e-06 | 71.45 | 1 | 310 | Customer | 3054 | Load | TranOpenDelta | RANDY D MASON | 580-977-8823 | [5 empty] | Other | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | #N/A
J2002.003006 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2229 | 852229 | 2020-02-10 09:04 | 2020-02-10 11:21 | 137.23 | 4 | 4 | 111 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | HARRAH | 2320 MAXEY DR | CMI_PLANNED | YES | NO | NO | 861858 | 114496 | 71251 | 11645 | 1392 | 0.00012879 | 4.6411e-06 | 27.75 | 1 | 310 | Load | 3165 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003007 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-02-10 09:08 | 2020-02-10 09:48 | 39.63 | 6 | 2 | 172.4 | 4 | DETERIORATION | 12 | POLE | LAVACA | 1910 BARBARA LANE LAVACA,ARK | CMI_PLANNED | YES | NO | NO | 861858 | 82319 | 61254 | 2740 | 2128 | 0.00020003 | 6.9617e-06 | 28.7333 | 1 | 308 | Load | 1090 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | Ark - Series 2
J2002.003010 |  | METRO WEST | WEST | 8335:BETHANY | BETHANY_3527 | 833527 | 2020-02-10 09:16 | 2020-02-10 09:55 | 39.42 | 1 | 1 | 39.4167 | 1 | CANCELLED | 57 | CANCELLED | WARR ACRES | 5915 NW 42ND ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 128953 | 116167 | 7878 | 1666 | 4.5735e-05 | 1.1603e-06 | 39.4167 | 1 | 310 | Customer | 30048 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | OK - 2022
J2002.003012 |  | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_450 | 710450 | 2020-02-10 09:17 | 2020-02-11 16:55 | 1898.7 | 1 | 0 | 1890.2333 | 28 | OTHER (DESCRIBE) | 37 | CONDUCTOR PRIMARY - OH | 0 | 1.5S OF HW66 ON ROZELL | CMI_PLANNED | YES | NO | NO | 861858 | 114496 | 7482 | 2829 | 403 | 0.0021932 | 1.1603e-06 | 1890.2333 | 1 | 0 | Mainline | 7774 | Switch | SwitchOH | Crew | [6 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | OK - 2021
J2002.003013 | PD-02102020-01913 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6124 | 836124 | 2020-02-10 09:17 | 2020-02-10 10:17 | 60.33 | 1 | 1 | 60.3333 | 13 | PREMATURE FAILURE | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | NW.25 & MCKINLY | CMI_NORMAL | NO | NO | NO | 861858 | 168324 | 148486 | 11122 | 1768 | 7.0004e-05 | 1.1603e-06 | 60.3333 | 1 | 320 | Load | 174932 | Load | Tran3phPadWye | MARK A. CALVERT | 405-820-9246 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | OK - 2020
J2002.003015 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3829 | 913829 | 2020-02-10 09:20 | 2020-02-10 09:33 | 12.58 | 1 | 1 | 12.5833 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 1915 S.T | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 82319 | 61254 | 2942 | 1189 | 1.46e-05 | 1.1603e-06 | 12.5833 | 1 | 310 | Customer | 11414 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-10 | 2020 |  | Ark - Series 2
J2002.003018 | PD-02102020-01920 | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_422 | 510422 | 2020-02-10 09:21 | 2020-02-10 10:29 | 67.83 | 17 | 7 | 1107.55 | 29 | TREES : GROW IN | 23 | FUSE - PRIMARY | ARDMORE | .5E 3RD NE + M NIBLACK | CMI_NORMAL | NO | NO | NO | 861858 | 77690 | 23604 | 2319 | 1058 | 0.0012851 | 1.9725e-05 | 65.15 | 1 | 310 | Tap | 2921 | Fuse | FuseOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003022 | PD-02102020-01948 | METRO WEST | WEST | 8321:PIEDMONT | PIEDMONT_2164 | 832164 | 2020-02-10 09:29 | 2020-02-10 14:14 | 284.58 | 1 | 2 | 22.5371 | 3 | DAMAGED BY PUBLIC | 31 | CONDUCTOR SERVICE - OH | PIEDMONT | MUSTANG RD + NW 206 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 128953 | 116167 | 6308 | 3013 | 2.6149e-05 | 1.1603e-06 | 22.5371 | 1 | 310 | Load | 53353 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003026 |  | NORTHEAST | MUSKOGEE | 3325:WELLS | WELLS_2549 | 332549 | 2020-02-10 09:34 | 2020-02-10 09:56 | 21.83 | 1 | 1 | 21.8333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKTAHA | OKTAHA OK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 74151 | 33320 | 2381 | 1053 | 2.5333e-05 | 1.1603e-06 | 21.8333 | 1 | 310 | Customer | 989 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | OK - 2021
J2002.003031 |  | METRO SOUTH | SOUTH | 8726:NOBLE | NOBLE_2621 | 872621 | 2020-02-10 09:39 | 2020-02-10 09:46 | 7.03 | 1 | 1 | 7.0333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NOBLE | 214 FRONT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159261 | 57036 | 2967 | 1446 | 8.1607e-06 | 1.1603e-06 | 7.0333 | 1 | 310 | Customer | 31564 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003030 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-02-10 09:40 | 2020-02-10 12:21 | 161.72 | 5 | 2 | 799.6667 | 4 | DETERIORATION | 12 | POLE | MOUNTAINBURG | WILLOW 700 E OF HWY 71 | CMI_PLANNED | YES | NO | NO | 861858 | 82319 | 61254 | 3791 | 2585 | 0.00092784 | 5.8014e-06 | 159.9333 | 1 | 310 | Tap | 7336 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-10 | 2020 |  | Ark - Series 2
J2002.003032 | PD-02102020-01950 | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_422 | 510422 | 2020-02-10 09:43 | 2020-02-10 10:45 | 61.85 | 1 | 1 | 61.85 | 13 | PREMATURE FAILURE | 16 | LINE RECLOSER | ARDMORE | 3124 WOODSIDE DR | CMI_NORMAL | NO | NO | NO | 861858 | 77690 | 23604 | 2319 | 1058 | 7.1764e-05 | 1.1603e-06 | 61.85 | 1 | 320 | Customer | 8814 | Load | Tran1phPad | GARRETT YOUNG | 580-276-6194 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003034 | PD-02102020-01960 | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1224 | 911224 | 2020-02-10 09:52 | 2020-02-10 11:02 | 70.17 | 1 | 1 | 70.1667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 900 N.16 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 82319 | 61254 | 6608 | 1804 | 8.1413e-05 | 1.1603e-06 | 70.1667 | 1 | 320 | Customer | 6255 | Load | Tran1phOH | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | Ark - Series 1
J2002.003037 | PD-02102020-01964 | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2122 | 892122 | 2020-02-10 10:00 | 2020-02-10 13:45 | 225.47 | 1 | 1 | 182.9667 | 11 | OVERLOAD | 2 | TRANSFORMER OH | EL RENO | 3535 S Choctaw AV | CMI_NORMAL | NO | NO | NO | 861858 | 0 | 0 | 0 | 0 | 0.00021229 | 1.1603e-06 | 182.9667 | 1 | 321 | Load | 418957 | Load | Tran3phWye | JESSE PHILLER | 405-512-8086 |  |  |  |  | 06/10/2020 note from burchamc. Reference J2002.003037 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Manually completed blank Job Region, Job Area, etc. | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003039 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-10 10:02 | 2020-02-10 14:17 | 254.42 | 1 | 1 | 242.5 | 4 | DETERIORATION | 12 | POLE | POCOLA | 1/4M S CHAMP HINTON ON HWY 112 | CMI_PLANNED | YES | NO | NO | 861858 | 82319 | 61254 | 1458 | 1240 | 0.00028137 | 1.1603e-06 | 242.5 | 1 | 308 | Load | 13982 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | Ark - Series 2
J2002.003041 |  | METRO EAST | EAST | 8542:RENO | RENO_4231 | 854231 | 2020-02-10 10:06 | 2020-02-10 11:19 | 73.07 | 4 | 5 | 272.7333 | 4 | DETERIORATION | 12 | POLE | DEL CITY | 3201 LONGRIDGE RD | CMI_PLANNED | YES | NO | NO | 861858 | 114496 | 71251 | 5215 | 959 | 0.00031645 | 4.6411e-06 | 68.1833 | 1 | 310 | Load | 20692 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | OK - 2021
J2002.003043 | PD-02102020-01971 | METRO EAST | EAST | 8542:RENO | RENO_4231 | 854231 | 2020-02-10 10:09 | 2020-02-10 10:42 | 32.97 | 1 | 2 | 32.9667 | 4 | DETERIORATION | 12 | POLE | DEL CITY | 860 S.SCOTT AV | CMI_PLANNED | YES | NO | NO | 861858 | 114496 | 71251 | 5215 | 959 | 3.8251e-05 | 1.1603e-06 | 32.9667 | 1 | 310 | Customer | 20691 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | OK - 2021
J2002.003046 | PD-02102020-01977 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2224 | 832224 | 2020-02-10 10:16 | 2020-02-10 11:40 | 83.93 | 1 | 1 | 83.9333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 3825 NW.27 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168324 | 148486 | 9179 | 1431 | 9.7386e-05 | 1.1603e-06 | 83.9333 | 1 | 310 | Customer | 4829 | Load | Tran1phOH | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | #N/A
J2002.003047 | PD-02102020-01976 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6521 | 836521 | 2020-02-10 10:18 | 2020-02-10 11:22 | 64.22 | 1 | 1 | 64.2167 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 4804 NW.77 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 128953 | 116167 | 7425 | 1646 | 7.451e-05 | 1.1603e-06 | 64.2167 | 1 | 310 | Customer | 28255 | Load | Tran1phOH | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | OK - 2022
J2002.003053 | PD-02102020-02315 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_861 | 830861 | 2020-02-10 10:31 | 2020-02-10 16:31 | 360.05 | 1 | 1 | 6.8201 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 15809 Rockwell Park Lane | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861858 | 168324 | 148486 | 19410 | 3948 | 7.9132e-06 | 1.1603e-06 | 6.8201 | 1 | 320 | Customer | 367666 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003058 |  | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5423 | 865423 | 2020-02-10 10:35 | 2020-02-10 12:41 | 126.55 | 13 | 3 | 1125.3667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | MOORE | 1109 WHISPERING OAKS BLVD | CMI_PLANNED | YES | NO | NO | 861858 | 159261 | 102225 | 9810 | 1722 | 0.0013057 | 1.5084e-05 | 86.5667 | 1 | 308 | Load | 71095 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003061 |  | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4024 | 914024 | 2020-02-10 10:38 | 2020-02-10 15:23 | 284.73 | 5 | 4 | 554.125 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 5018 S.29 | CMI_PLANNED | YES | NO | NO | 861858 | 82319 | 61254 | 4765 | 1167 | 0.00064294 | 5.8014e-06 | 110.825 | 1 | 308 | Load | 5783 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-10 | 2020 |  | Ark - Series 2
J2002.003062 |  | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1221 | 911221 | 2020-02-10 10:38 | 2020-02-10 13:45 | 186.58 | 8 | 0 | 1492.5127 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | SO.O + 22 ND | CMI_NORMAL | NO | NO | NO | 861858 | 82319 | 61254 | 6608 | 1742 | 0.0017317 | 9.2823e-06 | 186.5641 | 1 | 0 | Tap | 5861 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | Ark - Series 1
J2002.003067 |  | METRO NORTH | GUTHRIE | 8819:LIBERTY LAKE | LIBERTY_LAKE_1921 | 881921 | 2020-02-10 10:40 | 2020-02-10 10:59 | 18.48 | 2 | 0 | 36.9701 | 4 | DETERIORATION | 12 | POLE | 0 | 1/4MS SIMPSON,ES PINE | CMI_PLANNED | YES | NO | NO | 861858 | 168324 | 19838 | 3355 | 1527 | 4.2896e-05 | 2.3206e-06 | 18.4851 | 1 | 0 | Load | 37764 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003073 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_771 | 870771 | 2020-02-10 10:46 | 2020-02-10 10:58 | 12.07 | 1 | 1 | 12.0667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NOBLE | 601 SKYRIDGE TRAIL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159261 | 57036 | 11844 | 1816 | 1.4001e-05 | 1.1603e-06 | 12.0667 | 1 | 310 | Customer | 67381 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003074 | PD-02102020-02015 | NORTHEAST | MUSKOGEE | 3327:VIAN | VIAN 22 | 332722 | 2020-02-10 10:49 | 2020-02-10 12:08 | 79.23 | 6 | 2 | 419.6 | 13 | PREMATURE FAILURE | 23 | FUSE - PRIMARY | VIAN | N.OF WATER TOWER | CMI_NORMAL | NO | NO | NO | 861858 | 74151 | 33320 | 780 | 780 | 0.00048686 | 6.9617e-06 | 69.9333 | 1 | 310 | Tap | 28294 | Fuse | FuseOH | JAMES MCDONALD | 405-361-7186 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | OK - 2021
J2002.003075 | PD-02102020-02014 | METRO EAST | EAST | 8471:NE 30TH ST | NE_30TH_ST_7123 | 847123 | 2020-02-10 10:50 | 2020-02-10 11:41 | 51.37 | 1 | 1 | 11.7299 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | DEFAULT STATION | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 114496 | 71251 | 2403 | 1294 | 1.361e-05 | 1.1603e-06 | 11.7299 | 1 | 310 | Customer | 11462 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | OK - 2022
J2002.003076 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-10 11:02 | 2020-02-10 16:11 | 308.87 | 2 | 2 | 534.15 | 4 | DETERIORATION | 12 | POLE | LAMAR | CITY PARK ON KITCHEN ST. | CMI_PLANNED | YES | NO | NO | 861858 | 82319 | 7555 | 733 | 0 | 0.00061977 | 2.3206e-06 | 267.075 | 1 | 308 | Tap | 190392 | Fuse | FuseRiser | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | #N/A
J2002.003081 | PD-02102020-02036 | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2163 | 892163 | 2020-02-10 11:20 | 2020-02-10 12:15 | 55.47 | 1 | 1 | 55.4667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | UNION CITY | 16436 25TH CT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 128953 | 12786 | 3198 | 1146 | 6.4357e-05 | 1.1603e-06 | 55.4667 | 1 | 310 | Customer | 242924 | Load | Tran1phPad | ERIC S KAPPUS | 405-642-1454 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | OK - 2021
J2002.003083 | PD-02102020-02040 | METRO SOUTH | SOUTH CENTRAL | 8723:INDIAN HILL | INDIAN_HILL_2323 | 872323 | 2020-02-10 11:25 | 2020-02-10 11:57 | 31.82 | 1 | 1 | 29.1333 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | MOORE | .3ME EASTERN ON SS MOORE S34TH | CMI_NORMAL | NO | NO | NO | 861858 | 159261 | 102225 | 3192 | 1453 | 3.3803e-05 | 1.1603e-06 | 29.1333 | 1 | 310 | Customer | 74939 | Load | Tran3phPadWye | ETHAN MORRIS | 918-510-5170 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003084 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_771 | 870771 | 2020-02-10 11:26 | 2020-02-10 11:32 | 6.45 | 1 | 1 | 6.45 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | LOT26 BLK1 EASTRIDGE SEC 14 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159261 | 57036 | 11844 | 1816 | 7.4838e-06 | 1.1603e-06 | 6.45 | 1 | 310 | Customer | 102909 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003087 | PD-02102020-02044 | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5421 | 865421 | 2020-02-10 11:30 | 2020-02-10 12:20 | 49.53 | 1 | 1 | 9.0768 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MOORE | 609 NE 16TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159261 | 102225 | 9810 | 1880 | 1.0532e-05 | 1.1603e-06 | 9.0768 | 1 | 310 | Customer | 67774 | Load | Tran1phPad | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003091 | PD-02102020-02047 | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_823 | 870823 | 2020-02-10 11:40 | 2020-02-10 12:16 | 36.37 | 1 | 1 | 36.3667 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | NORMAN | 2825 S.DEWEY AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159261 | 57036 | 6776 | 2379 | 4.2196e-05 | 1.1603e-06 | 36.3667 | 1 | 310 | Customer | 17090 | Load | Tran1phPad | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003103 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-10 11:49 | 2020-02-10 12:07 | 17.93 | 61 | 17 | 979.4485 | 5 | ELECTRICAL TRACKING | 37 | CONDUCTOR PRIMARY - OH | POCOLA | HWY 112 AND TEXAS RD. | CMI_NORMAL | NO | NO | NO | 861858 | 82319 | 61254 | 1458 | 1240 | 0.0011364 | 7.0777e-05 | 16.0565 | 1 | 310 | Mainline | 418362 | Recloser | Tripsaver3ph | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | Ark - Series 2
J2002.003106 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2224 | 852224 | 2020-02-10 11:50 | 2020-02-10 12:57 | 67.33 | 15 | 9 | 806.75 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | CHOCTAW | .1 MN SE 15 ES CHOCTAW | CMI_PLANNED | YES | NO | NO | 861858 | 114496 | 71251 | 11645 | 1523 | 0.00093606 | 1.7404e-05 | 53.7833 | 1 | 310 | Tap | 19014 | Fuse | FuseOH | STEPHEN R MEADOWS | 405-641-5657 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003105 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2525 | 912525 | 2020-02-10 12:02 | 2020-02-10 13:21 | 78.98 | 12 | 2 | 660.7 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 7 AMBERWOOD CT | CMI_PLANNED | YES | NO | NO | 861858 | 82319 | 61254 | 2740 | 198 | 0.0007666 | 1.3923e-05 | 55.0583 | 1 | 308 | Load | 14625 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | Ark - Series 2
J2002.003108 | PD-02102020-02091 | METRO WEST | WEST | 8321:PIEDMONT | PIEDMONT_2169 | 832169 | 2020-02-10 12:10 | 2020-02-10 18:05 | 354.7 | 4 | 6 | 1394.7333 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | PIEDMONT | GOLDEN HILLS BLK 3, LOT 7 | CMI_NORMAL | NO | NO | NO | 861858 | 128953 | 116167 | 6308 | 1664 | 0.0016183 | 4.6411e-06 | 348.6833 | 1 | 310 | Secondary | 208513 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003112 | PD-02102020-02102 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-02-10 12:24 | 2020-02-10 12:59 | 35.18 | 1 | 1 | 5.7246 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1617 NW.20 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168324 | 148486 | 11122 | 2058 | 6.6421e-06 | 1.1603e-06 | 5.7246 | 1 | 310 | Customer | 10378 | Load | Tran1phOH | REX R WILSON | 405-535-4507 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | OK - 2021
J2002.003114 |  | METRO EAST | EAST | 8690:WILD MARY | WILD_MARY_9023 | 869023 | 2020-02-10 12:25 | 2020-02-10 12:33 | 8.15 | 1 | 1 | 8.15 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | SE 96TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 114496 | 71251 | 4023 | 2249 | 9.4563e-06 | 1.1603e-06 | 8.15 | 1 | 310 | Customer | 250948 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003118 | PD-02102020-02111 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7029 | 817029 | 2020-02-10 12:29 | 2020-02-10 13:02 | 33.15 | 6 | 8 | 152.9 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MOORE | 2816 WOODLAWN DR | CMI_NORMAL | NO | NO | NO | 861858 | 159261 | 102225 | 9939 | 1757 | 0.00017741 | 6.9617e-06 | 25.4833 | 1 | 310 | Load | 52261 | Load | Tran1phOH | MARK A PALMORE | 405-512-1933 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | OK - 2022
J2002.003119 |  | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6223 | 866223 | 2020-02-10 12:35 | 2020-02-10 14:18 | 103.52 | 1 | 1 | 30.2333 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | ANDRSON .4MN SE44 | CMI_PLANNED | YES | NO | NO | 861858 | 114496 | 71251 | 7214 | 2237 | 3.5079e-05 | 1.1603e-06 | 30.2333 | 1 | 308 | Tap | 16119 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003121 | PD-02102020-02112 | METRO SOUTH | SOUTH | 8722:MILLENNIUM | MILLENNIUM_2222 | 872222 | 2020-02-10 12:35 | 2020-02-10 13:18 | 42.78 | 1 | 1 | 42.7833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | 1415 FAIRLAWN DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159261 | 57036 | 4206 | 738 | 4.9641e-05 | 1.1603e-06 | 42.7833 | 1 | 310 | Load | 52122 | Load | Tran3phPadWye | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003120 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2525 | 912525 | 2020-02-10 12:36 | 2020-02-10 14:33 | 116.73 | 4 | 1 | 458.4667 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | FORT SMITH | 5309 HEATHER RIDGE | CMI_PLANNED | YES | NO | NO | 861858 | 82319 | 61254 | 2740 | 198 | 0.00053195 | 4.6411e-06 | 114.6167 | 1 | 308 | Load | 14626 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | Ark - Series 2
J2002.003127 |  | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5621 | 865621 | 2020-02-10 12:47 | 2020-02-10 12:54 | 6.43 | 1 | 1 | 6.4333 | 1 | CANCELLED | 57 | CANCELLED | VALLEY BROOK | 6016 PAT AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159261 | 102225 | 2761 | 541 | 7.4645e-06 | 1.1603e-06 | 6.4333 | 1 | 310 | Customer | 10234 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003124 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-10 12:47 | 2020-02-10 14:06 | 79.1 | 2 | 1 | 142.8833 | 4 | DETERIORATION | 12 | POLE | CHARLESTON | % RT 3 BOX 49 K | CMI_PLANNED | YES | NO | NO | 861858 | 82319 | 61254 | 962 | 491 | 0.00016579 | 2.3206e-06 | 71.4417 | 1 | 308 | Load | 9093 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-10 | 2020 |  | Ark - Series 2
J2002.003131 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-10 12:59 | 2020-02-10 13:06 | 7.18 | 1 | 1 | 7.1833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | POCOLA | ELIZABETH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 82319 | 61254 | 1458 | 1240 | 8.3347e-06 | 1.1603e-06 | 7.1833 | 1 | 310 | Customer | 13921 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | Ark - Series 2
J2002.003132 | PD-02102020-02139 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7422 | 847422 | 2020-02-10 12:59 | 2020-02-10 13:48 | 49.12 | 1 | 1 | 49.1167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 817 NE.31 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168324 | 148486 | 6171 | 1215 | 5.6989e-05 | 1.1603e-06 | 49.1167 | 1 | 310 | Customer | 15901 | Load | Tran1phOH | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | OK - 2022
J2002.003138 | PD-02102020-02182 | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_522 | 560522 | 2020-02-10 13:09 | 2020-02-10 13:53 | 43.8 | 1 | 1 | 43.8 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | PAULS VALLEY | 2N .6E PAULS VALLEY | CMI_NORMAL | NO | NO | NO | 861858 | 77690 | 6221 | 2465 | 828 | 5.082e-05 | 1.1603e-06 | 43.8 | 1 | 310 | Load | 29282 | Load | TranOpenDelta | GARRID H BROWN | 405-207-3948 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | OK - 2022
J2002.003149 | PD-02102020-02178 | ARKANSAS | FORT SMITH | 9512:ADABELL ROAD | ADABELL_ROAD_1221 | 951221 | 2020-02-10 13:28 | 2020-02-10 14:22 | 53.68 | 1 | 2 | 5.0833 | 12 | POOR CONNECTION | 50 | CONNECTOR | VAN BUREN | 711 DRENNEN ST | CMI_NORMAL | NO | NO | NO | 861858 | 82319 | 61254 | 3125 | 1097 | 5.8981e-06 | 1.1603e-06 | 5.0833 | 1 | 310 | Customer | 479 | Load | Tran1phOH | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-10 | 2020 |  | Ark - Series 1
J2002.003157 | PD-02102020-02222 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-02-10 13:56 | 2020-02-10 15:58 | 121.82 | 1 | 1 | 62.882 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4630 NW.19 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168324 | 148486 | 9250 | 1940 | 7.2961e-05 | 1.1603e-06 | 62.882 | 1 | 310 | Customer | 24600 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | OK - 2021
J2002.003159 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5127 | 815127 | 2020-02-10 14:11 | 2020-02-10 15:22 | 70.17 | 20 | 6 | 1075.5 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | OKLAHOMA CITY | 10200 SHADOWRIDGE DR | CMI_PLANNED | YES | NO | NO | 861858 | 159261 | 102225 | 13940 | 1995 | 0.0012479 | 2.3206e-05 | 53.775 | 1 | 308 | Load | 67146 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003160 | PD-02102020-02235 | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9924 | 829924 | 2020-02-10 14:14 | 2020-02-10 15:08 | 54.15 | 1 | 1 | 24.5546 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7100 MICHELLE LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 128953 | 116167 | 9242 | 1485 | 2.849e-05 | 1.1603e-06 | 24.5546 | 1 | 310 | Customer | 70740 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003164 | PD-02102020-02247 | ARKANSAS | OZARK | 9406:HELBERG | HELBERG_621 | 940621 | 2020-02-10 14:18 | 2020-02-10 15:08 | 50.4 | 1 | 1 | 50.4 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OZARK | 102.5 E.SPING ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 82319 | 7555 | 1722 | 835 | 5.8478e-05 | 1.1603e-06 | 50.4 | 1 | 310 | Customer | 7726 | Load | Tran1phOH | KRIS L HALMES | 479-430-9447 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | Ark - Series 3
J2002.003168 |  | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1423 | 311423 | 2020-02-10 14:33 | 2020-02-10 14:45 | 12.68 | 1 | 1 | 12.6833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 1123 ELGIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 74151 | 33320 | 4574 | 1498 | 1.4716e-05 | 1.1603e-06 | 12.6833 | 1 | 310 | Customer | 466 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | OK - 2020
J2002.003175 | PD-02102020-02278 | NORTHWEST | ENID | 4135:SO 4TH ST | SO_4TH_ST_3524 | 413524 | 2020-02-10 14:33 | 2020-02-10 16:12 | 99.1 | 8 | 11 | 238.4 | 22 | WIND | 17 | JUMPER | ENID | 1210 GANNON | CMI_NORMAL | NO | NO | NO | 861858 | 53589 | 37628 | 3098 | 1614 | 0.00027661 | 9.2823e-06 | 29.8 | 1 | 310 | Load | 2251 | Load | Tran1phOH | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003169 | PD-02102020-02256 | METRO EAST | SEMINOLE | 7208:CYPRESS | CYPRESS_821 | 720821 | 2020-02-10 14:37 | 2020-02-10 16:13 | 96.33 | 1 | 1 | 96.3333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | HOLDENVILLE | 904 S OAK ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 114496 | 13623 | 2522 | 1090 | 0.00011177 | 1.1603e-06 | 96.3333 | 1 | 310 | Customer | 10075 | Load | Tran1phOH | DELBERT HISAW | 405-683-1721 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | #N/A
J2002.003170 | PD-02102020-02261 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3621 | 853621 | 2020-02-10 14:38 | 2020-02-10 15:13 | 34.53 | 1 | 1 | 34.5333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1401 NE.17 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168324 | 148486 | 5934 | 2172 | 4.0068e-05 | 1.1603e-06 | 34.5333 | 1 | 310 | Customer | 23494 | Load | Tran1phOH | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | OK - 2022
J2002.003181 |  | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1621 | 581621 | 2020-02-10 15:05 | 2020-02-10 15:36 | 31.47 | 21 | 4 | 421.4 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | ADA | 200 W.COTTAGE | CMI_PLANNED | YES | NO | NO | 861858 | 77690 | 11522 | 3463 | 1809 | 0.00048894 | 2.4366e-05 | 20.0667 | 1 | 308 | Load | 21751 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003182 | PD-02102020-02301 | NORTHEAST | SAPULPA | 3220:KELLYVILLE | KELLYVILLE_2024 | 322024 | 2020-02-10 15:06 | 2020-02-10 15:59 | 53.42 | 1 | 1 | 53.4167 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | SAPULPA | SOUTH OF HICKORY BLUFF EST | CMI_NORMAL | NO | NO | NO | 861858 | 74151 | 40831 | 2552 | 1581 | 6.1979e-05 | 1.1603e-06 | 53.4167 | 1 | 310 | Customer | 19012 | Load | Tran1phOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | OK - 2020
J2002.003195 | PD-02102020-02351 | METRO NORTH | NORTH | 8464:BRYANT | BRYANT_6422 | 846422 | 2020-02-10 15:40 | 2020-02-10 20:30 | 289.8 | 6 | 6 | 1520.1 | 5 | ELECTRICAL TRACKING | 23 | FUSE - PRIMARY | OKLAHOMA CITY | .6ME BRYANT / NE 93RD | CMI_NORMAL | NO | NO | NO | 861858 | 168324 | 148486 | 1893 | 629 | 0.0017637 | 6.9617e-06 | 253.35 | 1 | 310 | Mainline | 7962 | Fuse | FuseOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003193 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6324 | 816324 | 2020-02-10 15:44 | 2020-02-10 16:10 | 26.35 | 1 | 1 | 26.35 | 1 | CANCELLED | 57 | CANCELLED | MOORE | 829 N.BUTLER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159261 | 102225 | 11849 | 2049 | 3.0573e-05 | 1.1603e-06 | 26.35 | 1 | 310 | Customer | 22883 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | OK - 2021
J2002.003197 | PD-02102020-02344 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5134 | 815134 | 2020-02-10 15:53 | 2020-02-10 17:07 | 74.07 | 1 | 1 | 74.0667 | 13 | PREMATURE FAILURE | 15 | METER - SECONDARY | OKLAHOMA CITY | 720 BROOKWOOD DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861858 | 159261 | 102225 | 13940 | 2469 | 8.5938e-05 | 1.1603e-06 | 74.0667 | 1 | 320 | Customer | 7530 | Load | Tran1phPad | THOMAS E COLE | 405-623-9338 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003198 |  | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_922 | 910922 | 2020-02-10 15:53 | 2020-02-10 16:00 | 6.97 | 1 | 1 | 6.9667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 3213 S.42 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 82319 | 61254 | 5015 | 960 | 8.0833e-06 | 1.1603e-06 | 6.9667 | 1 | 310 | Customer | 8417 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | Ark - Series 3
J2002.003199 | PD-02102020-02365 | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-02-10 15:59 | 2020-02-10 17:51 | 111.53 | 1 | 1 | 111.5333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 14201 SE 149TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159261 | 57036 | 4238 | 3069 | 0.00012941 | 1.1603e-06 | 111.5333 | 1 | 310 | Load | 229424 | Load | Tran1phOH | THOMAS E COLE | 405-623-9338 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003202 | PD-02102020-02360 | METRO EAST | EAST | 8542:RENO | RENO_4231 | 854231 | 2020-02-10 16:02 | 2020-02-10 16:58 | 55.7 | 1 | 1 | 55.7 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DEL CITY | 3927 SE.11 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 114496 | 71251 | 5215 | 959 | 6.4628e-05 | 1.1603e-06 | 55.7 | 1 | 310 | Customer | 10296 | Load | Tran1phOH | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | OK - 2021
J2002.003201 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_866 | 830866 | 2020-02-10 16:03 | 2020-02-10 16:12 | 8.18 | 1 | 1 | 8.1833 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | NW.140 + 1/4 ME-PENN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168324 | 148486 | 19410 | 4304 | 9.495e-06 | 1.1603e-06 | 8.1833 | 1 | 310 | Customer | 69646 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003205 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-10 16:08 | 2020-02-10 17:20 | 71.68 | 1 | 1 | 65.65 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | CHARLESTON | @ RODAEO GRD-N OF 22 | CMI_PLANNED | YES | NO | NO | 861858 | 82319 | 61254 | 962 | 491 | 7.6173e-05 | 1.1603e-06 | 65.65 | 1 | 308 | Mainline | 3321 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-10 | 2020 |  | Ark - Series 2
J2002.003209 | PD-02102020-02364 | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2124 | 332124 | 2020-02-10 16:17 | 2020-02-10 18:28 | 130.8 | 1 | 1 | 12.3667 | 12 | POOR CONNECTION | 50 | CONNECTOR | FORT GIBSON | 513 E.IRVING | CMI_NORMAL | NO | NO | NO | 861858 | 74151 | 33320 | 3337 | 1221 | 1.4349e-05 | 1.1603e-06 | 12.3667 | 1 | 320 | Customer | 11441 | Load | Tran1phOH | RICHARD R BLANCHET | 918-869-2563 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-10 | 2020 |  | #N/A
J2002.003213 | PD-02102020-02368 | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-10 16:34 | 2020-02-10 17:19 | 45.47 | 1 | 1 | 43.7667 | 5 | ELECTRICAL TRACKING | 27 | CUTOUT | BRANCH | HWY 22 BRANCH FEED STORE | CMI_NORMAL | NO | NO | NO | 861858 | 82319 | 61254 | 962 | 491 | 5.0782e-05 | 1.1603e-06 | 43.7667 | 1 | 310 | Customer | 1427 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-10 | 2020 |  | Ark - Series 2
J2002.003221 |  | METRO EAST | EAST | 8542:RENO | RENO_4231 | 854231 | 2020-02-10 17:18 | 2020-02-10 17:51 | 33.33 | 1 | 1 | 33.3333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DEL CITY | 3927 SE.11 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 114496 | 71251 | 5215 | 959 | 3.8676e-05 | 1.1603e-06 | 33.3333 | 1 | 315 | Customer | 10296 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | OK - 2021
J2002.003222 |  | SOUTHERN | ADA | 5809:VANOSS | VANOSS_922 | 580922 | 2020-02-10 17:22 | 2020-02-10 17:46 | 23.92 | 1 | 1 | 23.9167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | STRATFORD | BTWN GARVIN AND MURRAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 77690 | 11522 | 979 | 979 | 2.775e-05 | 1.1603e-06 | 23.9167 | 1 | 310 | Customer | 23686 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | OK - 2021
J2002.003224 | PD-02102020-02385 | NORTHEAST | SAPULPA | 7605:DRUMRIGHT | DRUMRIGHT_544 | 760544 | 2020-02-10 17:30 | 2020-02-10 18:32 | 61.52 | 6 | 8 | 362.9 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | OILTON | 707 S.E | CMI_NORMAL | NO | NO | NO | 861858 | 74151 | 40831 | 1696 | 1116 | 0.00042107 | 6.9617e-06 | 60.4833 | 1 | 310 | Load | 43283 | Load | Tran1phOH | NICHOLAS MANION | 918-290-1327 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | #N/A
J2002.003228 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2525 | 912525 | 2020-02-10 17:49 | 2020-02-10 20:39 | 170.17 | 1 | 1 | 92.4 | 4 | DETERIORATION | 28 | CROSSARM | FORT SMITH | PHOENIX + 540 S. SIDE | CMI_PLANNED | YES | NO | NO | 861858 | 82319 | 61254 | 2740 | 198 | 0.00010721 | 1.1603e-06 | 92.4 | 1 | 308 | Tap | 7111 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | Ark - Series 2
J2002.003231 |  | METRO WEST | WEST | 8323:RICHARDS | RICHARDS_2324 | 832324 | 2020-02-10 17:59 | 2020-02-10 18:22 | 23.18 | 1 | 1 | 23.1833 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 8600 NW 125TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 128953 | 116167 | 5020 | 1605 | 2.6899e-05 | 1.1603e-06 | 23.1833 | 1 | 310 | Customer | 253775 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003237 | PD-02102020-02389 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6329 | 816329 | 2020-02-10 18:25 | 2020-02-10 20:50 | 145.15 | 1 | 1 | 145.15 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 604 CEDAR RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159262 | 102226 | 11849 | 1713 | 0.00016842 | 1.1603e-06 | 145.15 | 1 | 310 | Customer | 25902 | Load | Tran1phPad | GERARDO D SOTO | 405-758-6334 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003238 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_866 | 830866 | 2020-02-10 18:27 | 2020-02-10 18:39 | 11.85 | 1 | 1 | 11.85 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | NW.140 + 1/4 ME-PENN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 168329 | 148491 | 19412 | 4304 | 1.3749e-05 | 1.1603e-06 | 11.85 | 1 | 310 | Customer | 69646 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003245 |  | METRO EAST | SHAWNEE | 7432:ST GREGORY | ST_GREGORY_3231 | 743231 | 2020-02-10 18:59 | 2020-02-10 19:34 | 35.25 | 1 | 1 | 35.25 | 1 | CANCELLED | 57 | CANCELLED | SHAWNEE | BRENTWOOD APTS-1901 W MCARTHUR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 114498 | 22140 | 4100 | 1208 | 4.09e-05 | 1.1603e-06 | 35.25 | 1 | 310 | Customer | 12457 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003251 | PD-02102020-02391 | NORTHEAST | SAPULPA | 3220:KELLYVILLE | KELLYVILLE_2024 | 322024 | 2020-02-10 19:31 | 2020-02-10 20:26 | 54.55 | 1 | 1 | 42.4667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | SAPULPA | 3/4W.OF 66 ON HWY 33,+ 1/8S. | CMI_NORMAL | NO | NO | NO | 861858 | 74152 | 40831 | 2552 | 1581 | 4.9273e-05 | 1.1603e-06 | 42.4667 | 1 | 310 | Load | 19353 | Load | Tran1phOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | OK - 2020
J2002.003254 |  | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5629 | 865629 | 2020-02-10 19:48 | 2020-02-10 20:13 | 25.18 | 1 | 1 | 25.1833 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1513 SE.47 PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159262 | 102226 | 2761 | 736 | 2.922e-05 | 1.1603e-06 | 25.1833 | 1 | 310 | Customer | 25644 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003256 | PD-02102020-02399 | SOUTHERN | SULPHUR | 5705:SULPHUR | SULPHUR_521 | 570521 | 2020-02-10 20:23 | 2020-02-10 21:43 | 79.68 | 1 | 1 | 79.6833 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | SULPHUR | 17 E.VINITA WA | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861858 | 77694 | 6817 | 3635 | 757 | 9.2455e-05 | 1.1603e-06 | 79.6833 | 1 | 310 | Customer | 3998 | Load | Tran1phOH | JOE LOFTIS | 918-884-5349 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003267 |  | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5822 | 845822 | 2020-02-10 22:08 | 2020-02-11 00:37 | 148.55 | 23 | 13 | 2546.4833 | 5 | ELECTRICAL TRACKING | 37 | CONDUCTOR PRIMARY - OH | SPENCER | DOUGLAS BL + .7MNNE.50 | CMI_NORMAL | NO | NO | NO | 861858 | 114498 | 71252 | 2984 | 935 | 0.0029546 | 2.6687e-05 | 110.7167 | 1 | 310 | Mainline | 21085 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-10 | 2020 |  | #N/A
J2002.003270 | PD-02102020-02409 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_769 | 870769 | 2020-02-10 22:17 | 2020-02-11 02:30 | 253.17 | 6 | 15 | 308.1 | 4 | DETERIORATION | 2 | TRANSFORMER OH | NORMAN | 201 E.HADDOCK | CMI_NORMAL | NO | NO | NO | 861858 | 159262 | 57036 | 11844 | 2307 | 0.00035748 | 6.9617e-06 | 51.35 | 1 | 310 | Load | 36447 | Load | Tran1phOH | COLBY T LLOYD | 405-312-0110 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003273 | PD-02102020-02412 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5134 | 815134 | 2020-02-10 22:32 | 2020-02-10 23:40 | 68.17 | 1 | 1 | 68.1667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 825 BROOKWOOD DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861858 | 159262 | 102226 | 13941 | 2469 | 7.9093e-05 | 1.1603e-06 | 68.1667 | 1 | 310 | Customer | 48909 | Load | Tran1phPad | DARREN L STOCKTON | 918-777-1697 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-10 | 2020 |  | #N/A
J2002.003291 | PD-02112020-00006 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_864 | 830864 | 2020-02-11 02:56 | 2020-02-11 07:29 | 272.28 | 14 | 10 | 2321.3167 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | EDMOND | .5W PORTLAND + NW.234 | CMI_NORMAL | NO | NO | NO | 861858 | 168329 | 148491 | 19412 | 2762 | 0.0026934 | 1.6244e-05 | 165.8083 | 1 | 310 | Mainline | 24432 | Fuse | FuseRiser | BAD ORDER PRIMARY RES COORD | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | OK - 2021
J2002.003294 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_864 | 830864 | 2020-02-11 03:03 | 2020-02-11 05:42 | 159.3 | 4 | 4 | 491.15 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | EDMOND | 130 NW.ST. LUCIA | CMI_NORMAL | NO | NO | NO | 861858 | 168329 | 148491 | 19412 | 2762 | 0.00056987 | 4.6411e-06 | 122.7875 | 1 | 310 | Secondary | 69443 | Load | Tran1phPad | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | OK - 2021
J2002.003316 | PD-02112020-00014 | METRO WEST | WEST | 8359:YUKON | YUKON_5922 | 835922 | 2020-02-11 06:57 | 2020-02-11 08:14 | 76.85 | 1 | 1 | 40.4361 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | YUKON | 400 S.RANCHWOOD BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 128959 | 116173 | 6434 | 1640 | 4.6911e-05 | 1.1601e-06 | 40.4361 | 1 | 310 | Customer | 38787 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | #N/A
J2002.003321 | PD-02112020-00027 | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2163 | 892163 | 2020-02-11 07:36 | 2020-02-11 12:11 | 274.9 | 1 | 1 | 264.85 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 3/8ME-SH 92.51/8MN-SW 59TH | CMI_NORMAL | NO | NO | NO | 861981 | 128959 | 12786 | 3198 | 1146 | 0.00030726 | 1.1601e-06 | 264.85 | 1 | 310 | Customer | 44429 | Load | Tran1phPad | BEAU S HUDSON | 405-306-8284 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | OK - 2021
J2002.003323 | PD-02112020-00034 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-02-11 07:53 | 2020-02-11 09:48 | 115.38 | 10 | 3 | 1144 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | MOUNTAINBURG | GODS RANCH RD E-HWY 71 | CMI_NORMAL | NO | NO | NO | 861981 | 82326 | 61259 | 3791 | 2585 | 0.0013272 | 1.1601e-05 | 114.4 | 1 | 310 | Mainline | 3706 | Fuse | FuseOH | KRIS L HALMES | 479-430-9447 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-02-11 | 2020 |  | Ark - Series 2
J2002.003325 | PD-02112020-00033 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6021 | 836021 | 2020-02-11 07:54 | 2020-02-11 09:59 | 124.77 | 1 | 2 | 110.6833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | BETHANY | NW 30 + COUNCIL RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 128959 | 116173 | 5507 | 1451 | 0.00012841 | 1.1601e-06 | 110.6833 | 1 | 310 | Secondary | 7138 | Load | TranOpenDelta | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | #N/A
J2002.003326 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-11 08:03 | 2020-02-11 12:21 | 258.22 | 2 | 0 | 496.2667 | 4 | DETERIORATION | 12 | POLE | 0 | HWY.22 W. @ HWY 252 | CMI_PLANNED | YES | NO | NO | 861981 | 82326 | 61259 | 962 | 491 | 0.00057573 | 2.3202e-06 | 248.1333 | 1 | 0 | Tap | 7876 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-11 | 2020 |  | Ark - Series 2
J2002.003330 |  | NORTHWEST | ALVA | 4705:ALVA | ALVA_523 | 470523 | 2020-02-11 08:12 | 2020-02-11 08:24 | 12.37 | 1 | 1 | 12.3667 | 1 | CANCELLED | 57 | CANCELLED | CAPRON | S-MCKINLEY, .5BE-1ST--CAPRON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 53591 | 5524 | 2439 | 582 | 1.4347e-05 | 1.1601e-06 | 12.3667 | 1 | 310 | Customer | 9253 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | #N/A
J2002.003331 | PD-02112020-00054 | NORTHEAST | MUSKOGEE | 3325:WELLS | WELLS_2549 | 332549 | 2020-02-11 08:15 | 2020-02-11 11:02 | 167.43 | 1 | 2 | 114.6833 | 4 | DETERIORATION | 50 | CONNECTOR | COUNCIL HILL | 1ST & PINE NW CORNER | CMI_NORMAL | NO | NO | NO | 861981 | 74152 | 33321 | 2382 | 1054 | 0.00013305 | 1.1601e-06 | 114.6833 | 1 | 320 | Customer | 244382 | Load | Tran1phOH | JOSH CHENEY | 918-619-3590 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | OK - 2021
J2002.003332 |  | METRO EAST | EAST | 8471:NE 30TH ST | NE_30TH_ST_7121 | 847121 | 2020-02-11 08:15 | 2020-02-11 08:26 | 11.45 | 1 | 2 | 11.45 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2000 N.VINE AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 114498 | 71252 | 2404 | 343 | 1.3283e-05 | 1.1601e-06 | 11.45 | 1 | 310 | Customer | 26101 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | OK - 2022
J2002.003334 | PD-02112020-00057 | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_924 | 910924 | 2020-02-11 08:18 | 2020-02-11 09:02 | 44.17 | 1 | 1 | 41.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 3500 JENNY-LIND | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 82326 | 61259 | 5015 | 1724 | 4.8145e-05 | 1.1601e-06 | 41.5 | 1 | 310 | Customer | 714 | Load | Tran3phWye | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | Ark - Series 3
J2002.003337 | PD-02112020-00063 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7424 | 847424 | 2020-02-11 08:21 | 2020-02-11 09:11 | 50.38 | 1 | 1 | 50.3833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1225 NE.46 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 168329 | 148491 | 6171 | 2199 | 5.8451e-05 | 1.1601e-06 | 50.3833 | 1 | 310 | Customer | 10466 | Load | Tran1phOH | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | OK - 2020
J2002.003335 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3829 | 913829 | 2020-02-11 08:21 | 2020-02-11 12:41 | 260.12 | 14 | 10 | 3573.2667 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 1911 S.T | CMI_PLANNED | YES | NO | NO | 861981 | 82326 | 61259 | 2944 | 1190 | 0.0041454 | 1.6242e-05 | 255.2333 | 1 | 308 | Load | 6622 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-11 | 2020 |  | Ark - Series 2
J2002.003336 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1522 | 921522 | 2020-02-11 08:21 | 2020-02-11 13:54 | 333.05 | 2 | 2 | 648.15 | 4 | DETERIORATION | 12 | POLE | CHARLESTON | 0 | CMI_PLANNED | YES | NO | NO | 861981 | 82326 | 61259 | 962 | 471 | 0.00075193 | 2.3202e-06 | 324.075 | 1 | 308 | Mainline |  | 0 | 0 | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-11 | 2020 |  | Ark - Series 2
J2002.003338 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-11 08:25 | 2020-02-11 16:04 | 458.8 | 2 | 2 | 857.9833 | 4 | DETERIORATION | 12 | POLE | LAMAR | LAMAR | CMI_PLANNED | YES | NO | NO | 861981 | 82326 | 7555 | 733 | 0 | 0.00099536 | 2.3202e-06 | 428.9917 | 1 | 308 | Load | 12291 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | #N/A
J2002.003340 | PD-02112020-00058 | METRO EAST | SEMINOLE | 7208:CYPRESS | CYPRESS_821 | 720821 | 2020-02-11 08:30 | 2020-02-11 11:28 | 178.35 | 1 | 1 | 166.2667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | HOLDENVILLE | 1MW-48 ON 270 2MS 3/4MW N.S. | CMI_NORMAL | NO | NO | NO | 861981 | 114498 | 13624 | 2522 | 1090 | 0.00019289 | 1.1601e-06 | 166.2667 | 1 | 310 | Load | 21184 | Load | Tran1phOH | DELBERT HISAW | 405-683-1721 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | #N/A
J2002.003351 |  | NORTHWEST | ENID | 4518:MENO TAP | MENO TAP 22 | 451822 | 2020-02-11 08:58 | 2020-02-11 12:10 | 192.08 | 2 | 1 | 371.9 | 4 | DETERIORATION | 12 | POLE | LAHOMA | 2W 1/8 N LAHOMA | CMI_PLANNED | YES | NO | NO | 861981 | 53591 | 37630 | 1332 | 830 | 0.00043145 | 2.3202e-06 | 185.95 | 1 | 308 | Load | 11751 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003354 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-11 09:05 | 2020-02-11 11:31 | 145.95 | 12 | 4 | 1645 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | FORT SMITH | S/WINDBROOK, E/VICKERY | CMI_PLANNED | YES | NO | NO | 861981 | 82326 | 61259 | 1458 | 1240 | 0.0019084 | 1.3921e-05 | 137.0833 | 1 | 308 | Load | 234097 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | Ark - Series 2
J2002.003355 | PD-02112020-00082 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2225 | 832225 | 2020-02-11 09:06 | 2020-02-11 10:35 | 89.42 | 1 | 1 | 89.4167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2100 NW.27 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 168329 | 148491 | 9180 | 2040 | 0.00010373 | 1.1601e-06 | 89.4167 | 1 | 310 | Customer | 27431 | Load | Tran1phOH | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | OK - 2021
J2002.003358 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-02-11 09:14 | 2020-02-11 12:33 | 198.7 | 6 | 2 | 1046 | 4 | DETERIORATION | 12 | POLE | LAVACA | 2307 BARBARA LANE LAVACA,ARK | CMI_PLANNED | YES | NO | NO | 861981 | 82326 | 61259 | 2740 | 2128 | 0.0012135 | 6.9607e-06 | 174.3333 | 1 | 308 | Load | 12966 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | Ark - Series 2
J2002.003363 | PD-02112020-00092 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2122 | 822122 | 2020-02-11 09:14 | 2020-02-11 11:40 | 145.53 | 1 | 1 | 145.5333 | 3 | DAMAGED BY PUBLIC | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 4021 NW.18 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 168329 | 148491 | 9251 | 1838 | 0.00016884 | 1.1601e-06 | 145.5333 | 1 | 320 | Customer | 23134 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | OK - 2020
J2002.003362 | PD-02112020-00089 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5031 | 865031 | 2020-02-11 09:15 | 2020-02-11 15:21 | 365.97 | 1 | 1 | 358.4667 | 25 | LIGHTNING | 36 | CONDUCTOR PRIMARY - UG | MIDWEST CITY | 213 E.ELM ST | CMI_NORMAL | NO | NO | NO | 861981 | 114498 | 71252 | 8633 | 1597 | 0.00041586 | 1.1601e-06 | 358.4667 | 1 | 310 | Load | 37780 | Load | Tran3phPadWye | DAVID M CLEMMONS | 405-777-8355 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | OK - 2022
J2002.003364 | PD-02112020-00091 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4035 | 834035 | 2020-02-11 09:17 | 2020-02-11 10:29 | 72 | 1 | 1 | 18.2348 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | *400 E MACARTHUR-400 N HEFNER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 128959 | 116173 | 10845 | 1423 | 2.1155e-05 | 1.1601e-06 | 18.2348 | 1 | 320 | Customer | 73182 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003366 | PD-02112020-00094 | ARKANSAS | POTEAU | 3509:PANAMA | PANAMA 21 | 350921 | 2020-02-11 09:20 | 2020-02-11 09:59 | 39.23 | 1 | 1 | 36.9 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | PANAMA | N END OF INDIANA ST. PANAMA | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861981 | 82326 | 13512 | 1390 | 821 | 4.2808e-05 | 1.1601e-06 | 36.9 | 1 | 310 | Load | 16819 | Load | Tran1phOH | JOHN MEEH | 918-413-0959 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | #N/A
J2002.003368 |  | NORTHEAST | SAPULPA | 7614:KNIPE | KNIPE_1422 | 761422 | 2020-02-11 09:32 | 2020-02-11 10:07 | 35.12 | 8 | 8 | 280.5292 | 4 | DETERIORATION | 12 | POLE | PERKINS | 522 E.CHANTRY | CMI_PLANNED | YES | NO | NO | 861981 | 74152 | 40831 | 1826 | 1036 | 0.00032545 | 9.2809e-06 | 35.0662 | 1 | 310 | Load | 47270 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003370 | PD-02112020-00098 | METRO EAST | SHAWNEE | 7432:ST GREGORY | ST_GREGORY_3231 | 743231 | 2020-02-11 09:32 | 2020-02-11 10:33 | 60.92 | 1 | 1 | 60.9167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SHAWNEE | BRENTWOOD APTS-1901 W MCARTHUR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 114498 | 22140 | 4100 | 1208 | 7.0671e-05 | 1.1601e-06 | 60.9167 | 1 | 310 | Customer | 18639 | Load | Tran1phPad | BRYAN K TATUM | 405-659-0746 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003377 |  | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_863 | 550863 | 2020-02-11 09:47 | 2020-02-11 12:11 | 143.85 | 3 | 0 | 290.8 | 4 | DETERIORATION | 12 | POLE | 0 | HWY 70 AND LAKE WOOD RANCHETTE | CMI_PLANNED | YES | NO | NO | 861981 | 77694 | 15518 | 1105 | 623 | 0.00033736 | 3.4804e-06 | 96.9333 | 1 | 0 | Load | 26017 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003379 |  | METRO SOUTH | SOUTH | 8722:MILLENNIUM | MILLENNIUM_2224 | 872224 | 2020-02-11 09:52 | 2020-02-11 11:23 | 91.33 | 9 | 3 | 730.5 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | NORMAN | LOT 7 BLK 3 SHADOWLAKE SEC 2 | CMI_PLANNED | YES | NO | NO | 861981 | 159262 | 57036 | 4206 | 640 | 0.00084747 | 1.0441e-05 | 81.1667 | 1 | 310 | Load | 101517 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003382 | PD-02112020-00119 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2022 | 822022 | 2020-02-11 09:58 | 2020-02-11 12:01 | 123.02 | 1 | 1 | 17.0548 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2533 NW 13TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 168329 | 148491 | 6036 | 2119 | 1.9786e-05 | 1.1601e-06 | 17.0548 | 1 | 310 | Customer | 1652 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | OK - 2020
J2002.003389 |  | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1924 | 851924 | 2020-02-11 10:22 | 2020-02-11 11:47 | 85.12 | 5 | 4 | 339.1667 | 4 | DETERIORATION | 12 | POLE | MIDWEST CITY | 514 N.DOUGLAS BL | CMI_PLANNED | YES | NO | NO | 861981 | 114498 | 71252 | 12468 | 1608 | 0.00039347 | 5.8006e-06 | 67.8333 | 1 | 308 | Load | 4365 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003390 |  | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1422 | 911422 | 2020-02-11 10:28 | 2020-02-11 10:50 | 21.37 | 1 | 1 | 21.3667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 5018 JOHNSON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 82326 | 61259 | 4742 | 1955 | 2.4788e-05 | 1.1601e-06 | 21.3667 | 1 | 310 | Customer | 9075 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-11 | 2020 |  | Ark - Series 1
J2002.003403 | PD-02112020-00176 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5127 | 815127 | 2020-02-11 10:57 | 2020-02-11 12:36 | 99.32 | 20 | 9 | 1943 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | SW 97 AND ROSS | CMI_NORMAL | NO | NO | NO | 861981 | 159262 | 102226 | 13941 | 1995 | 0.0022541 | 2.3202e-05 | 97.15 | 1 | 310 | Mainline | 20912 | Fuse | FuseRiser | DERICK WINSETT | 405-650-6102 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003398 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5127 | 815127 | 2020-02-11 10:57 | 2020-02-11 10:57 | 0.02 | 2039 | 0 | 33.9833 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 8101 S PENNSYLVANIA AVE | CMI_MOMENTARY | YES | NO | NO | 861981 | 159262 | 102226 | 13941 | 1995 | 3.9425e-05 | 0.0023655 | 0.016667 | 1 | 0 | Feeder | PENNSYLV_5127 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003401 |  | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3722 | 913722 | 2020-02-11 10:58 | 2020-02-11 11:21 | 23.03 | 1 | 1 | 23.0333 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 7500 FREE-FERRY RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 82326 | 61259 | 4573 | 1442 | 2.6721e-05 | 1.1601e-06 | 23.0333 | 1 | 310 | Customer | 17178 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | Ark - Series 3
J2002.003411 | PD-02112020-00189 | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-02-11 11:24 | 2020-02-11 12:33 | 68.5 | 1 | 1 | 14.8449 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | S OF NW.10 + W OF DAVIS ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 128959 | 116173 | 3412 | 2042 | 1.7222e-05 | 1.1601e-06 | 14.8449 | 1 | 310 | Customer | 70831 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003416 | PD-02112020-00211 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-02-11 11:56 | 2020-02-11 12:43 | 46.65 | 1 | 1 | 14.1111 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2729 JANENE DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 114498 | 71252 | 11645 | 3538 | 1.6371e-05 | 1.1601e-06 | 14.1111 | 1 | 310 | Customer | 51102 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003420 | PD-02112020-00225 | METRO NORTH | GUTHRIE | 8814:PINE STREET | PINE_STREET_1429 | 881429 | 2020-02-11 12:15 | 2020-02-11 13:13 | 57.52 | 1 | 1 | 57.5167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | GUTHRIE | 1123 E.NOBLE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 168329 | 19838 | 3105 | 1714 | 6.6726e-05 | 1.1601e-06 | 57.5167 | 1 | 320 | Customer | 40064 | Load | Tran1phOH | JOSEPH WAYNE POOL | 405-919-2253 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003422 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 22 | 320922 | 2020-02-11 12:19 | 2020-02-11 12:26 | 7.08 | 1 | 1 | 7.0833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BIXBY | SHADOW VALLEY TR CT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 74152 | 40831 | 2755 | 1312 | 8.2175e-06 | 1.1601e-06 | 7.0833 | 1 | 310 | Customer | 46695 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | OK - 2021
J2002.003427 | PD-02112020-00232 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3722 | 833722 | 2020-02-11 12:34 | 2020-02-11 13:25 | 50.78 | 15 | 15 | 688.125 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1146 NW.79 | CMI_NORMAL | NO | NO | NO | 861981 | 168329 | 148491 | 5768 | 1111 | 0.00079831 | 1.7402e-05 | 45.875 | 1 | 310 | Load | 12332 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | OK - 2022
J2002.003433 | PD-02112020-00242 | NORTHEAST | MUSKOGEE | 3111:FIVE TRIBES | FIVE_TRIBES_1131 | 311131 | 2020-02-11 12:58 | 2020-02-11 13:47 | 49.43 | 1 | 1 | 47.7667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MUSKOGEE | 1020 SOUTH "C" STREET | CMI_NORMAL | NO | NO | NO | 861981 | 74152 | 33321 | 1683 | 817 | 5.5415e-05 | 1.1601e-06 | 47.7667 | 1 | 310 | Load | 17220 | Load | Tran1phOH | REID R WILLIAMS | 512-618-8800 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-02-11 | 2020 |  | #N/A
J2002.003434 |  | METRO EAST | SEMINOLE | 7312:JUMPER CREEK | JUMPER_CREEK_1225 | 731225 | 2020-02-11 12:59 | 2020-02-11 14:03 | 64.77 | 1 | 0 | 64.7737 | 4 | DETERIORATION | 2 | TRANSFORMER OH | 0 | ONE THIRD MILE S OF EW 140 RD ON NS 545 RD | CMI_NORMAL | NO | NO | NO | 861981 | 114498 | 13624 | 1217 | 332 | 7.5145e-05 | 1.1601e-06 | 64.7737 | 1 | 0 | Load | 20044 | Load | TranOpenDelta | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | OK - 2021
J2002.003435 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5127 | 815127 | 2020-02-11 13:05 | 2020-02-11 13:06 | 1.08 | 5 | 0 | 5.4512 | 1 | CANCELLED | 57 | CANCELLED | 0 | 0 | CMI_MOMENTARY | YES | NO | NO | 861981 | 159262 | 102226 | 13941 | 1995 | 6.3241e-06 | 5.8006e-06 | 1.0902 | 1 | 0 | Mainline | 62675-2 | Switch | SwitchDefault | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003437 |  | ARKANSAS | OZARK | 9410:IGO | IGO_1022 | 941022 | 2020-02-11 13:10 | 2020-02-11 13:31 | 20.73 | 1 | 2 | 20.7333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | COAL HILL | COALHILL, CAROLINA + RIVER RD. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 82326 | 7555 | 1508 | 1204 | 2.4053e-05 | 1.1601e-06 | 20.7333 | 1 | 310 | Customer | 19217 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-11 | 2020 |  | Ark - Series 2
J2002.003442 | PD-02112020-00289 | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_622 | 410622 | 2020-02-11 13:25 | 2020-02-11 14:27 | 62.4 | 1 | 1 | 62.4 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ENID | 811 E.ASH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 53591 | 37630 | 6030 | 1512 | 7.2391e-05 | 1.1601e-06 | 62.4 | 1 | 310 | Customer | 5743 | Load | Tran1phOH | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | #N/A
J2002.003443 |  | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_861 | 550861 | 2020-02-11 13:28 | 2020-02-11 15:24 | 115.97 | 2 | 1 | 224.9333 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | DURANT | SILO RD/HWY 78 .6N | CMI_PLANNED | YES | NO | NO | 861981 | 77694 | 15518 | 1105 | 482 | 0.00026095 | 2.3202e-06 | 112.4667 | 1 | 308 | Load | 144686 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003444 | PD-02112020-00285 | METRO WEST | WEST | 8342:BRADEN PARK | BRADEN_PARK_4223 | 834223 | 2020-02-11 13:29 | 2020-02-11 14:35 | 66.07 | 1 | 1 | 66.0667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 6200 W. Memorial Rd. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 128959 | 116173 | 3402 | 1783 | 7.6645e-05 | 1.1601e-06 | 66.0667 | 1 | 320 | Customer | 387518 | Load | Tran3phPadWye | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | OK - 2022
J2002.003446 |  | ARKANSAS | FORT SMITH | 9111:MASSARD | MASSARD_1131 | 911131 | 2020-02-11 13:33 | 2020-02-11 13:46 | 13.33 | 1 | 1 | 13.3333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 908 P | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 82326 | 61259 | 4983 | 1565 | 1.5468e-05 | 1.1601e-06 | 13.3333 | 1 | 310 | Customer | 13810 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-11 | 2020 |  | Ark - Series 3
J2002.003447 |  | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1724 | 911724 | 2020-02-11 13:39 | 2020-02-11 16:48 | 188.82 | 5 | 3 | 865.25 | 4 | DETERIORATION | 2 | TRANSFORMER OH | BARLING | 150 S-S.A,100 W-S.11, BARLING | CMI_PLANNED | YES | NO | NO | 861981 | 82326 | 61259 | 4246 | 611 | 0.0010038 | 5.8006e-06 | 173.05 | 1 | 308 | Load | 3429 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-11 | 2020 |  | #N/A
J2002.003449 | PD-02112020-00297 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1226 | 831226 | 2020-02-11 13:45 | 2020-02-11 14:40 | 54.97 | 1 | 1 | 33.9532 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1701 NW.46 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 168329 | 148491 | 7755 | 1748 | 3.939e-05 | 1.1601e-06 | 33.9532 | 1 | 310 | Customer | 85510 | Load | Tran1phPad | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | OK - 2021
J2002.003453 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-02-11 13:52 | 2020-02-11 17:54 | 241.98 | 2 | 1 | 414.8 | 4 | DETERIORATION | 12 | POLE | BARLING | 4TH AVE. & 3RD STR. | CMI_PLANNED | YES | NO | NO | 861981 | 82326 | 61259 | 2740 | 2128 | 0.00048122 | 2.3202e-06 | 207.4 | 1 | 308 | Load | 19271 | Load | TranOpenDelta | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | Ark - Series 2
J2002.003456 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-11 13:56 | 2020-02-11 14:54 | 57.93 | 1 | 1 | 43.7833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | STONE HILL | CHARLESTN AR 72933 | CMI_PLANNED | YES | NO | NO | 861981 | 82326 | 61259 | 962 | 491 | 5.0794e-05 | 1.1601e-06 | 43.7833 | 1 | 308 | Load | 5754 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-11 | 2020 |  | Ark - Series 2
J2002.003467 |  | ARKANSAS | FORT SMITH | 9508:WHITESIDE | WHITESIDE_821 | 950821 | 2020-02-11 14:05 | 2020-02-11 15:20 | 74.95 | 6 | 6 | 438.25 | 4 | DETERIORATION | 12 | POLE | VAN BUREN | 13 + MARY-ALLEN | CMI_PLANNED | YES | NO | NO | 861981 | 82326 | 61259 | 1920 | 1281 | 0.00050842 | 6.9607e-06 | 73.0417 | 1 | 308 | Load | 8448 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-11 | 2020 |  | Ark - Series 2
J2002.003468 | PD-02112020-00312 | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5822 | 845822 | 2020-02-11 14:07 | 2020-02-11 15:27 | 80.18 | 1 | 1 | 80.1833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6927 N POST RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 114498 | 71252 | 2984 | 935 | 9.3022e-05 | 1.1601e-06 | 80.1833 | 1 | 310 | Load | 68570 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | #N/A
J2002.003469 | PD-02112020-00316 | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_922 | 910922 | 2020-02-11 14:08 | 2020-02-11 15:03 | 54.78 | 3 | 3 | 146.7 | 5 | ELECTRICAL TRACKING | 21 | FUSE - TRANSFORMER | FORT SMITH | 4303 S.24 | CMI_NORMAL | NO | NO | NO | 861981 | 82326 | 61259 | 5015 | 960 | 0.00017019 | 3.4804e-06 | 48.9 | 1 | 310 | Load | 11016 | Load | Tran1phOH | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | Ark - Series 3
J2002.003470 | PD-02112020-00315 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1522 | 811522 | 2020-02-11 14:17 | 2020-02-11 15:03 | 46.4 | 1 | 1 | 7.1816 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2709 SW.31 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 159262 | 102226 | 6070 | 1945 | 8.3315e-06 | 1.1601e-06 | 7.1816 | 1 | 310 | Customer | 6424 | Load | Tran1phOH | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | OK - 2022
J2002.003476 | PD-02112020-00321 | METRO EAST | SHAWNEE | 7435:MISSION HILL | MISSION HILL 24 | 743524 | 2020-02-11 14:29 | 2020-02-11 15:49 | 80 | 1 | 1 | 80 | 4 | DETERIORATION | 50 | CONNECTOR | SHAWNEE | 236 S.CENTER | CMI_NORMAL | NO | NO | NO | 861981 | 114498 | 22140 | 948 | 948 | 9.2809e-05 | 1.1601e-06 | 80 | 1 | 320 | Customer | 2401 | Load | Tran1phOH | BRYAN K TATUM | 405-659-0746 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | OK - 2021
J2002.003478 |  | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1623 | 581623 | 2020-02-11 14:32 | 2020-02-11 15:16 | 43.37 | 15 | 1 | 612.5 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | ADA | 322 E.17 | CMI_PLANNED | YES | NO | NO | 861981 | 77694 | 11523 | 3464 | 1654 | 0.00071057 | 1.7402e-05 | 40.8333 | 1 | 308 | Load | 2811 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003481 | PD-02112020-00339 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-02-11 14:44 | 2020-02-11 16:18 | 93.9 | 1 | 1 | 93.9 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MOUNTAINBURG | MTNBURG AR 72946 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 82326 | 61259 | 3791 | 2585 | 0.00010894 | 1.1601e-06 | 93.9 | 1 | 311 | Customer | 10454 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-11 | 2020 |  | Ark - Series 2
J2002.003485 | PD-02112020-00342 | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-02-11 14:55 | 2020-02-11 17:05 | 129.77 | 1 | 2 | 129.7667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MUSTANG | 844 W.HWY 152 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 128959 | 116173 | 18283 | 4430 | 0.00015054 | 1.1601e-06 | 129.7667 | 1 | 310 | Load | 76725 | Load | Tran3phWye | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | OK - 2022
J2002.003490 | PD-02112020-00360 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_861 | 830861 | 2020-02-11 15:22 | 2020-02-11 16:38 | 76.15 | 1 | 1 | 72.1333 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 6824 Big Spring Dr | CMI_EQUIP_EXCLUSION | YES | NO | NO | 861981 | 168329 | 148491 | 19412 | 3948 | 8.3683e-05 | 1.1601e-06 | 72.1333 | 1 | 310 | Customer | 389034 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003493 | PD-02112020-00369 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5138 | 815138 | 2020-02-11 15:31 | 2020-02-11 15:55 | 24.15 | 1 | 1 | 24.15 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7607 S.DOUGLAS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 159262 | 102226 | 13941 | 1416 | 2.8017e-05 | 1.1601e-06 | 24.15 | 1 | 310 | Customer | 48978 | Load | Tran1phPad | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003496 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-02-11 15:54 | 2020-02-11 16:01 | 6.18 | 1 | 1 | 6.1833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 551 N COUNCIL RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 128959 | 116173 | 3412 | 2042 | 7.1734e-06 | 1.1601e-06 | 6.1833 | 1 | 310 | Customer | 34639 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003499 |  | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1521 | 811521 | 2020-02-11 16:09 | 2020-02-11 18:34 | 145.43 | 2 | 2 | 131.25 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | 1100 W.IH 40 | CMI_PLANNED | YES | NO | NO | 861981 | 159262 | 102226 | 6070 | 1247 | 0.00015227 | 2.3202e-06 | 65.625 | 1 | 308 | Load | 3191 | Load | TranOpenDelta | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | OK - 2022
J2002.003504 |  | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_524 | 510524 | 2020-02-11 16:36 | 2020-02-11 16:47 | 10.8 | 1 | 1 | 10.8 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ARDMORE | GOLDEN OAKS ADDITION | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 77694 | 23604 | 4778 | 1434 | 1.2529e-05 | 1.1601e-06 | 10.8 | 1 | 310 | Customer | 23708 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | OK - 2021
J2002.003507 |  | ARKANSAS | FORT SMITH | 9111:MASSARD | MASSARD_1121 | 911121 | 2020-02-11 16:51 | 2020-02-11 17:05 | 13.5 | 1 | 1 | 13.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 6701 S.DALLAS 15B | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 82326 | 61259 | 4983 | 1013 | 1.5662e-05 | 1.1601e-06 | 13.5 | 1 | 310 | Customer | 5479 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-11 | 2020 |  | Ark - Series 3
J2002.003512 | PD-02112020-00450 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_622 | 870622 | 2020-02-11 17:21 | 2020-02-11 18:49 | 87.63 | 1 | 1 | 71.7333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 2502 W.BROOKS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 159262 | 57036 | 7375 | 1261 | 8.3219e-05 | 1.1601e-06 | 71.7333 | 1 | 310 | Customer | 39031 | Load | Tran1phPad | THOMAS E COLE | 405-623-9338 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003516 | PD-02112020-00455 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1122 | 511122 | 2020-02-11 17:58 | 2020-02-11 18:35 | 36.82 | 1 | 1 | 34.25 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | DICKSON | 70 3.5E NS | CMI_NORMAL | NO | NO | NO | 861981 | 77694 | 23604 | 2210 | 1207 | 3.9734e-05 | 1.1601e-06 | 34.25 | 1 | 310 | Customer | 10529 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | #N/A
J2002.003518 |  | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4821 | 824821 | 2020-02-11 18:06 | 2020-02-11 18:37 | 30.15 | 14 | 0 | 306.3667 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | YOUNG / NW 9TH | CMI_PLANNED | YES | NO | NO | 861981 | 168346 | 148505 | 4202 | 241 | 0.00035542 | 1.6242e-05 | 21.8833 | 1 | 0 | Mainline | 27071 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | OK - 2022
J2002.003521 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6335 | 816335 | 2020-02-11 18:21 | 2020-02-11 19:52 | 91.08 | 1 | 1 | 91.094 | 23 | CUSTOMER EQUIPMENT | 12 | POLE | MOORE | 900 SW.4 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 159264 | 102234 | 11848 | 1214 | 0.00010568 | 1.1601e-06 | 91.094 | 1 | 308 | Load | 25102 | Load | TranOpenDelta | Crew | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | OK - 2022
J2002.003524 |  | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4029 | 914029 | 2020-02-11 18:34 | 2020-02-11 18:40 | 5.47 | 1 | 1 | 5.4667 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 8509 S.HWY-271 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 82341 | 61272 | 4765 | 1103 | 6.342e-06 | 1.1601e-06 | 5.4667 | 1 | 310 | Customer | 14913 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-11 | 2020 |  | Ark - Series 2
J2002.003526 | PD-02112020-00456 | ARKANSAS | FORT SMITH | 9512:ADABELL ROAD | ADABELL_ROAD_1224 | 951224 | 2020-02-11 18:43 | 2020-02-11 21:09 | 145.52 | 36 | 28 | 4040.4 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | VAN BUREN | WATER PUMP HS VISTAB | CMI_NORMAL | NO | NO | NO | 861981 | 82341 | 61272 | 3125 | 939 | 0.0046873 | 4.1764e-05 | 112.2333 | 1 | 310 | Mainline | 1749 | Fuse | FuseRiser | 1384: NOT FOUND 1384: NOT FOUND | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-11 | 2020 |  | Ark - Series 1, Ark - Series 2
J2002.003533 |  | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2924 | 812924 | 2020-02-11 19:20 | 2020-02-11 19:28 | 7.37 | 1 | 1 | 7.3667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3020 SW.64 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 159264 | 102234 | 6390 | 2130 | 8.5462e-06 | 1.1601e-06 | 7.3667 | 1 | 310 | Customer | 17770 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | #N/A
J2002.003535 | PD-02112020-00461 | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_424 | 580424 | 2020-02-11 20:05 | 2020-02-11 21:40 | 95.47 | 1 | 1 | 95.4667 | 12 | POOR CONNECTION | 50 | CONNECTOR | STONEWALL | S OF MANTOOTH HOMES | CMI_NORMAL | NO | NO | NO | 861981 | 77698 | 11523 | 3417 | 436 | 0.00011075 | 1.1601e-06 | 95.4667 | 1 | 320 | Customer | 1637 | Load | Tran1phOH | CAMERON BRADY | 580-307-7052 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-11 | 2020 |  | OK - 2021
J2002.003536 | PD-02112020-00460 | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3422 | 843422 | 2020-02-11 20:05 | 2020-02-11 20:55 | 49.88 | 1 | 1 | 47.6 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1700 NE.69 | CMI_NORMAL | NO | NO | NO | 861981 | 168346 | 148505 | 1228 | 729 | 5.5222e-05 | 1.1601e-06 | 47.6 | 1 | 310 | Customer | 8174 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | #N/A
J2002.003546 | PD-02112020-00472 | METRO EAST | EAST | 8471:NE 30TH ST | NE_30TH_ST_7122 | 847122 | 2020-02-11 21:05 | 2020-02-11 23:18 | 132.67 | 1 | 2 | 132.6667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FOREST PARK | 3012 NORCREST DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 861981 | 114506 | 71259 | 2404 | 766 | 0.00015391 | 1.1601e-06 | 132.6667 | 1 | 311 | Customer | 9095 | Load | Tran1phOH | DARREN L STOCKTON | 918-777-1697 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-11 | 2020 |  | OK - 2022
J2002.003586 |  | METRO EAST | SEMINOLE | 7505:WEWOKA | WEWOKA 21 | 750521 | 2020-02-12 03:56 | 2020-02-12 03:56 | 0 | 1 | 1 | 0 | 17 | TRANSMISSION OPERATION | 56 | SCADA - LOCKOUT | WEWOKA | 224 E 6TH | CMI_MOMENTARY | YES | NO | NO | 862063 | 114506 | 13626 | 2478 | 1284 | 0 | 1.16e-06 | 0 | 1 | 308 | Load | 4363 | Load | Tran1phOH | [7 empty] | Equipment | N | TRANSMISSION | 69kV | 2020-02-12 | 2020 |  | OK - 2021
J2002.003582 |  | METRO EAST | SEMINOLE | 7208:CYPRESS | CYPRESS_822 | 720822 | 2020-02-12 03:56 | 2020-02-12 03:56 | 0 | 3 | 3 | 0 | 17 | TRANSMISSION OPERATION | 56 | SCADA - LOCKOUT | HOLDENVILLE | 110 N HINCKLEY ST | CMI_MOMENTARY | YES | NO | NO | 862063 | 114506 | 13626 | 2522 | 1432 | 0 | 3.48e-06 | 0 | 1 | 308 | Load | 3213 | Load | TranOpenDelta | [7 empty] | Equipment | N | TRANSMISSION | 69kV | 2020-02-12 | 2020 |  | OK - 2020
J2002.003583 |  | METRO EAST | SEMINOLE | 7208:CYPRESS | CYPRESS_821 | 720821 | 2020-02-12 03:56 | 2020-02-12 03:56 | 0 | 2 | 2 | 0 | 17 | TRANSMISSION OPERATION | 56 | SCADA - LOCKOUT | HOLDENVILLE | 214.5 S BULLITT | CMI_MOMENTARY | YES | NO | NO | 862063 | 114506 | 13626 | 2522 | 1090 | 0 | 2.32e-06 | 0 | 1 | 308 | Load | 4484 | Load | Tran1phOH | [7 empty] | Equipment | N | TRANSMISSION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.003587 |  | METRO EAST | SEMINOLE | 7505:WEWOKA | WEWOKA 21 | 750521 | 2020-02-12 03:56 | 2020-02-12 03:56 | 0 | 1 | 1 | 0 | 17 | TRANSMISSION OPERATION | 56 | SCADA - LOCKOUT | WEWOKA | 1 3/4MW OF WEWOKA ON HWY 270 | CMI_MOMENTARY | YES | NO | NO | 862063 | 114506 | 13626 | 2478 | 1284 | 0 | 1.16e-06 | 0 | 1 | 308 | Load | 19270 | Load | Tran1phOH | [7 empty] | Equipment | N | TRANSMISSION | 69kV | 2020-02-12 | 2020 |  | OK - 2021
J2002.003590 |  | METRO EAST | SEMINOLE | 7506:SASAKWA | SASAKWA 29 | 750629 | 2020-02-12 03:56 | 2020-02-12 04:34 | 37.85 | 1 | 1 | 37.85 | 17 | TRANSMISSION OPERATION | 56 | SCADA - LOCKOUT | SASAKWA | 4MS 1MW SASAKWA | CMI_NORMAL | NO | NO | NO | 862063 | 114506 | 13626 | 300 | 228 | 4.3906e-05 | 1.16e-06 | 37.85 | 1 | 308 | Load | 209721 | Load | Tran1phOH | [7 empty] | Equipment | N | TRANSMISSION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.003588 |  | METRO EAST | SEMINOLE | 7312:JUMPER CREEK | JUMPER_CREEK_1227 | 731227 | 2020-02-12 03:56 | 2020-02-12 04:24 | 28.32 | 1 | 1 | 28.3167 | 17 | TRANSMISSION OPERATION | 56 | SCADA - LOCKOUT | KONAWA | 1/2MS SCARED HEART OK 1/2MN HWY 39 | CMI_NORMAL | NO | NO | NO | 862063 | 114506 | 13626 | 1217 | 885 | 3.2848e-05 | 1.16e-06 | 28.3167 | 1 | 308 | Load | 205714 | Load | Tran1phOH | [7 empty] | Equipment | N | TRANSMISSION | 69kV | 2020-02-12 | 2020 |  | OK - 2021
J2002.003592 |  | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1421 | 911421 | 2020-02-12 04:06 | 2020-02-12 04:25 | 18.97 | 1 | 1 | 18.6833 | 17 | TRANSMISSION OPERATION | 56 | SCADA - LOCKOUT | FORT SMITH | 3720 YOUNG | CMI_NORMAL | NO | NO | NO | 862063 | 82341 | 61272 | 4742 | 1751 | 2.1673e-05 | 1.16e-06 | 18.6833 | 1 | 308 | Customer | 11143 | Load | Tran1phOH | [7 empty] | Equipment | N | TRANSMISSION | 161kV | 2020-02-12 | 2020 |  | Ark - Series 1
J2002.003589 |  | METRO NORTH | GUTHRIE | 8807:CRESCENT | CRESCENT_721 | 880721 | 2020-02-12 04:15 | 2020-02-12 04:15 | 0.05 | 874 | 0 | 43.7 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | CRESCENT | N MERIDIAN AVE + W COUNTY RD 76 | CMI_MOMENTARY | YES | NO | NO | 862063 | 168346 | 19841 | 1768 | 874 | 5.0692e-05 | 0.0010138 | 0.05 | 1 | 0 | Feeder | CRESCENT_721 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.003604 | PD-02122020-00026 | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2523 | 512523 | 2020-02-12 05:36 | 2020-02-12 07:47 | 131.47 | 1 | 2 | 130.75 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | LONE GROVE | GOOSEBERRY AND HWY.70 | CMI_NORMAL | NO | NO | NO | 862063 | 77698 | 23604 | 3308 | 960 | 0.00015167 | 1.16e-06 | 130.75 | 1 | 310 | Customer | 29062 | Load | Tran1phOH | RANDAL G CALLAWAY | 580-220-8449 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | OK - 2021
J2002.003610 | PD-02122020-00024 | NORTHEAST | SAPULPA | 3220:KELLYVILLE | KELLYVILLE_2024 | 322024 | 2020-02-12 05:52 | 2020-02-12 08:24 | 152.23 | 5 | 2 | 696.5 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | SAPULPA | 1-1/4 W OF 33 + 66 JCT | CMI_NORMAL | NO | NO | NO | 862063 | 74136 | 40818 | 2553 | 1582 | 0.00080795 | 5.8e-06 | 139.3 | 1 | 310 | Tap | 68278 | Fuse | FuseOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | OK - 2020
J2002.003765 | PD-02122020-00186 | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3422 | 843422 | 2020-02-12 05:58 | 2020-02-12 11:03 | 305.83 | 388 | 157 | 26807.1081 | 5 | ELECTRICAL TRACKING | 28 | CROSSARM | OKLAHOMA CITY | 0 | CMI_NORMAL | NO | NO | NO | 862063 | 168346 | 148505 | 1228 | 729 | 0.031096 | 0.00045008 | 69.0905 | 1 | 310 | Feeder | DEEP FORK 22 | Breaker | 0 | GARY D FRANKLIN | 405-626-2420 | [5 empty] | Equipment | N | SUBSTATION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.003629 |  | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3422 | 843422 | 2020-02-12 06:03 | 2020-02-12 09:38 | 215.72 | 29 | 9 | 5938.2333 | 22 | WIND | 17 | JUMPER | OKLAHOMA CITY | NS-I44 + EASTERN | CMI_NORMAL | NO | NO | NO | 862063 | 168346 | 148505 | 1228 | 729 | 0.0068884 | 3.364e-05 | 204.7667 | 1 | 310 | Mainline | 9337 | Switch | SwitchOH | [7 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.003623 | PD-02122020-00028 | NORTHWEST | ENID | 4158:FAIRMONT | FAIRMONT_5829 | 415829 | 2020-02-12 06:52 | 2020-02-12 11:07 | 254.8 | 1 | 2 | 121.4167 | 5 | ELECTRICAL TRACKING | 18 | INSULATOR | GARBER | BRECK 3E,1S,3/4E | CMI_NORMAL | NO | NO | NO | 862063 | 53594 | 37633 | 1643 | 1625 | 0.00014084 | 1.16e-06 | 121.4167 | 1 | 320 | Load | 1223 | Load | Tran1phOH | PATRICK R KIFER | 405-509-0114 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | OK - 2021
J2002.003622 |  | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_521 | 560521 | 2020-02-12 06:53 | 2020-02-12 06:53 | 0.02 | 468 | 0 | 7.8 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | PAULS VALLEY | 121 E BRADLEY | CMI_MOMENTARY | YES | NO | NO | 862063 | 77698 | 6226 | 2467 | 468 | 9.0481e-06 | 0.00054288 | 0.016667 | 1 | 0 | Feeder | PAULS_VALLEY_521 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-12 | 2020 |  | OK - 2022
J2002.003628 |  | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6023 | 836023 | 2020-02-12 06:53 | 2020-02-12 07:12 | 18.93 | 1 | 1 | 18.9333 | 1 | CANCELLED | 57 | CANCELLED | BETHANY | 5112 N.ROCKWELL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 128977 | 116187 | 5508 | 1480 | 2.1963e-05 | 1.16e-06 | 18.9333 | 1 | 308 | Customer | 7740 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | OK - 2022
J2002.003625 | PD-02122020-00029 | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_521 | 560521 | 2020-02-12 06:58 | 2020-02-12 07:58 | 60.13 | 3 | 1 | 180.4 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | PAULS VALLEY | NW OF PV HIGH SCHOOL | CMI_NORMAL | NO | NO | NO | 862063 | 77698 | 6226 | 2467 | 468 | 0.00020927 | 3.48e-06 | 60.1333 | 1 | 310 | Mainline | 10135 | Fuse | FuseOH | CHAD A DOTSON | 405-488-5658 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | OK - 2022
J2002.003631 | PD-02122020-00035 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1423 | 311423 | 2020-02-12 07:13 | 2020-02-12 08:13 | 60.48 | 7 | 3 | 1018.15 | 4 | DETERIORATION | 18 | INSULATOR | MUSKOGEE | OFF TAMAROA BET 9 + 10 | CMI_NORMAL | NO | NO | NO | 862063 | 74136 | 33318 | 4574 | 1498 | 0.0011811 | 8.1201e-06 | 145.45 | 1 | 310 | Tap | 26768 | Fuse | FuseOH | GARY MICHAEL KNUPP | 918-577-8564 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | OK - 2020
J2002.003637 | PD-02122020-00084 | METRO SOUTH | SOUTH | 8728:CHERRY CREEK | CHERRY_CREEK_2831 | 872831 | 2020-02-12 07:39 | 2020-02-12 10:22 | 162.8 | 3 | 3 | 468.9 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | NORMAN | 4808 BAKER ST | CMI_NORMAL | NO | NO | NO | 862063 | 159264 | 57030 | 7109 | 1644 | 0.00054393 | 3.48e-06 | 156.3 | 1 | 310 | Secondary | 79734 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.003639 | PD-02122020-00070 | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2163 | 892163 | 2020-02-12 07:48 | 2020-02-12 12:13 | 264.88 | 1 | 1 | 250.6167 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | SW 55 + CASTLERIDGE DR | CMI_NORMAL | NO | NO | NO | 862063 | 128977 | 12790 | 3200 | 1148 | 0.00029072 | 1.16e-06 | 250.6167 | 1 | 320 | Customer | 59731 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | OK - 2021
J2002.003641 |  | NORTHWEST | ENID | 4135:SO 4TH ST | SO_4TH_ST_3524 | 413524 | 2020-02-12 07:54 | 2020-02-12 07:54 | 0.27 | 1614 | 0 | 430.4 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ENID | 2318 S LEONA MITCHELL BLVD | CMI_MOMENTARY | YES | NO | NO | 862063 | 53594 | 37633 | 3099 | 1614 | 0.00049927 | 0.0018723 | 0.26667 | 1 | 0 | Feeder | SOUTH 4_3524 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.003643 | PD-02122020-00054 | NORTHEAST | MUSKOGEE | 3312:CHECOTAH | CHECOTAH 21 | 331221 | 2020-02-12 07:56 | 2020-02-12 08:47 | 50.83 | 1 | 1 | 50.8333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | CHECOTAH | 128 SW MAIN LITE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 74136 | 33318 | 2891 | 1360 | 5.8967e-05 | 1.16e-06 | 50.8333 | 1 | 310 | Customer | 7230 | Load | TranOpenDelta | NICHOLAS SELVIDGE | 918-652-1986 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | OK - 2020
J2002.003648 |  | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3422 | 843422 | 2020-02-12 08:08 | 2020-02-12 11:22 | 193.43 | 1 | 1 | 79.15 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 0 | 0 | 0 | 0 | 9.1815e-05 | 1.16e-06 | 79.15 | 1 | 310 | Customer |  | 0 | 0 | [6 empty] | 06/10/2020 note from burchamc. Reference J2002.003648 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.003649 | PD-02122020-00061 | NORTHWEST | ENID | 4135:SO 4TH ST | SO_4TH_ST_3524 | 413524 | 2020-02-12 08:10 | 2020-02-12 09:11 | 60.65 | 1 | 1 | 60.65 | 3 | DAMAGED BY PUBLIC | 26 | DOWN GUY | ENID | garfield co jail | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 53594 | 37633 | 3099 | 1614 | 7.0354e-05 | 1.16e-06 | 60.65 | 1 | 310 | Load | 222920 | Load | Tran3phPadWye | RONALD K GOSE | 580-541-3131 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.003661 |  | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3621 | 853621 | 2020-02-12 08:49 | 2020-02-12 09:00 | 10.92 | 1 | 1 | 10.9167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1421 NE.8 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 168346 | 148505 | 5934 | 2172 | 1.2663e-05 | 1.16e-06 | 10.9167 | 1 | 310 | Customer | 3972 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | OK - 2022
J2002.003669 |  | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1822 | 931822 | 2020-02-12 09:14 | 2020-02-12 09:29 | 14.4 | 1 | 1 | 14.4 | 1 | CANCELLED | 57 | CANCELLED | ALMA | 111 COUNTRY LANE DR, ALMA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 82341 | 61272 | 2850 | 787 | 1.6704e-05 | 1.16e-06 | 14.4 | 1 | 310 | Customer | 4318 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | Ark - Series 2
J2002.003672 | PD-02122020-00143 | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_523 | 530523 | 2020-02-12 09:18 | 2020-02-12 10:38 | 79.95 | 1 | 1 | 79.0167 | 5 | ELECTRICAL TRACKING | 21 | FUSE - TRANSFORMER | WILSON | 4.5ms of Healdton | CMI_NORMAL | NO | NO | NO | 862063 | 77698 | 6809 | 2131 | 869 | 9.166e-05 | 1.16e-06 | 79.0167 | 1 | 310 | Load | 19837 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.003674 | PD-02122020-00152 | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-02-12 09:20 | 2020-02-12 10:44 | 83.57 | 1 | 2 | 119.85 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | LAVACA | HWY 253 AT NORTH DAVIS | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862063 | 82341 | 61272 | 2741 | 2129 | 0.00013903 | 1.16e-06 | 119.85 | 1 | 310 | Load | 16360 | Load | Tran1phOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | Ark - Series 2
J2002.003673 |  | NORTHWEST | ENID | 4158:FAIRMONT | FAIRMONT_5829 | 415829 | 2020-02-12 09:21 | 2020-02-12 09:45 | 24.77 | 1 | 1 | 24.7667 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | GARBER | 3W-GARBER | CMI_NORMAL | NO | NO | NO | 862063 | 53594 | 37633 | 1643 | 1625 | 2.873e-05 | 1.16e-06 | 24.7667 | 1 | 310 | Load | 6913 | Load | Tran1phOH | [7 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | OK - 2021
J2002.003697 |  | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5134 | 815134 | 2020-02-12 09:36 | 2020-02-12 09:55 | 18.78 | 478 | 183 | 8978.4333 | 6 | HOT LINE HOLD ORDER | 28 | CROSSARM | OKLAHOMA CITY | SW 89TH BTWN GRACE DR AND MCKINLEY AVE | CMI_NORMAL | NO | NO | NO | 862063 | 159264 | 102234 | 13940 | 2470 | 0.010415 | 0.00055448 | 18.7833 | 1 | 310 | Mainline | 348010 | Recloser | Rec3phElectronic | [7 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.003713 |  | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5822 | 845822 | 2020-02-12 09:40 | 2020-02-12 11:50 | 130.38 | 1 | 1 | 130.3833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7100 N E 63RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 114506 | 71259 | 2984 | 935 | 0.00015125 | 1.16e-06 | 130.3833 | 1 | 310 | Load | 72697 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.003750 | PD-02122020-00226 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5127 | 815127 | 2020-02-12 09:44 | 2020-02-12 12:06 | 141.72 | 1 | 1 | 141.7167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 9501 S.PENN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 159264 | 102234 | 13940 | 1995 | 0.00016439 | 1.16e-06 | 141.7167 | 1 | 310 | Load | 74643 | Load | Tran3phWye | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.003757 | PD-02122020-00176 | SOUTHERN | ARDMORE | 5109:ARDMORE WEST | ARDMORE_WEST_931 | 510931 | 2020-02-12 09:49 | 2020-02-12 11:09 | 80.02 | 1 | 1 | 80.0167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ARDMORE | 3W OF I35 ON PRAIRIE VALLEY NS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 77698 | 23604 | 1317 | 702 | 9.282e-05 | 1.16e-06 | 80.0167 | 1 | 320 | Customer | 19489 | Load | Tran1phPad | RANDAL G CALLAWAY | 580-220-8449 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.003758 | PD-02122020-00194 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6023 | 836023 | 2020-02-12 09:51 | 2020-02-12 11:59 | 127.9 | 1 | 1 | 123.8333 | 4 | DETERIORATION | 50 | CONNECTOR | BETHANY | 5112 N.ROCKWELL | CMI_NORMAL | NO | NO | NO | 862063 | 128977 | 116187 | 5508 | 1480 | 0.00014365 | 1.16e-06 | 123.8333 | 1 | 320 | Customer | 7740 | Load | Tran1phOH | STEVEN GILES | 405-227-2802 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | OK - 2022
J2002.003759 | PD-02122020-00225 | METRO NORTH | NORTH | 8430:REMINGTON PARK | REMINGTON_PARK_3024 | 843024 | 2020-02-12 09:53 | 2020-02-12 11:47 | 114.3 | 1 | 1 | 114.3 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | M.L.KING + REMINGTON PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 168346 | 148505 | 848 | 179 | 0.00013259 | 1.16e-06 | 114.3 | 1 | 310 | Customer | 85037 | Load | Tran3phPadWye | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.003761 |  | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_623 | 870623 | 2020-02-12 09:55 | 2020-02-12 12:00 | 124.42 | 1 | 1 | 124.4167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 1318 LINDALE ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 159264 | 57030 | 7375 | 1901 | 0.00014432 | 1.16e-06 | 124.4167 | 1 | 310 | Customer | 46535 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | OK - 2021
J2002.003762 |  | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1222 | 911222 | 2020-02-12 09:57 | 2020-02-12 10:08 | 10.77 | 1 | 1 | 10.7667 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 821 N.13 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 82341 | 61272 | 6612 | 1293 | 1.2489e-05 | 1.16e-06 | 10.7667 | 1 | 310 | Customer | 339 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | Ark - Series 1
J2002.003814 |  | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4029 | 914029 | 2020-02-12 10:01 | 2020-02-12 10:15 | 14.37 | 1 | 1 | 14.3667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 8509 S.HWY-271 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 82341 | 61272 | 4765 | 1103 | 1.6665e-05 | 1.16e-06 | 14.3667 | 1 | 310 | Customer | 14913 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-12 | 2020 |  | Ark - Series 2
J2002.003828 | PD-02122020-00219 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_524 | 510524 | 2020-02-12 10:23 | 2020-02-12 11:26 | 63.27 | 37 | 15 | 2163.2667 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | ARDMORE | CARTER + STOLFA ST | CMI_NORMAL | NO | NO | NO | 862063 | 77698 | 23604 | 4778 | 1434 | 0.0025094 | 4.292e-05 | 58.4667 | 1 | 310 | Mainline | 2647 | Fuse | FuseOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | OK - 2021
J2002.003821 | PD-02122020-00227 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2122 | 822122 | 2020-02-12 10:25 | 2020-02-12 14:18 | 233.3 | 1 | 1 | 233.3 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 4304 NW.11 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862063 | 168346 | 148505 | 9252 | 1837 | 0.00027063 | 1.16e-06 | 233.3 | 1 | 310 | Customer | 1582 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | OK - 2020
J2002.003826 | PD-02122020-00211 | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1222 | 911222 | 2020-02-12 10:29 | 2020-02-12 11:09 | 40.23 | 1 | 1 | 40.2333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | FORT SMITH | 821 N.13 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 82341 | 61272 | 6612 | 1293 | 4.6671e-05 | 1.16e-06 | 40.2333 | 1 | 310 | Customer | 339 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | Ark - Series 1
J2002.003825 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-02-12 10:29 | 2020-02-12 10:29 | 0 | 878 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | FT SMITH | 1904 SOUTH 7TH ST | CMI_MOMENTARY | YES | NO | NO | 862063 | 82341 | 61272 | 2943 | 878 | 0 | 0.0010185 | 0 | 1 | 0 | Feeder | ARKOMA_3824 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-02-12 | 2020 |  | Ark - Series 2
J2002.003840 | PD-02122020-00251 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2225 | 832225 | 2020-02-12 10:42 | 2020-02-12 12:25 | 102.75 | 1 | 1 | 79.0328 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2125 NW.22 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 168346 | 148505 | 9180 | 2040 | 9.1679e-05 | 1.16e-06 | 79.0328 | 1 | 310 | Customer | 13640 | Load | Tran1phOH | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | OK - 2021
J2002.003839 |  | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3022 | 743022 | 2020-02-12 10:43 | 2020-02-12 10:49 | 6.1 | 1 | 1 | 6.1 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SHAWNEE | 1230 N.BROADWAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 114506 | 22140 | 6654 | 2171 | 7.076e-06 | 1.16e-06 | 6.1 | 1 | 310 | Customer | 4476 | Load | TranOHDeltaSplitBank | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | OK - 2020
J2002.003845 | PD-02122020-00265 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-02-12 10:47 | 2020-02-12 12:19 | 92.02 | 1 | 1 | 92.0167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ALMA | 618 STONE MOUNTAIN LOOP | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 82341 | 61272 | 3791 | 2586 | 0.00010674 | 1.16e-06 | 92.0167 | 1 | 310 | Customer | 256731 | Load | Tran1phPad | KRIS L HALMES | 479-430-9447 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-12 | 2020 |  | Ark - Series 2
J2002.003854 | PD-02122020-00255 | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-02-12 10:59 | 2020-02-12 13:08 | 128.95 | 1 | 1 | 128.95 | 5 | ELECTRICAL TRACKING | 23 | FUSE - PRIMARY | ARKOMA | BRADEN BOTTOMS | CMI_NORMAL | NO | NO | NO | 862063 | 82341 | 61272 | 2943 | 878 | 0.00014958 | 1.16e-06 | 128.95 | 1 | 320 | Customer | 13915 | Load | TranOH3phDelta | JOSHUA J SMITH | 479-461-4484 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-12 | 2020 |  | Ark - Series 2
J2002.003861 |  | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1722 | 861722 | 2020-02-12 11:04 | 2020-02-12 11:42 | 37.92 | 1 | 1 | 37.9167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4208 SE.53 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 114506 | 71259 | 6953 | 1788 | 4.3984e-05 | 1.16e-06 | 37.9167 | 1 | 310 | Customer | 48126 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.003862 | PD-02122020-00286 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3222 | 813222 | 2020-02-12 11:04 | 2020-02-12 13:06 | 121.53 | 1 | 2 | 78.4591 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1605 SW.60 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 159264 | 102234 | 7607 | 1484 | 9.1013e-05 | 1.16e-06 | 78.4591 | 1 | 320 | Customer | 25923 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.003876 | PD-02122020-00292 | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3422 | 843422 | 2020-02-12 11:15 | 2020-02-12 12:46 | 90.83 | 1 | 1 | 90.8333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1/8ME-EASTERN ON NE.86 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 168346 | 148505 | 1228 | 729 | 0.00010537 | 1.16e-06 | 90.8333 | 1 | 310 | Customer | 85217 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.003875 | PD-02122020-00280 | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3421 | 843421 | 2020-02-12 11:16 | 2020-02-12 13:01 | 105.42 | 1 | 2 | 90.95 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1329 NE.56 | CMI_NORMAL | NO | NO | NO | 862063 | 168346 | 148505 | 1228 | 499 | 0.0001055 | 1.16e-06 | 90.95 | 1 | 310 | Customer | 35166 | Load | Tran1phOH | BRADLEY SUDBECK | 405-999-6850 | [5 empty] | Other | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.003877 |  | NORTHEAST | MUSKOGEE | 3111:FIVE TRIBES | FIVE_TRIBES_1131 | 311131 | 2020-02-12 11:18 | 2020-02-12 11:41 | 23.12 | 1 | 1 | 23.1167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 3401 S.27 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 74136 | 33318 | 1683 | 817 | 2.6816e-05 | 1.16e-06 | 23.1167 | 1 | 310 | Customer | 12705 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-12 | 2020 |  | #N/A
J2002.003879 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-02-12 11:26 | 2020-02-12 12:30 | 63.92 | 4 | 2 | 197.1333 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 14700 OAKS CROSSING | CMI_PLANNED | YES | NO | NO | 862063 | 159264 | 57030 | 4238 | 3069 | 0.00022868 | 4.64e-06 | 49.2833 | 1 | 308 | Load | 89218 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.003888 | PD-02122020-00285 | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2824 | 312824 | 2020-02-12 11:41 | 2020-02-12 14:06 | 145.23 | 1 | 1 | 145.2333 | 12 | POOR CONNECTION | 50 | CONNECTOR | MUSKOGEE | 922 CREEK | CMI_NORMAL | NO | NO | NO | 862063 | 74136 | 33318 | 5286 | 1617 | 0.00016847 | 1.16e-06 | 145.2333 | 1 | 320 | Customer | 13340 | Load | Tran1phOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-12 | 2020 |  | OK - 2020
J2002.003914 |  | ARKANSAS | POTEAU | 3608:MULDROW | MULDROW 24 | 360824 | 2020-02-12 11:44 | 2020-02-12 12:52 | 68.58 | 2276 | 312 | 133039.7167 | 17 | TRANSMISSION OPERATION | 45 | SUBSTATION CIRCUIT | MULDROW | 703 E SEQUOYAH | CMI_NORMAL | NO | NO | NO | 862063 | 82341 | 13516 | 2275 | 522 | 0.15433 | 0.0026402 | 58.4533 | 1 | 310 | Feeder | MULDROW 24 | Breaker | SubBreaker | [7 empty] | Equipment | N | TRANSMISSION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.003900 |  | NORTHEAST | MUSKOGEE | 3327:VIAN | VIAN 22 | 332722 | 2020-02-12 11:44 | 2020-02-12 12:53 | 69.13 | 780 | 98 | 48503 | 17 | TRANSMISSION OPERATION | 45 | SUBSTATION CIRCUIT | VIAN | I-40 TO VIAN EXIT, HWY 82. GO NORTH ON HWY 82 1/2 MILE TO SANDERS ST, TURN EAST ON SANDERS ST AND GO 1/2 MILE SOUTH INTO SUB | CMI_NORMAL | NO | NO | NO | 862063 | 74136 | 33318 | 780 | 780 | 0.056264 | 0.00090481 | 62.1833 | 1 | 310 | Feeder | VIAN 22 | Breaker | SubBreaker | [7 empty] | Equipment | N | TRANSMISSION | 69kV | 2020-02-12 | 2020 |  | OK - 2021
J2002.004087 | PD-02122020-00297 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1423 | 311423 | 2020-02-12 12:03 | 2020-02-12 13:29 | 86.43 | 1 | 1 | 86.4333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MUSKOGEE | 1111 W BROADWAY AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 74136 | 33318 | 4574 | 1498 | 0.00010026 | 1.16e-06 | 86.4333 | 1 | 310 | Load | 13641 | Load | Tran3phPadWye | REID R WILLIAMS | 512-618-8800 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | OK - 2020
J2002.004091 | PD-02122020-00311 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_866 | 830866 | 2020-02-12 12:15 | 2020-02-12 13:16 | 61.33 | 1 | 2 | 61.3333 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1401 w memorial rd | CMI_NORMAL | NO | NO | NO | 862063 | 168346 | 148505 | 19420 | 4304 | 7.1147e-05 | 1.16e-06 | 61.3333 | 1 | 310 | Load | 387522 | Load | Tran3phPadWye | KIRK REILLEY | 405-550-3062 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.004093 | PD-02122020-00309 | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1421 | 911421 | 2020-02-12 12:20 | 2020-02-12 14:47 | 146.72 | 3 | 3 | 428.25 | 12 | POOR CONNECTION | 50 | CONNECTOR | FORT SMITH | 3321 N.ALBERTPIKE | CMI_NORMAL | NO | NO | NO | 862063 | 82341 | 61272 | 4742 | 1751 | 0.00049677 | 3.48e-06 | 142.75 | 1 | 310 | Secondary | 8515 | Load | Tran1phOH | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-12 | 2020 |  | Ark - Series 1
J2002.004092 |  | NORTHEAST | MUSKOGEE | 3312:CHECOTAH | CHECOTAH 21 | 331221 | 2020-02-12 12:21 | 2020-02-12 17:41 | 319.87 | 3 | 0 | 959.6082 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | CHECOTAH | 128 SW MAIN LITE | CMI_PLANNED | YES | NO | NO | 862063 | 74136 | 33318 | 2891 | 1360 | 0.0011132 | 3.48e-06 | 319.8694 | 1 | 0 | Load | 7230 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | OK - 2020
J2002.004101 | PD-02122020-00312 | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_724 | 510724 | 2020-02-12 12:39 | 2020-02-12 14:36 | 116.8 | 1 | 1 | 106.05 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | ARDMORE | 822 BIXBY | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862063 | 77698 | 23604 | 4516 | 1630 | 0.00012302 | 1.16e-06 | 106.05 | 1 | 310 | Customer | 1496 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.004103 |  | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2024 | 822024 | 2020-02-12 12:40 | 2020-02-12 13:16 | 35.95 | 1 | 1 | 35.95 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1913 NW.PARK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 168346 | 148505 | 6038 | 1776 | 4.1702e-05 | 1.16e-06 | 35.95 | 1 | 310 | Customer | 7565 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | OK - 2020
J2002.004111 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3824 | 913824 | 2020-02-12 12:58 | 2020-02-12 13:23 | 24.28 | 1 | 2 | 24.2833 | 5 | ELECTRICAL TRACKING | 37 | CONDUCTOR PRIMARY - OH | ARKOMA | HWY 9A + POTEAU RBR | CMI_NORMAL | NO | NO | NO | 862063 | 82341 | 61272 | 2943 | 878 | 2.8169e-05 | 1.16e-06 | 24.2833 | 1 | 310 | Load | 13926 | Load | Tran3phWye | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-12 | 2020 |  | Ark - Series 2
J2002.004121 | PD-02122020-00382 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1523 | 811523 | 2020-02-12 13:19 | 2020-02-12 15:28 | 128.67 | 1 | 1 | 128.6667 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 1927 SW.11 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 159264 | 102234 | 6069 | 805 | 0.00014925 | 1.16e-06 | 128.6667 | 1 | 310 | Customer | 1325 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | OK - 2022
J2002.004122 | PD-02122020-00393 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3022 | 743022 | 2020-02-12 13:20 | 2020-02-12 15:36 | 136.45 | 1 | 2 | 129.1 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | SHAWNEE | BENEDICT + BONITA | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862063 | 114506 | 22140 | 6654 | 2171 | 0.00014976 | 1.16e-06 | 129.1 | 1 | 310 | Customer | 3277 | Load | TranOpenDelta | BRYAN K TATUM | 405-659-0746 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | OK - 2020
J2002.004127 | PD-02122020-00375 | NORTHWEST | WOODWARD | 4616:NEWMAN AVE | NEWMAN_AVE_1641 | 461641 | 2020-02-12 13:28 | 2020-02-12 14:47 | 79.22 | 1 | 1 | 79.2167 | 12 | POOR CONNECTION | 50 | CONNECTOR | ARNETT | S-HASKELL,W-ADAMS-- ARNETT | CMI_NORMAL | NO | NO | NO | 862063 | 53594 | 10437 | 2017 | 2017 | 9.1892e-05 | 1.16e-06 | 79.2167 | 1 | 320 | Customer | 11957 | Load | TranOpenDelta | ROY L THRASH | 580-334-5371 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | OK - 2020
J2002.004140 |  | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2823 | 312823 | 2020-02-12 13:47 | 2020-02-12 14:28 | 41.07 | 1 | 2 | 41.0667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 519 S.7TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 74136 | 33318 | 5286 | 1396 | 4.7638e-05 | 1.16e-06 | 41.0667 | 1 | 310 | Customer | 9265 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-12 | 2020 |  | #N/A
J2002.004144 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-12 13:56 | 2020-02-12 15:23 | 87.33 | 3 | 1 | 153.4 | 4 | DETERIORATION | 2 | TRANSFORMER OH | CHARLESTON | HWY 22-900 E-CO LINE | CMI_PLANNED | YES | NO | NO | 862063 | 82341 | 61272 | 962 | 491 | 0.00017795 | 3.48e-06 | 51.1333 | 1 | 308 | Load | 18799 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-12 | 2020 |  | Ark - Series 2
J2002.004154 | PD-02122020-00444 | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-02-12 13:58 | 2020-02-12 16:02 | 123.43 | 1 | 2 | 93.7667 | 5 | ELECTRICAL TRACKING | 20 | FUSE BARREL | BIXBY | 1/4M E OF LEONARD | CMI_NORMAL | NO | NO | NO | 862063 | 74136 | 40818 | 2755 | 1443 | 0.00010877 | 1.16e-06 | 93.7667 | 1 | 310 | Load | 13618 | Load | Tran1phOH | JOSHUA N MCKINNEY | 918-863-6313 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | OK - 2021
J2002.004149 |  | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_626 | 550626 | 2020-02-12 14:02 | 2020-02-12 17:01 | 178.52 | 7 | 6 | 1211.35 | 4 | DETERIORATION | 2 | TRANSFORMER OH | DURANT | 312 S 15TH | CMI_PLANNED | YES | NO | NO | 862063 | 77698 | 15516 | 6748 | 1005 | 0.0014052 | 8.1201e-06 | 173.05 | 1 | 310 | Load | 10561 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.004151 | PD-02122020-00428 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3022 | 743022 | 2020-02-12 14:03 | 2020-02-12 16:12 | 129.1 | 1 | 1 | 109.2333 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | SHAWNEE | 1230 N.BROADWAY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 114506 | 22140 | 6654 | 2171 | 0.00012671 | 1.16e-06 | 109.2333 | 1 | 310 | Customer | 4476 | Load | TranOHDeltaSplitBank | BRYAN K TATUM | 405-659-0746 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | OK - 2020
J2002.004156 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6963 | 846963 | 2020-02-12 14:23 | 2020-02-12 14:58 | 34.68 | 1 | 1 | 34.6833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | BLDG10, LINKS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 168346 | 148505 | 7731 | 1172 | 4.0233e-05 | 1.16e-06 | 34.6833 | 1 | 310 | Customer | 143467 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.004158 | PD-02122020-00463 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_624 | 870624 | 2020-02-12 14:31 | 2020-02-12 15:39 | 68.4 | 1 | 1 | 68.4 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | NORMAN | 2313 CRESTMONT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 159264 | 57030 | 7375 | 649 | 7.9345e-05 | 1.16e-06 | 68.4 | 1 | 310 | Customer | 67319 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.004165 |  | NORTHEAST | MUSKOGEE | 3325:WELLS | WELLS_2542 | 332542 | 2020-02-12 14:46 | 2020-02-12 15:32 | 46.08 | 1 | 1 | 46.0833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | EUFAULA | 231 BELT AVE. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 74136 | 33318 | 2383 | 1325 | 5.3457e-05 | 1.16e-06 | 46.0833 | 1 | 310 | Customer | 390184 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | OK - 2022
J2002.004168 | PD-02122020-00475 | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_624 | 410624 | 2020-02-12 14:48 | 2020-02-12 15:33 | 44.6 | 1 | 1 | 44.6 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ENID | 1524 N.VANBUREN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 53594 | 37633 | 6030 | 1861 | 5.1736e-05 | 1.16e-06 | 44.6 | 1 | 310 | Customer | 6461 | Load | TranOpenDelta | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.004172 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-12 14:53 | 2020-02-12 16:18 | 84.93 | 6 | 6 | 171.8 | 4 | DETERIORATION | 1 | TRANSFORMER UG | CHARLESTON | 332 EASTGATE DR | CMI_PLANNED | YES | NO | NO | 862063 | 82341 | 61272 | 962 | 491 | 0.00019929 | 6.96e-06 | 28.6333 | 1 | 308 | Load | 14428 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-12 | 2020 |  | Ark - Series 2
J2002.004174 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-12 15:22 | 2020-02-12 16:53 | 91.35 | 2 | 0 | 169.7667 | 28 | OTHER (DESCRIBE) | 2 | TRANSFORMER OH | 0 | CHARLESTN AR 72933 | CMI_PLANNED | YES | NO | NO | 862063 | 82341 | 61272 | 962 | 491 | 0.00019693 | 2.32e-06 | 84.8833 | 1 | 0 | Load | 7457 | Load | Tran1phOH | Contractor | [6 empty] | Other | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-12 | 2020 |  | Ark - Series 2
J2002.004179 | PD-02122020-00492 | METRO SOUTH | SOUTH CENTRAL | 8717:TURNER | TURNER_1721 | 871721 | 2020-02-12 15:37 | 2020-02-12 16:13 | 36.23 | 1 | 1 | 36.2333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 716 SW 155 PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 159264 | 102234 | 3085 | 1988 | 4.2031e-05 | 1.16e-06 | 36.2333 | 1 | 320 | Customer | 80405 | Load | Tran1phPad | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.004180 |  | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1722 | 861722 | 2020-02-12 15:46 | 2020-02-12 15:55 | 9.18 | 1 | 1 | 9.1833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4208 SE.53 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 114506 | 71259 | 6953 | 1788 | 1.0653e-05 | 1.16e-06 | 9.1833 | 1 | 310 | Customer | 48126 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.004182 |  | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2022 | 822022 | 2020-02-12 15:52 | 2020-02-12 16:12 | 20.05 | 1 | 1 | 20.05 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1213 N.VILLA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 168346 | 148505 | 6038 | 2121 | 2.3258e-05 | 1.16e-06 | 20.05 | 1 | 310 | Customer | 24207 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | OK - 2020
J2002.004183 |  | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3621 | 853621 | 2020-02-12 15:53 | 2020-02-12 16:07 | 13.57 | 1 | 1 | 13.5667 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 2214 N.PROSPECT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 168346 | 148505 | 5934 | 2172 | 1.5737e-05 | 1.16e-06 | 13.5667 | 1 | 310 | Customer | 2340 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | OK - 2022
J2002.004184 |  | METRO WEST | WEST | 8335:BETHANY | BETHANY_3529 | 833529 | 2020-02-12 15:55 | 2020-02-12 16:15 | 20.45 | 1 | 1 | 20.45 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4112 NW.31 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 128977 | 116187 | 7879 | 2018 | 2.3722e-05 | 1.16e-06 | 20.45 | 1 | 310 | Customer | 21437 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.004189 | PD-02122020-00522 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-02-12 16:11 | 2020-02-12 17:23 | 71.93 | 1 | 1 | 50.1333 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 2233 SW.36 | CMI_NORMAL | NO | NO | NO | 862063 | 159264 | 102234 | 7607 | 2461 | 5.8155e-05 | 1.16e-06 | 50.1333 | 1 | 320 | Customer | 8350 | Load | Tran1phOH | THOMAS E COLE | 405-623-9338 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.004190 |  | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1823 | 931823 | 2020-02-12 16:16 | 2020-02-12 16:36 | 19.78 | 9 | 1 | 150.75 | 4 | DETERIORATION | 39 | BUSHING | ALMA | KINGS POINT CIR, Lot 6 | CMI_PLANNED | YES | NO | NO | 862063 | 82341 | 61272 | 2850 | 1240 | 0.00017487 | 1.044e-05 | 16.75 | 1 | 310 | Load | 16786 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | Ark - Series 2
J2002.004191 | PD-02122020-00520 | NORTHEAST | SAPULPA | 3218:BEGGS | BEGGS_1824 | 321824 | 2020-02-12 16:18 | 2020-02-12 17:57 | 99.18 | 1 | 2 | 95.2833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | BEGGS | 900 N.SAPULPA | CMI_NORMAL | NO | NO | NO | 862063 | 74136 | 40818 | 1844 | 940 | 0.00011053 | 1.16e-06 | 95.2833 | 1 | 310 | Load | 47463 | Load | TranOpenDelta | PHIL STICKLER | 918-991-1321 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | OK - 2020
J2002.004193 | PD-02122020-00528 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5031 | 865031 | 2020-02-12 16:24 | 2020-02-12 17:06 | 41.95 | 1 | 1 | 41.95 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MIDWEST CITY | 500 ADAIR BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 114506 | 71259 | 8633 | 1597 | 4.8662e-05 | 1.16e-06 | 41.95 | 1 | 320 | Customer | 66549 | Load | Tran3phPadWye | KYLE L GOODIN | 405-426-9802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | OK - 2022
J2002.004197 | PD-02122020-00531 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-02-12 16:26 | 2020-02-12 19:18 | 171.88 | 1 | 2 | 150.85 | 22 | WIND | 17 | JUMPER | ARDMORE | .2W MARY NIBL ON HWY70 .2N | CMI_NORMAL | NO | NO | NO | 862063 | 77698 | 23604 | 2209 | 1003 | 0.00017499 | 1.16e-06 | 150.85 | 1 | 310 | Load | 26021 | Load | Tran1phOH | ROBERT J BEARDSLEE | 580-618-2506 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.004194 |  | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-02-12 16:26 | 2020-02-12 16:26 | 0.03 | 1003 | 0 | 33.4333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ARDMORE | 3623 RED CEDAR RD | CMI_MOMENTARY | YES | NO | NO | 862063 | 77698 | 23604 | 2209 | 1003 | 3.8783e-05 | 0.0011635 | 0.033333 | 1 | 0 | Feeder | DRIPPING_SPRI_1129 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.004196 |  | NORTHWEST | ENID | 4112:CHESTNUT | CHESTNUT_1221 | 411221 | 2020-02-12 16:30 | 2020-02-12 16:37 | 7.1 | 1 | 1 | 7.1 | 1 | CANCELLED | 57 | CANCELLED | ENID | 1318 NANCY DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 53594 | 37633 | 2868 | 1115 | 8.2361e-06 | 1.16e-06 | 7.1 | 1 | 310 | Customer | 977 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.004199 | PD-02122020-00543 | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1722 | 861722 | 2020-02-12 16:40 | 2020-02-12 18:40 | 119.73 | 1 | 1 | 119.7333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4300 SE.46 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 114506 | 71259 | 6953 | 1788 | 0.00013889 | 1.16e-06 | 119.7333 | 1 | 310 | Customer | 52726 | Load | Tran1phPad | THOMAS E COLE | 405-623-9338 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.004201 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7429 | 847429 | 2020-02-12 16:51 | 2020-02-12 17:00 | 8.93 | 1 | 1 | 8.9333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1744 E.EUBANKS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 168346 | 148505 | 6170 | 680 | 1.0363e-05 | 1.16e-06 | 8.9333 | 1 | 310 | Customer | 7723 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | OK - 2022
J2002.004202 | PD-02122020-00540 | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_522 | 890522 | 2020-02-12 17:03 | 2020-02-12 19:11 | 127.7 | 1 | 1 | 108.8333 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | EL RENO | 1MW CONCHO | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862063 | 128977 | 12790 | 6967 | 1830 | 0.00012625 | 1.16e-06 | 108.8333 | 1 | 320 | Customer | 58197 | Load | Tran1phOH | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.004208 | PD-02122020-00545 | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-02-12 17:36 | 2020-02-12 19:07 | 91.05 | 1 | 1 | 79.1667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | BIXBY | MW LEONARD | CMI_NORMAL | NO | NO | NO | 862063 | 74136 | 40818 | 2755 | 1443 | 9.1834e-05 | 1.16e-06 | 79.1667 | 1 | 310 | Load | 41822 | Load | Tran1phOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | OK - 2021
J2002.004210 | PD-02122020-00546 | METRO EAST | SHAWNEE | 7407:REMINGTON | REMINGTON 21 | 740721 | 2020-02-12 17:54 | 2020-02-13 00:17 | 383.18 | 1 | 1 | 375.15 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | SHAWNEE | 2424 E.HIGHLAND | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862063 | 114506 | 22140 | 3669 | 2024 | 0.00043518 | 1.16e-06 | 375.15 | 1 | 320 | Load | 14899 | Load | TranOpenDeltaPad | DAVID M CLEMMONS | 405-777-8355 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | OK - 2021
J2002.004213 |  | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-02-12 18:12 | 2020-02-12 18:21 | 9.15 | 1 | 1 | 9.15 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 7901 S COUNCIL RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 128989 | 116198 | 18285 | 4430 | 1.0614e-05 | 1.16e-06 | 9.15 | 1 | 310 | Customer | 38930 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | OK - 2022
J2002.004217 |  | METRO EAST | EAST | 8416:DUNJEE | DUNJEE_1623 | 841623 | 2020-02-12 18:24 | 2020-02-12 21:11 | 167.12 | 8 | 7 | 1074.6667 | 3 | DAMAGED BY PUBLIC | 12 | POLE | NICOMA PARK | 10212 NE 23rd St. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 114515 | 71266 | 3543 | 1991 | 0.0012466 | 9.2801e-06 | 134.3333 | 1 | 308 | Load | 3623 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.004221 |  | METRO EAST | EAST | 8416:DUNJEE | DUNJEE_1623 | 841623 | 2020-02-12 18:27 | 2020-02-12 21:12 | 164.5 | 81 | 53 | 11105.775 | 3 | DAMAGED BY PUBLIC | 12 | POLE | NICOMA PARK | WS AVERY AV SS NE.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 114515 | 71266 | 3543 | 1991 | 0.012883 | 9.3961e-05 | 137.1083 | 1 | 310 | Mainline | 13604 | Fuse | FuseOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.004219 | PD-02122020-00547 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4864 | 824864 | 2020-02-12 18:28 | 2020-02-12 19:19 | 51.27 | 1 | 1 | 51.2667 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 23 | FUSE - PRIMARY | OKLAHOMA CITY | 4325 SW 29th St | CMI_NORMAL | NO | NO | NO | 862063 | 168360 | 148518 | 4203 | 2035 | 5.947e-05 | 1.16e-06 | 51.2667 | 1 | 320 | Load | 332465 | Load | Tran3phPadWye | TONY J ILG | 405-714-7441 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | OK - 2021
J2002.004232 | PD-02122020-00549 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_723 | 870723 | 2020-02-12 19:05 | 2020-02-12 19:43 | 37.8 | 1 | 1 | 37.8 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | NORMAN | 2632 Classen Blvd. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 159281 | 57035 | 11836 | 2044 | 4.3848e-05 | 1.16e-06 | 37.8 | 1 | 310 | Customer | 377830 | Load | Tran3phWye | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.004237 | PD-02122020-00554 | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_622 | 410622 | 2020-02-12 19:26 | 2020-02-12 20:46 | 80.23 | 1 | 1 | 80.2333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ENID | 2700 N.VANBUREN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 53603 | 37639 | 6032 | 1513 | 9.3071e-05 | 1.16e-06 | 80.2333 | 1 | 310 | Customer | 6847 | Load | Tran1phOH | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.004241 | PD-02122020-00555 | METRO EAST | SEMINOLE | 7208:CYPRESS | CYPRESS_821 | 720821 | 2020-02-12 19:44 | 2020-02-12 21:37 | 112.87 | 1 | 1 | 112.8667 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | HOLDENVILLE | 7 FOX RUN | CMI_NORMAL | NO | NO | NO | 862063 | 114515 | 13626 | 2522 | 1090 | 0.00013093 | 1.16e-06 | 112.8667 | 1 | 310 | Load | 227780 | Load | Tran1phOH | DELBERT HISAW | 405-683-1721 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.004243 | PD-02122020-00557 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3221 | 813221 | 2020-02-12 19:54 | 2020-02-12 23:38 | 224.33 | 1 | 1 | 203.1167 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 1140 SW 54TH | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862063 | 159281 | 102246 | 7609 | 2077 | 0.00023562 | 1.16e-06 | 203.1167 | 1 | 310 | Customer | 12572 | Load | Tran1phOH | THOMAS E COLE | 405-623-9338 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.004251 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-02-12 21:13 | 2020-02-12 21:18 | 4.68 | 1 | 1 | 4.6833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1301 W.HEFNER RD | CMI_MOMENTARY | YES | NO | NO | 862063 | 168360 | 148518 | 8790 | 1953 | 5.4327e-06 | 1.16e-06 | 4.6833 | 1 | 310 | Customer | 75516 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | OK - 2021
J2002.004262 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2126 | 822126 | 2020-02-12 22:37 | 2020-02-12 22:43 | 6.62 | 1 | 1 | 6.6167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 801 N.VIRGINIA DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 168360 | 148518 | 9253 | 679 | 7.6754e-06 | 1.16e-06 | 6.6167 | 1 | 310 | Customer | 31317 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.004261 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9923 | 829923 | 2020-02-12 22:37 | 2020-02-13 01:28 | 170.93 | 105 | 104 | 16835 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | 808 WHISPERING OAKS RD | CMI_NORMAL | NO | NO | NO | 862063 | 128989 | 116198 | 9242 | 872 | 0.019529 | 0.0001218 | 160.3333 | 1 | 310 | Mainline | 19753 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-12 | 2020 |  | #N/A
J2002.004263 |  | SOUTHERN | PAULS VALLEY | 5608:SHELL ELMORE C | SHELL ELMORE 21 | 560821 | 2020-02-12 22:43 | 2020-02-13 00:49 | 126.3 | 71 | 25 | 8533.0167 | 3 | DAMAGED BY PUBLIC | 12 | POLE | PAULS VALLEY | 1W HWY77 ON SH29 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 77712 | 6227 | 114 | 114 | 0.0098984 | 8.2361e-05 | 120.1833 | 1 | 310 | Mainline | 111 | Switch | SwitchOH | Ties | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-12 | 2020 |  | #N/A
J2002.004282 | PD-02132020-00008 | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9862 | 839862 | 2020-02-13 02:11 | 2020-02-13 04:23 | 132.47 | 1 | 1 | 132.4667 | 22 | WIND | 23 | FUSE - PRIMARY | OKLAHOMA CITY | .5 miles west of intersection | CMI_NORMAL | NO | NO | NO | 862063 | 168360 | 148518 | 10668 | 2316 | 0.00015366 | 1.16e-06 | 132.4667 | 1 | 310 | Load | 362401 | Load | 0 | DARREN L STOCKTON | 918-777-1697 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004285 |  | METRO EAST | SEMINOLE | 7208:CYPRESS | CYPRESS_822 | 720822 | 2020-02-13 03:08 | 2020-02-13 03:40 | 31.72 | 1 | 1 | 16.489 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | HOLDENVILLE | 521 E POPLAR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862063 | 114515 | 13626 | 2522 | 1432 | 1.9127e-05 | 1.16e-06 | 16.489 | 1 | 310 | Customer | 1382 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | OK - 2020
J2002.004288 | PD-02132020-00009 | NORTHEAST | SAPULPA | 7608:TIGER CREEK | TIGER_CREEK_821 | 760821 | 2020-02-13 03:39 | 2020-02-13 06:47 | 187.77 | 39 | 13 | 4314.1167 | 22 | WIND | 16 | LINE RECLOSER | DRUMRIGHT | 1ME 3MS OF DRUMRIGHT | CMI_NORMAL | NO | NO | NO | 862050 | 74150 | 40827 | 776 | 345 | 0.0050045 | 4.5241e-05 | 110.6184 | 1 | 310 | Mainline | 3770 | Fuse | FuseOH | NICHOLAS MANION | 918-290-1327 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | #N/A
J2002.004290 | PD-02132020-00010 | METRO NORTH | NORTH | 8347:WILSHIRE | WILSHIRE_4722 | 834722 | 2020-02-13 03:39 | 2020-02-13 10:35 | 415.68 | 67 | 75 | 25291.35 | 4 | DETERIORATION | 27 | CUTOUT | OKLAHOMA CITY | CLERMONT PL + ES-MAY | CMI_NORMAL | NO | NO | NO | 862050 | 168360 | 148518 | 4624 | 1590 | 0.029339 | 7.7722e-05 | 377.4828 | 1 | 310 | Tap | 23463 | Fuse | FuseOH | DENNY J MORGAN | 405-501-1556 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | OK - 2021
J2002.004312 | PD-02132020-00022 | NORTHEAST | SAPULPA | 7608:TIGER CREEK | TIGER_CREEK_821 | 760821 | 2020-02-13 06:58 | 2020-02-13 10:37 | 219.28 | 1 | 1 | 176.05 | 22 | WIND | 17 | JUMPER | DRUMRIGHT | MS JOSEPHS, MS 3 BARN | CMI_NORMAL | NO | NO | NO | 862050 | 74150 | 40827 | 776 | 345 | 0.00020422 | 1.16e-06 | 176.05 | 1 | 315 | Customer | 218289 | Load | Tran1phOH | BRAD WRIGHT | 918-629-1747 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | #N/A
J2002.004314 | PD-02132020-00024 | NORTHEAST | SAPULPA | 7608:TIGER CREEK | TIGER_CREEK_821 | 760821 | 2020-02-13 07:11 | 2020-02-13 10:47 | 215.7 | 1 | 1 | 162.3667 | 12 | POOR CONNECTION | 17 | JUMPER | DRUMRIGHT | 2S HWY33&16 JCT, 3/4E | CMI_NORMAL | NO | NO | NO | 862050 | 74150 | 40827 | 776 | 345 | 0.00018835 | 1.16e-06 | 162.3667 | 1 | 315 | Customer | 191084 | Load | Tran1phOH | BRAD WRIGHT | 918-629-1747 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | #N/A
J2002.004319 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-13 07:38 | 2020-02-13 07:53 | 15.45 | 25 | 2 | 333.3333 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | POCOLA | 1702 N Hwy | CMI_PLANNED | YES | NO | NO | 862050 | 82345 | 61272 | 1458 | 1240 | 0.00038668 | 2.9001e-05 | 13.3333 | 1 | 310 | Mainline | 258332 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | Ark - Series 2
J2002.004331 | PD-02132020-00046 | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2161 | 892161 | 2020-02-13 08:08 | 2020-02-13 17:27 | 558.72 | 1 | 1 | 15.0064 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | 3500 N.CIMMARON RD | CMI_NORMAL | NO | NO | NO | 862050 | 128989 | 12791 | 3201 | 739 | 1.7408e-05 | 1.16e-06 | 15.0064 | 1 | 320 | Load | 65996 | Load | Tran3phPadWye | BAD ORDER PRIMARY RES COORD | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004346 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-13 08:50 | 2020-02-13 10:24 | 94.12 | 2 | 2 | 180.6833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | CHARLESTON | STONE HILL | CMI_PLANNED | YES | NO | NO | 862050 | 82345 | 61272 | 962 | 491 | 0.0002096 | 2.3201e-06 | 90.3417 | 1 | 308 | Load | 12388 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-13 | 2020 |  | Ark - Series 2
J2002.004351 |  | METRO WEST | WEST | 8158:SARA | SARA_5864 | 815864 | 2020-02-13 09:04 | 2020-02-13 14:04 | 300.6 | 4 | 2 | 1052.1 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | W FRISCO SS NW.23 | CMI_PLANNED | YES | NO | NO | 862050 | 128989 | 116198 | 18285 | 4819 | 0.0012205 | 4.6401e-06 | 263.025 | 1 | 308 | Mainline | 35862 | Switch | SwitchOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | OK - 2022
J2002.004352 |  | NORTHEAST | SAPULPA | 7608:TIGER CREEK | TIGER_CREEK_821 | 760821 | 2020-02-13 09:04 | 2020-02-13 10:49 | 105.63 | 1 | 1 | 105.6333 | 22 | WIND | 17 | JUMPER | DRUMRIGHT | THOMAS CAIN LEASE | CMI_NORMAL | NO | NO | NO | 862050 | 74150 | 40827 | 776 | 345 | 0.00012254 | 1.16e-06 | 105.6333 | 1 | 310 | Load | 91129 | Load | 0 | [7 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | #N/A
J2002.004355 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-13 09:09 | 2020-02-13 11:30 | 141.55 | 3 | 0 | 255.55 | 4 | DETERIORATION | 2 | TRANSFORMER OH | 0 | APPROX 1 M E. OF BLOOMER | CMI_PLANNED | YES | NO | NO | 862050 | 82345 | 61272 | 962 | 491 | 0.00029644 | 3.4801e-06 | 85.1833 | 1 | 0 | Load | 15967 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-13 | 2020 |  | Ark - Series 2
J2002.004356 |  | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1722 | 861722 | 2020-02-13 09:10 | 2020-02-13 09:15 | 5.12 | 1 | 1 | 5.1167 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 4208 SE.53 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 114515 | 71266 | 6955 | 1789 | 5.9355e-06 | 1.16e-06 | 5.1167 | 1 | 310 | Customer | 48126 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | #N/A
J2002.004422 | PD-02132020-00123 | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-02-13 09:14 | 2020-02-13 11:47 | 153.32 | 195 | 95 | 29599.8167 | 5 | ELECTRICAL TRACKING | 23 | FUSE - PRIMARY | BIXBY | .5E. MINGO ON HWY 64 | CMI_NORMAL | NO | NO | NO | 862050 | 74150 | 40827 | 2756 | 1443 | 0.034337 | 0.0002262 | 151.7939 | 1 | 310 | Mainline | 63046 | Recloser | Rec3phHydralic | JOSHUA N MCKINNEY | 918-863-6313 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | OK - 2021
J2002.004362 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-13 09:18 | 2020-02-13 09:25 | 7.12 | 1 | 0 | 7.1269 | 1 | CANCELLED | 57 | CANCELLED | POCOLA | 207 W STANDFIELD AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 82345 | 61272 | 1458 | 1240 | 8.2673e-06 | 1.16e-06 | 7.1269 | 1 | 0 | Load | 7821 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | Ark - Series 2
J2002.004371 | PD-02132020-00099 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3631 | 833631 | 2020-02-13 09:21 | 2020-02-13 10:16 | 54.88 | 1 | 1 | 54.8833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3008 ROSEWOOD LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 168360 | 148518 | 8790 | 1336 | 6.3666e-05 | 1.16e-06 | 54.8833 | 1 | 310 | Customer | 21913 | Load | Tran1phPad | STEPHEN R MEADOWS | 405-641-5657 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | OK - 2021
J2002.004372 | PD-02132020-00095 | METRO EAST | EAST | 8542:RENO | RENO_4231 | 854231 | 2020-02-13 09:21 | 2020-02-13 10:30 | 68.8 | 1 | 1 | 61.474 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DEL CITY | 3109 DEL-RANCHO RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 114515 | 71266 | 5218 | 960 | 7.1311e-05 | 1.16e-06 | 61.474 | 1 | 320 | Customer | 20876 | Load | Tran1phOH | STEVEN CASKEY | 405-777-8855 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | OK - 2021
J2002.004370 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-02-13 09:22 | 2020-02-13 10:14 | 52.73 | 1 | 1 | 49.3833 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | LAVACA | LAVACA-RIVER ROAD | CMI_PLANNED | YES | NO | NO | 862050 | 82345 | 61272 | 2741 | 2129 | 5.7286e-05 | 1.16e-06 | 49.3833 | 1 | 308 | Load | 17930 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | Ark - Series 2
J2002.004376 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7029 | 817029 | 2020-02-13 09:27 | 2020-02-13 10:30 | 62.97 | 2 | 1 | 118.8 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 9600 S.SHIELDS | CMI_PLANNED | YES | NO | NO | 862050 | 159281 | 102246 | 9937 | 1756 | 0.00013781 | 2.3201e-06 | 59.4 | 1 | 308 | Load | 20437 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | OK - 2022
J2002.004385 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7024 | 817024 | 2020-02-13 09:33 | 2020-02-13 10:17 | 43.23 | 9 | 7 | 324.3 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 6401 S.BYERS | CMI_PLANNED | YES | NO | NO | 862050 | 159281 | 102246 | 9937 | 1751 | 0.0003762 | 1.044e-05 | 36.0333 | 1 | 310 | Load | 20404 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004386 |  | NORTHWEST | ENID | 4210:MEDFORD | MEDFORD 22 | 421022 | 2020-02-13 09:36 | 2020-02-13 10:03 | 26.97 | 1 | 1 | 26.9667 | 1 | CANCELLED | 57 | CANCELLED | LEONARD | 1N MEDFORD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 53603 | 37639 | 744 | 681 | 3.1282e-05 | 1.16e-06 | 26.9667 | 1 | 310 | Customer | 351819 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | #N/A
J2002.004387 | PD-02132020-00142 | NORTHEAST | SAPULPA | 7632:OAK GROVE | OAK_GROVE_3221 | 763221 | 2020-02-13 09:37 | 2020-02-13 12:24 | 166.87 | 1 | 1 | 166.8667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DRUMRIGHT | 101 E.5TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 74150 | 40827 | 1021 | 1021 | 0.00019357 | 1.16e-06 | 166.8667 | 1 | 310 | Customer | 41901 | Load | Tran1phOH | NICHOLAS MANION | 918-290-1327 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | OK - 2021
J2002.004388 |  | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1724 | 911724 | 2020-02-13 09:40 | 2020-02-13 15:33 | 352.87 | 9 | 5 | 2793 | 4 | DETERIORATION | 12 | POLE | BARLING | 1003 A ST | CMI_PLANNED | YES | NO | NO | 862050 | 82345 | 61272 | 4247 | 611 | 0.00324 | 1.044e-05 | 310.3333 | 1 | 308 | Load | 12556 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-13 | 2020 |  | #N/A
J2002.004394 | PD-02132020-00130 | METRO SOUTH | SOUTH | 5607:ROSEDALE TAP | ROSEDALE_TAP_722 | 560722 | 2020-02-13 09:50 | 2020-02-13 11:18 | 88.13 | 1 | 1 | 88.1333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | WAYNE | 2MN-WAYNE ON HWY 77,3 1/2ME | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 159281 | 57035 | 992 | 652 | 0.00010224 | 1.16e-06 | 88.1333 | 1 | 310 | Customer | 25863 | Load | TranOpenDelta | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | #N/A
J2002.004396 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6329 | 816329 | 2020-02-13 09:52 | 2020-02-13 10:01 | 8.45 | 1 | 1 | 8.45 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 604 CEDAR RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 159281 | 102246 | 11849 | 1712 | 9.8022e-06 | 1.16e-06 | 8.45 | 1 | 310 | Customer | 25902 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004403 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7023 | 817023 | 2020-02-13 10:14 | 2020-02-13 10:46 | 31.43 | 1 | 1 | 17.8 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 8041 S.LINDA LN | CMI_PLANNED | YES | NO | NO | 862050 | 159281 | 102246 | 9937 | 646 | 2.0648e-05 | 1.16e-06 | 17.8 | 1 | 308 | Load | 48096 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004426 | PD-02132020-00155 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3635 | 833635 | 2020-02-13 10:20 | 2020-02-13 12:08 | 107.55 | 1 | 1 | 107.55 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1301 W.HEFNER RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 168360 | 148518 | 8790 | 1953 | 0.00012476 | 1.16e-06 | 107.55 | 1 | 310 | Customer | 75516 | Load | Tran1phPad | STEPHEN R MEADOWS | 405-641-5657 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | OK - 2021
J2002.004442 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7024 | 817024 | 2020-02-13 10:28 | 2020-02-13 12:15 | 106.25 | 1 | 1 | 32.65 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 337 SE.62 | CMI_PLANNED | YES | NO | NO | 862050 | 159281 | 102246 | 9937 | 1751 | 3.7875e-05 | 1.16e-06 | 32.65 | 1 | 308 | Load | 67459 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004445 | PD-02132020-00213 | NORTHEAST | SAPULPA | 3208:TIBBENS ROAD | TIBBENS_RD_822 | 320822 | 2020-02-13 10:34 | 2020-02-13 14:46 | 251.8 | 1 | 1 | 251.8 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | SAPULPA | lot 7 east of laney rd | CMI_NORMAL | NO | NO | NO | 862050 | 74150 | 40827 | 3146 | 524 | 0.00029209 | 1.16e-06 | 251.8 | 1 | 310 | Customer | 365346 | Load | Tran1phPad | CONTRACTOR 5 DAVID ELLIOT INC | 918-639-5055 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004447 |  | METRO NORTH | NORTH | 8347:WILSHIRE | WILSHIRE_4722 | 834722 | 2020-02-13 10:41 | 2020-02-13 10:45 | 4.63 | 1 | 1 | 4.6333 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 2748 CLERMONT PL | CMI_MOMENTARY | YES | NO | NO | 862050 | 168360 | 148518 | 4624 | 1590 | 5.3748e-06 | 1.16e-06 | 4.6333 | 1 | 310 | Customer | 28373 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | OK - 2021
J2002.004451 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-13 10:56 | 2020-02-13 13:09 | 132.6 | 3 | 1 | 393.2 | 4 | DETERIORATION | 28 | CROSSARM | STONE HILL | STONE HILL | CMI_PLANNED | YES | NO | NO | 862050 | 82345 | 61272 | 962 | 491 | 0.00045612 | 3.4801e-06 | 131.0667 | 1 | 308 | Load | 7269 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-13 | 2020 |  | Ark - Series 2
J2002.004452 | PD-02132020-00183 | METRO EAST | SEMINOLE | 7312:JUMPER CREEK | JUMPER_CREEK_1227 | 731227 | 2020-02-13 10:58 | 2020-02-13 12:02 | 64.18 | 1 | 1 | 64.1833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SEMINOLE | ,5 MS OF EW 144 ON NS 350 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 114515 | 13626 | 1217 | 885 | 7.4454e-05 | 1.16e-06 | 64.1833 | 1 | 320 | Load | 335268 | Load | Tran1phOH | BRADY A HUFF | 405-519-0701 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | OK - 2021
J2002.004455 |  | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3922 | 833922 | 2020-02-13 11:07 | 2020-02-13 11:07 | 0 | 1636 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 4107 NW 55TH ST | CMI_MOMENTARY | YES | NO | NO | 862050 | 168360 | 148518 | 7853 | 1637 | 0 | 0.0018978 | 0 | 1 | 0 | Feeder | TULSA_3922 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-13 | 2020 |  | OK - 2022
J2002.004460 | PD-02132020-00220 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2129 | 822129 | 2020-02-13 11:07 | 2020-02-13 12:31 | 83.73 | 1 | 1 | 68.8833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4144 NW.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 168360 | 148518 | 9253 | 1559 | 7.9906e-05 | 1.16e-06 | 68.8833 | 1 | 310 | Customer | 111 | Load | Tran1phOH | ADAM CLARK | 580-310-8924 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | OK - 2020
J2002.004462 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-13 11:17 | 2020-02-13 13:09 | 112.6 | 1 | 0 | 110.8667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | 0 | 32611 HWY 22, R-CHASTN | CMI_PLANNED | YES | NO | NO | 862050 | 82345 | 61272 | 962 | 491 | 0.00012861 | 1.16e-06 | 110.8667 | 1 | 0 | Load | 11885 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-13 | 2020 |  | Ark - Series 2
J2002.004471 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_622 | 460622 | 2020-02-13 11:37 | 2020-02-13 12:13 | 35.23 | 1 | 1 | 35.2333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | WOODWARD | 703 6TH-WOODWARD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 53603 | 10441 | 5690 | 765 | 4.0872e-05 | 1.16e-06 | 35.2333 | 1 | 310 | Customer | 10434 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | #N/A
J2002.004474 | PD-02132020-00260 | SOUTHERN | HEALDTON | 5321:WILDHORSE | WILDHORSE_2121 | 532121 | 2020-02-13 11:46 | 2020-02-13 12:56 | 70.22 | 1 | 1 | 68.3667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | RATLIFF CITY | SE SW SW SEC16 T1S R3W | CMI_NORMAL | NO | NO | NO | 862050 | 77712 | 6810 | 155 | 119 | 7.9307e-05 | 1.16e-06 | 68.3667 | 1 | 310 | Load | 25648 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | #N/A
J2002.004485 | PD-02132020-00273 | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_622 | 880622 | 2020-02-13 12:03 | 2020-02-13 13:14 | 71.08 | 1 | 1 | 71.0833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | GUTHRIE | L14 B3 FOUR CREEKS EST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 168360 | 19842 | 5175 | 1167 | 8.2458e-05 | 1.16e-06 | 71.0833 | 1 | 310 | Customer | 72091 | Load | Tran1phOH | JOSEPH WAYNE POOL | 405-919-2253 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004486 | PD-02132020-00280 | NORTHEAST | MUSKOGEE | 3117:THREE RIVERS | THREE_RIVERS_1721 | 311721 | 2020-02-13 12:05 | 2020-02-13 13:25 | 79.77 | 1 | 1 | 64.3167 | 12 | POOR CONNECTION | 50 | CONNECTOR | MUSKOGEE | 2321 MANILA | CMI_NORMAL | NO | NO | NO | 862050 | 74150 | 33323 | 2835 | 1048 | 7.4609e-05 | 1.16e-06 | 64.3167 | 1 | 320 | Customer | 5448 | Load | Tran1phOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-13 | 2020 |  | #N/A
J2002.004488 | PD-02132020-00281 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_722 | 870722 | 2020-02-13 12:11 | 2020-02-13 16:48 | 277.2 | 1 | 2 | 269.35 | 3 | DAMAGED BY PUBLIC | 32 | CONDUCTOR SECONDARY - UG | NORMAN | SS HWY9 1/2M E.72 SE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 159281 | 57035 | 11836 | 1582 | 0.00031245 | 1.16e-06 | 269.35 | 1 | 310 | Load | 179463 | Load | Tran1phOH | CARL BILYEU | 405-820-9246 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004487 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7023 | 817023 | 2020-02-13 12:16 | 2020-02-13 13:26 | 69.92 | 1 | 1 | 39.4167 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 709 SE.79 | CMI_PLANNED | YES | NO | NO | 862050 | 159281 | 102246 | 9937 | 646 | 4.5724e-05 | 1.16e-06 | 39.4167 | 1 | 308 | Load | 21973 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004490 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-02-13 12:25 | 2020-02-13 12:47 | 22.27 | 1 | 1 | 22.2667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | LEONARD | 17645 S.161 E. AVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 74150 | 40827 | 2756 | 1443 | 2.583e-05 | 1.16e-06 | 22.2667 | 1 | 310 | Load | 400469 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | OK - 2021
J2002.004491 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-13 12:27 | 2020-02-13 15:08 | 161.12 | 1 | 1 | 150.7667 | 4 | DETERIORATION | 12 | POLE | BRANCH | 1125 1/2 SO. HOPPINS | CMI_PLANNED | YES | NO | NO | 862050 | 82345 | 61272 | 962 | 491 | 0.00017489 | 1.16e-06 | 150.7667 | 1 | 308 | Load | 203134 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-13 | 2020 |  | Ark - Series 2
J2002.004499 | PD-02132020-00299 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5123 | 815123 | 2020-02-13 12:44 | 2020-02-13 14:35 | 110.73 | 1 | 1 | 88.8667 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 7109 S.DOUGLAS PL | CMI_NORMAL | NO | NO | NO | 862050 | 159281 | 102246 | 13943 | 1328 | 0.00010309 | 1.16e-06 | 88.8667 | 1 | 310 | Customer | 25529 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004502 | PD-02132020-00302 | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-02-13 12:50 | 2020-02-13 13:00 | 9.77 | 1 | 1 | 9.7667 | 1 | CANCELLED | 57 | CANCELLED | BIXBY | 1/4E OF LEONARD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 74150 | 40827 | 2756 | 1443 | 1.133e-05 | 1.16e-06 | 9.7667 | 1 | 310 | Customer | 40715 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | OK - 2021
J2002.004501 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-13 12:52 | 2020-02-13 14:19 | 87.28 | 1 | 1 | 83.05 | 4 | DETERIORATION | 12 | POLE | POCOLA | 207 W STANDFIELD AV | CMI_PLANNED | YES | NO | NO | 862050 | 82345 | 61272 | 1458 | 1240 | 9.634e-05 | 1.16e-06 | 83.05 | 1 | 308 | Load | 7821 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | Ark - Series 2
J2002.004505 | PD-02132020-00301 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6922 | 846922 | 2020-02-13 12:53 | 2020-02-13 13:26 | 33.25 | 1 | 2 | 33.25 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 1024 NW.105 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 168360 | 148518 | 7732 | 1490 | 3.8571e-05 | 1.16e-06 | 33.25 | 1 | 310 | Customer | 49079 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004506 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7029 | 817029 | 2020-02-13 12:56 | 2020-02-13 13:33 | 37.13 | 3 | 2 | 95.3 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 9600 S.EASTERN | CMI_PLANNED | YES | NO | NO | 862050 | 159281 | 102246 | 9937 | 1756 | 0.00011055 | 3.4801e-06 | 31.7667 | 1 | 308 | Load | 48219 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | OK - 2022
J2002.004508 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-02-13 13:05 | 2020-02-13 13:25 | 20.27 | 1 | 1 | 20.2667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BIXBY | 12931 E.182ND | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 74150 | 40827 | 2756 | 1443 | 2.351e-05 | 1.16e-06 | 20.2667 | 1 | 310 | Customer | 43362 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | OK - 2021
J2002.004511 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-13 13:12 | 2020-02-13 16:21 | 189.12 | 5 | 4 | 868.25 | 4 | DETERIORATION | 12 | POLE | POCOLA | 0 | CMI_PLANNED | YES | NO | NO | 862050 | 82345 | 61272 | 1458 | 1240 | 0.0010072 | 5.8001e-06 | 173.65 | 1 | 308 | Mainline |  | 0 | 0 | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | Ark - Series 2
J2002.004515 |  | SOUTHERN | ARDMORE | 5106:HARRIS ST | HARRIS_ST_623 | 510623 | 2020-02-13 13:19 | 2020-02-13 17:44 | 265.85 | 6 | 6 | 1546.4 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | ARDMORE | 828 LOCUST | CMI_PLANNED | YES | NO | NO | 862050 | 77712 | 23608 | 2069 | 900 | 0.0017939 | 6.9602e-06 | 257.7333 | 1 | 310 | Load | 13551 | Load | TranOH3phDelta | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | #N/A
J2002.004517 | PD-02132020-00328 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7431 | 847431 | 2020-02-13 13:25 | 2020-02-13 13:47 | 22.4 | 1 | 1 | 22.4 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 138 NE.38 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 168360 | 148518 | 6172 | 374 | 2.5985e-05 | 1.16e-06 | 22.4 | 1 | 320 | Customer | 3706 | Load | TranOpenDelta | ADAM COX | 405-328-8938 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | OK - 2022
J2002.004519 |  | SOUTHERN | DURANT | 5512:COLBERT | COLBERT_1222 | 551222 | 2020-02-13 13:28 | 2020-02-13 16:36 | 188.1 | 2 | 1 | 217.7 | 4 | DETERIORATION | 12 | POLE | COLBERT | WS 69/75 AT KOA CAMP | CMI_PLANNED | YES | NO | NO | 862050 | 77712 | 15520 | 2174 | 1276 | 0.00025254 | 2.3201e-06 | 108.85 | 1 | 308 | Load | 29257 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004524 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-13 13:40 | 2020-02-13 14:55 | 75.47 | 2 | 0 | 150.9569 | 25 | LIGHTNING | 47 | ARRESTOR OH | LAMAR | LAMAR AR | CMI_PLANNED | YES | NO | NO | 862050 | 82345 | 7553 | 730 | 0 | 0.00017511 | 2.3201e-06 | 75.4784 | 1 | 0 | Load | 11951 | Load | Tran1phOH | [7 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | #N/A
J2002.004537 | PD-02132020-00366 | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1722 | 861722 | 2020-02-13 14:05 | 2020-02-13 15:48 | 103.18 | 1 | 1 | 103.1833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4208 SE.53 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 114515 | 71266 | 6955 | 1789 | 0.0001197 | 1.16e-06 | 103.1833 | 1 | 310 | Customer | 48126 | Load | Tran1phPad | THOMAS E COLE | 405-623-9338 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | #N/A
J2002.004542 |  | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1724 | 911724 | 2020-02-13 14:15 | 2020-02-13 15:35 | 79.28 | 5 | 1 | 275.0833 | 4 | DETERIORATION | 12 | POLE | BARLING | 150 S-S.A,100 W-S.11, BARLING | CMI_PLANNED | YES | NO | NO | 862050 | 82345 | 61272 | 4247 | 611 | 0.0003191 | 5.8001e-06 | 55.0167 | 1 | 308 | Load | 3429 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-13 | 2020 |  | #N/A
J2002.004548 | PD-02132020-00380 | METRO EAST | SHAWNEE | 7407:REMINGTON | REMINGTON 22 | 740722 | 2020-02-13 14:31 | 2020-02-13 16:03 | 91.9 | 1 | 2 | 85.4167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SHAWNEE | 926 E.INDEPENDENCE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 114515 | 22142 | 3669 | 1645 | 9.9086e-05 | 1.16e-06 | 85.4167 | 1 | 320 | Customer | 10811 | Load | Tran1phOH | BRYAN K TATUM | 405-659-0746 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | #N/A
J2002.004550 |  | NORTHWEST | ENID | 4153:IMO | IMO_5322 | 415322 | 2020-02-13 14:38 | 2020-02-13 15:59 | 81.52 | 1 | 0 | 81.5196 | 4 | DETERIORATION | 2 | TRANSFORMER OH | 0 | WHEAT + FOX-1/4N,SS | CMI_PLANNED | YES | NO | NO | 862050 | 53603 | 37639 | 1177 | 506 | 9.4565e-05 | 1.16e-06 | 81.5196 | 1 | 0 | Load | 9945 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004551 |  | METRO NORTH | NORTH | 8347:WILSHIRE | WILSHIRE_4722 | 834722 | 2020-02-13 14:38 | 2020-02-13 14:56 | 18.53 | 1 | 1 | 18.5333 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 2748 CLERMONT PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 168360 | 148518 | 4624 | 1590 | 2.1499e-05 | 1.16e-06 | 18.5333 | 1 | 310 | Customer | 28373 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | OK - 2021
J2002.004553 |  | ARKANSAS | POTEAU | 3505:POTEAU | POTEAU_524 | 350524 | 2020-02-13 14:48 | 2020-02-13 14:58 | 10.42 | 1 | 1 | 10.4167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | POTEAU | HWY 59 + RIDGE RD. R. POTEAU | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 82345 | 13520 | 2306 | 725 | 1.2084e-05 | 1.16e-06 | 10.4167 | 1 | 310 | Customer | 16952 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | #N/A
J2002.004563 |  | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3722 | 913722 | 2020-02-13 15:21 | 2020-02-13 15:44 | 22.68 | 1 | 1 | 22.6833 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 5801 KINKEAD AV B10L | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 82345 | 61272 | 4575 | 1441 | 2.6313e-05 | 1.16e-06 | 22.6833 | 1 | 310 | Customer | 27 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | Ark - Series 3
J2002.004565 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3829 | 913829 | 2020-02-13 15:25 | 2020-02-13 16:01 | 36.07 | 1 | 1 | 36.0667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 1722.5 S.T | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 82345 | 61272 | 2944 | 1190 | 4.1838e-05 | 1.16e-06 | 36.0667 | 1 | 310 | Customer | 5559 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-13 | 2020 |  | Ark - Series 2
J2002.004566 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3829 | 913829 | 2020-02-13 15:25 | 2020-02-13 16:01 | 35.9 | 1 | 1 | 35.9 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 1704 S.P | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 82345 | 61272 | 2944 | 1190 | 4.1645e-05 | 1.16e-06 | 35.9 | 1 | 310 | Customer | 1085 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-13 | 2020 |  | Ark - Series 2
J2002.004568 | PD-02132020-00425 | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_624 | 880624 | 2020-02-13 15:31 | 2020-02-13 17:01 | 89.55 | 1 | 1 | 63.15 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | GUTHRIE | montigo fields north | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862050 | 168360 | 19842 | 5175 | 709 | 7.3256e-05 | 1.16e-06 | 63.15 | 1 | 320 | Customer | 227555 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004569 |  | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4029 | 914029 | 2020-02-13 15:33 | 2020-02-13 15:33 | 0 | 260 | 0 | 0 | 16 | SUBSTATION OPERATION | 16 | LINE RECLOSER | FORT SMITH | CAVANAUGH RD + HWY 271 | CMI_MOMENTARY | YES | NO | NO | 862050 | 82345 | 61272 | 4765 | 1103 | 0 | 0.00030161 | 0 | 1 | 0 | Mainline | 352920 | Recloser | Rec3phElectronic | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-02-13 | 2020 |  | Ark - Series 2
J2002.004570 |  | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4029 | 914029 | 2020-02-13 15:33 | 2020-02-13 15:33 | 0 | 225 | 0 | 0 | 16 | SUBSTATION OPERATION | 16 | LINE RECLOSER | FORT SMITH | CAVANAUGH RD + HWY 271 | CMI_MOMENTARY | YES | NO | NO | 862050 | 82345 | 61272 | 4765 | 1103 | 0 | 0.00026101 | 0 | 1 | 0 | Mainline | 352920 | Recloser | Rec3phElectronic | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-02-13 | 2020 |  | Ark - Series 2
J2002.004571 |  | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4029 | 914029 | 2020-02-13 15:33 | 2020-02-13 15:33 | 0 | 288 | 0 | 0 | 5 | ELECTRICAL TRACKING | 16 | LINE RECLOSER | FORT SMITH | CAVANAUGH RD + HWY 271 | CMI_MOMENTARY | YES | NO | NO | 862050 | 82345 | 61272 | 4765 | 1103 | 0 | 0.00033409 | 0 | 1 | 0 | Mainline | 352920 | Recloser | Rec3phElectronic | Circuit Operation | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-13 | 2020 |  | Ark - Series 2
J2002.004579 | PD-02132020-00464 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_722 | 870722 | 2020-02-13 16:13 | 2020-02-13 18:55 | 161.55 | 1 | 2 | 136.2667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | NORMAN | 1660 SE 24TH AVE IN VACANT LOT | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862050 | 159281 | 57035 | 11836 | 1582 | 0.00015807 | 1.16e-06 | 136.2667 | 1 | 310 | Customer | 64454 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004580 | PD-02132020-00459 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_864 | 830864 | 2020-02-13 16:16 | 2020-02-13 17:02 | 46.02 | 1 | 1 | 43.1833 | 13 | PREMATURE FAILURE | 44 | METER - PRIMARY | EDMOND | 237TH AND N MACARTHUR | CMI_NORMAL | NO | NO | NO | 862050 | 168360 | 148518 | 19423 | 2766 | 5.0094e-05 | 1.16e-06 | 43.1833 | 1 | 310 | Load | 341845 | Load | 0 | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | OK - 2021
J2002.004581 | PD-02132020-00461 | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1621 | 581621 | 2020-02-13 16:19 | 2020-02-13 17:26 | 67.37 | 1 | 1 | 67.3667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ADA | 320 E.13 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 77712 | 11525 | 3466 | 1812 | 7.8147e-05 | 1.16e-06 | 67.3667 | 1 | 310 | Customer | 4259 | Load | TranOpenDelta | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004585 | PD-02132020-00472 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2024 | 862024 | 2020-02-13 16:37 | 2020-02-13 18:41 | 123.7 | 1 | 1 | 123.7 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 318 SE 28TH ST | CMI_NORMAL | NO | NO | NO | 862050 | 159281 | 102246 | 4759 | 772 | 0.0001435 | 1.16e-06 | 123.7 | 1 | 310 | Customer | 78202 | Load | Tran1phOH | THOMAS E COLE | 405-623-9338 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004593 | PD-02132020-00477 | SOUTHERN | ARDMORE | 5117:MARIETTA | MARIETTA_1721 | 511721 | 2020-02-13 17:05 | 2020-02-13 17:30 | 24.8 | 1 | 1 | 24.8 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MARIETTA | 305 N W 4TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 77712 | 23608 | 1595 | 638 | 2.8769e-05 | 1.16e-06 | 24.8 | 1 | 310 | Customer | 7039 | Load | TranOpenDelta | GARRETT YOUNG | 580-276-6194 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | #N/A
J2002.004599 | PD-02132020-00479 | NORTHEAST | MUSKOGEE | 3117:THREE RIVERS | THREE_RIVERS_1721 | 311721 | 2020-02-13 17:18 | 2020-02-13 20:47 | 209.38 | 26 | 30 | 5399.3333 | 5 | ELECTRICAL TRACKING | 18 | INSULATOR | MUSKOGEE | RISSER + HAYES | CMI_NORMAL | NO | NO | NO | 862050 | 74150 | 33323 | 2835 | 1048 | 0.0062634 | 3.0161e-05 | 207.6667 | 1 | 310 | Tap | 23767 | Fuse | FuseOH | STEVE K HIGHFILL | 918-869-2785 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-13 | 2020 |  | #N/A
J2002.004605 | PD-02132020-00480 | NORTHEAST | MUSKOGEE | 3117:THREE RIVERS | THREE_RIVERS_1721 | 311721 | 2020-02-13 17:18 | 2020-02-13 19:15 | 117.37 | 1 | 2 | 117.3667 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | MUSKOGEE | 2500 HASKELL BLVD. | CMI_NORMAL | NO | NO | NO | 862050 | 74150 | 33323 | 2835 | 1048 | 0.00013615 | 1.16e-06 | 117.3667 | 1 | 310 | Customer | 5932 | Load | Tran1phOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-02-13 | 2020 |  | #N/A
J2002.004608 | PD-02132020-00482 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_869 | 830869 | 2020-02-13 17:45 | 2020-02-13 19:18 | 93.15 | 1 | 1 | 89.2333 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | Iron Ridge Rd Lot 18 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862050 | 168360 | 148518 | 19423 | 2471 | 0.00010351 | 1.16e-06 | 89.2333 | 1 | 310 | Customer | 406760 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004611 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7021 | 817021 | 2020-02-13 17:47 | 2020-02-13 18:39 | 51.43 | 1 | 1 | 51.4333 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 131A SW.74 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 159281 | 102246 | 9937 | 1789 | 5.9664e-05 | 1.16e-06 | 51.4333 | 1 | 310 | Customer | 36313 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004617 | PD-02132020-00485 | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1723 | 861723 | 2020-02-13 18:03 | 2020-02-13 21:20 | 196.88 | 28 | 26 | 4301.3282 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | 0 | CMI_NORMAL | NO | NO | NO | 862050 | 114515 | 71267 | 6954 | 1599 | 0.0049897 | 3.2481e-05 | 153.6189 | 1 | 310 | Mainline | 103638-2 | Switch | SwitchDefault | CARL F KEMP | 405-618-8371 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | #N/A
J2002.004615 |  | NORTHEAST | SAPULPA | 3216:BEELINE | BEELINE_1633 | 321633 | 2020-02-13 18:05 | 2020-02-13 18:16 | 10.6 | 1 | 1 | 10.6 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | GLENPOOL | 11 N.COLLEGE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 74141 | 40822 | 5564 | 1948 | 1.2296e-05 | 1.16e-06 | 10.6 | 1 | 310 | Customer | 47921 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004616 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-02-13 18:10 | 2020-02-13 21:37 | 206.55 | 1 | 1 | 137.7667 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | OKLAHOMA CITY | 7401 RIDGE MANNER LN | CMI_NORMAL | NO | NO | NO | 862050 | 159282 | 57037 | 4238 | 1005 | 0.00015981 | 1.16e-06 | 137.7667 | 1 | 310 | Customer | 260995 | Load | Tran1phPad | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004624 | PD-02132020-00490 | METRO WEST | EL RENO | 8906:SOUTHARD | SOUTHARD_647 | 890647 | 2020-02-13 18:21 | 2020-02-13 21:10 | 169.47 | 1 | 1 | 169.4667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | CANTON | 307 W MAIN ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 128984 | 12791 | 1365 | 1070 | 0.00019659 | 1.16e-06 | 169.4667 | 1 | 320 | Customer | 38993 | Load | Tran1phOH | MICHAEL T MAHEN | 405-210-6029 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004630 |  | METRO SOUTH | SOUTH CENTRAL | 8194:WESTMOORE | WESTMOORE_9423 | 819423 | 2020-02-13 18:33 | 2020-02-13 18:47 | 14.45 | 1 | 1 | 14.45 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | THE VILLAGE ON SW 104 & PENN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 159282 | 102245 | 8105 | 1347 | 1.6762e-05 | 1.16e-06 | 14.45 | 1 | 310 | Customer | 103136 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004638 | PD-02132020-00492 | SOUTHERN | PAULS VALLEY | 5605:PAULS VALLEY | PAULS_VALLEY_521 | 560521 | 2020-02-13 18:53 | 2020-02-13 20:36 | 103.4 | 1 | 2 | 94.9 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | PAULS VALLEY | 1O1 CHESTNUT | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862050 | 77710 | 6228 | 2467 | 468 | 0.00011009 | 1.16e-06 | 94.9 | 1 | 320 | Customer | 387 | Load | Tran1phOH | GARRID H BROWN | 405-207-3948 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | OK - 2022
J2002.004645 | PD-02132020-00495 | NORTHEAST | SAPULPA | 7604:PAYNE | PAYNE 51 | 760451 | 2020-02-13 19:31 | 2020-02-13 20:33 | 61.53 | 1 | 1 | 61.5333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | RIPLEY | MORTON + KNIPE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 74141 | 40822 | 365 | 365 | 7.138e-05 | 1.16e-06 | 61.5333 | 1 | 310 | Customer | 44309 | Load | TranOpenDelta | BRAD WRIGHT | 918-629-1747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004646 | PD-02132020-00519 | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_621 | 770621 | 2020-02-13 19:34 | 2020-02-14 01:25 | 350.7 | 1 | 2 | 351.8667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | BRISTOW | 2 S ON 48 ON W | CMI_NORMAL | NO | NO | NO | 862050 | 74141 | 40822 | 3783 | 1575 | 0.00040817 | 1.16e-06 | 351.8667 | 1 | 310 | Customer | 15061 | Load | Tran1phOH | DWAYNE FOX | 405-695-8501 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | OK - 2021
J2002.004647 | PD-02132020-00498 | METRO SOUTH | SOUTH | 8726:NOBLE | NOBLE_2621 | 872621 | 2020-02-13 19:58 | 2020-02-13 22:11 | 133.22 | 2 | 2 | 230.1333 | 12 | POOR CONNECTION | 50 | CONNECTOR | NOBLE | 708 JACQUELYN | CMI_NORMAL | NO | NO | NO | 862050 | 159282 | 57037 | 2968 | 1447 | 0.00026696 | 2.3201e-06 | 115.0667 | 1 | 310 | Secondary | 39931 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004651 |  | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6022 | 836022 | 2020-02-13 20:05 | 2020-02-13 20:11 | 6.02 | 1 | 1 | 6.0167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BETHANY | 6802 NW.36 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 128984 | 116193 | 5509 | 1234 | 6.9795e-06 | 1.16e-06 | 6.0167 | 1 | 310 | Customer | 7868 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | OK - 2022
J2002.004654 |  | METRO WEST | WEST | 8245:COUNCIL | COUNCIL_4533 | 824533 | 2020-02-13 20:11 | 2020-02-13 20:19 | 7.68 | 1 | 1 | 7.6833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 8300 NW 10TH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 128984 | 116193 | 3412 | 2042 | 8.9129e-06 | 1.16e-06 | 7.6833 | 1 | 310 | Customer | 70830 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | #N/A
J2002.004657 |  | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1723 | 861723 | 2020-02-13 20:19 | 2020-02-13 20:26 | 6.35 | 1 | 1 | 6.35 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | DEL CITY | 3515 DELTA PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 114515 | 71267 | 6954 | 1599 | 7.3662e-06 | 1.16e-06 | 6.35 | 1 | 310 | Customer | 52252 | Load | Tran1phOH | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-13 | 2020 |  | #N/A
J2002.004660 |  | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5821 | 845821 | 2020-02-13 20:27 | 2020-02-13 20:39 | 11.45 | 1 | 1 | 11.45 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1BW ANDERSS WILSHI | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862050 | 114515 | 71267 | 2987 | 1189 | 1.3282e-05 | 1.16e-06 | 11.45 | 1 | 310 | Load | 18637 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-13 | 2020 |  | OK - 2020
J2002.004666 | PD-02132020-00517 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-02-13 20:51 | 2020-02-13 22:14 | 82.67 | 5 | 5 | 367.9167 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | OKLAHOMA CITY | 1209 N.ANN-ARBOR | CMI_NORMAL | NO | NO | NO | 862050 | 168350 | 148508 | 9250 | 1940 | 0.00042679 | 5.8001e-06 | 73.5833 | 1 | 310 | Load | 13228 | Load | Tran1phOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-13 | 2020 |  | OK - 2021
J2002.004700 | PD-02142020-00013 | METRO WEST | WEST | 8359:YUKON | YUKON_5923 | 835923 | 2020-02-14 00:17 | 2020-02-14 02:00 | 102.6 | 28 | 10 | 2793.4667 | 13 | PREMATURE FAILURE | 23 | FUSE - PRIMARY | YUKON | 1105 First Place Blvd | CMI_NORMAL | NO | NO | NO | 862050 | 128984 | 116193 | 6438 | 1152 | 0.0032405 | 3.2481e-05 | 99.7667 | 1 | 310 | Mainline | 385948 | Fuse | FuseOH | DARREN L STOCKTON | 918-777-1697 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | #N/A
J2002.004704 | PD-02142020-00016 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7031 | 817031 | 2020-02-14 00:46 | 2020-02-14 06:31 | 345.22 | 19 | 18 | 6038.8333 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | 9004 S.SHARTEL | CMI_NORMAL | NO | NO | NO | 862050 | 159282 | 102245 | 9937 | 1892 | 0.0070052 | 2.204e-05 | 317.8333 | 1 | 310 | Load | 2515 | Load | Tran1phPad | DUSTY STEJSKAL | 405-249-3863 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004745 | PD-02142020-00054 | NORTHWEST | ENID | 4414:HENNESSEY | HENNESSEY_1422 | 441422 | 2020-02-14 07:43 | 2020-02-14 13:22 | 338.6 | 2 | 4 | 478.25 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | HENNESSEY | 3.5W HWY 51 250 WS | CMI_NORMAL | NO | NO | NO | 862173 | 53601 | 37638 | 1954 | 541 | 0.0005547 | 2.3197e-06 | 239.125 | 1 | 310 | Load | 3209 | Load | Tran1phOH | PATRICK R KIFER | 405-509-0114 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004742 | PD-02142020-00041 | NORTHEAST | MUSKOGEE | 3312:CHECOTAH | CHECOTAH 22 | 331222 | 2020-02-14 07:46 | 2020-02-14 11:20 | 213.6 | 4 | 5 | 800.8667 | 11 | OVERLOAD | 2 | TRANSFORMER OH | CHECOTAH | 517 N BDWY | CMI_NORMAL | NO | NO | NO | 862173 | 74141 | 33319 | 2891 | 1531 | 0.00092889 | 4.6394e-06 | 200.2167 | 1 | 310 | Secondary | 14270 | Load | Tran1phOH | STEVE K HIGHFILL | 918-869-2785 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | OK - 2020
J2002.004747 | PD-02142020-00046 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6021 | 836021 | 2020-02-14 08:00 | 2020-02-14 09:39 | 98.58 | 1 | 1 | 98.5833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | BETHANY | NW 30 + COUNCIL RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 128984 | 116193 | 5509 | 1452 | 0.00011434 | 1.1599e-06 | 98.5833 | 1 | 310 | Customer | 7138 | Load | TranOpenDelta | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | #N/A
J2002.004748 | PD-02142020-00066 | ARKANSAS | FORT SMITH | 9126:OAK PARK | OAK_PARK_2623 | 912623 | 2020-02-14 08:09 | 2020-02-14 10:38 | 149.13 | 1 | 1 | 100.5167 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | FORT SMITH | 2912 WALNUT | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862173 | 82344 | 61271 | 2286 | 1993 | 0.00011659 | 1.1599e-06 | 100.5167 | 1 | 320 | Customer | 12395 | Load | Tran1phOH | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-14 | 2020 |  | Ark - Series 1
J2002.004754 | PD-02142020-00064 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1522 | 811522 | 2020-02-14 08:13 | 2020-02-14 09:24 | 71.48 | 7 | 8 | 480.6083 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2530.5 SW.30 | CMI_NORMAL | NO | NO | NO | 862173 | 159282 | 102245 | 6069 | 1946 | 0.00055744 | 8.119e-06 | 68.6583 | 1 | 310 | Load | 13034 | Load | Tran1phOH | GARY A DUNCAN | 405-474-9336 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.004751 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7031 | 817031 | 2020-02-14 08:17 | 2020-02-14 08:26 | 9.25 | 3 | 3 | 27.75 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 9004 S.SHARTEL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 159282 | 102245 | 9937 | 1892 | 3.2186e-05 | 3.4796e-06 | 9.25 | 1 | 310 | Secondary | 2515 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004753 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-14 08:20 | 2020-02-14 14:04 | 344.9 | 2 | 1 | 411.85 | 4 | DETERIORATION | 12 | POLE | LAMAR | 150 S-HWY 64 ON E MAIN, LAMAR | CMI_PLANNED | YES | NO | NO | 862173 | 82344 | 7553 | 730 | 0 | 0.00047769 | 2.3197e-06 | 205.925 | 1 | 308 | Load | 4163 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | #N/A
J2002.004757 | PD-02142020-00073 | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3421 | 843421 | 2020-02-14 08:27 | 2020-02-14 11:42 | 194.93 | 7 | 6 | 1346.1 | 15 | SQUIRREL | 20 | FUSE BARREL | OKLAHOMA CITY | 1716 NE.51 | CMI_NORMAL | NO | NO | NO | 862173 | 168350 | 148508 | 1228 | 499 | 0.0015613 | 8.119e-06 | 192.3 | 1 | 310 | Load | 18518 | Load | Tran1phOH | CAMERON PITTS | 405-537-6633 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | #N/A
J2002.004761 | PD-02142020-00075 | ARKANSAS | FORT SMITH | 9126:OAK PARK | OAK_PARK_2623 | 912623 | 2020-02-14 08:33 | 2020-02-14 10:29 | 115.68 | 1 | 1 | 115.6833 | 12 | POOR CONNECTION | 50 | CONNECTOR | FORT SMITH | 2323 BIRNIE AV | CMI_NORMAL | NO | NO | NO | 862173 | 82344 | 61271 | 2286 | 1993 | 0.00013418 | 1.1599e-06 | 115.6833 | 1 | 320 | Customer | 8503 | Load | Tran1phOH | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-14 | 2020 |  | Ark - Series 1
J2002.004762 | PD-02142020-00074 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3621 | 853621 | 2020-02-14 08:35 | 2020-02-14 12:39 | 243.87 | 1 | 1 | 243.8667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2016 NE.19 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 168350 | 148508 | 5935 | 2172 | 0.00028285 | 1.1599e-06 | 243.8667 | 1 | 310 | Customer | 5536 | Load | TranOpenDelta | CAMERON PITTS | 405-537-6633 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.004765 | PD-02142020-00078 | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3421 | 843421 | 2020-02-14 08:39 | 2020-02-14 12:01 | 202.13 | 1 | 1 | 202.1333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1828 NE.54 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 168350 | 148508 | 1228 | 499 | 0.00023445 | 1.1599e-06 | 202.1333 | 1 | 310 | Customer | 18245 | Load | Tran1phOH | CAMERON PITTS | 405-537-6633 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | #N/A
J2002.004766 | PD-02142020-00076 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1524 | 811524 | 2020-02-14 08:42 | 2020-02-14 09:53 | 70.87 | 1 | 1 | 70.8667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 924 SW.34 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 159282 | 102245 | 6069 | 2071 | 8.2195e-05 | 1.1599e-06 | 70.8667 | 1 | 320 | Customer | 4377 | Load | Tran1phOH | GARY A DUNCAN | 405-474-9336 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.004768 | PD-02142020-00086 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4031 | 834031 | 2020-02-14 08:48 | 2020-02-14 10:12 | 84.48 | 1 | 1 | 79.1333 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 6516 NW 113TH ST | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862173 | 128984 | 116193 | 10845 | 1642 | 9.1784e-05 | 1.1599e-06 | 79.1333 | 1 | 310 | Customer | 73943 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004772 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9921 | 829921 | 2020-02-14 08:49 | 2020-02-14 09:32 | 42.55 | 40 | 35 | 1664 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | NW 23 + NORMAN AVE | CMI_PLANNED | YES | NO | NO | 862173 | 128984 | 116193 | 9241 | 1637 | 0.00193 | 4.6394e-05 | 41.6 | 1 | 310 | Mainline | 19251 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004770 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7031 | 817031 | 2020-02-14 08:52 | 2020-02-14 22:01 | 789.43 | 3 | 5 | 2200.5 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 9004 S.SHARTEL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 159282 | 102245 | 9937 | 1892 | 0.0025523 | 3.4796e-06 | 733.5 | 1 | 310 | Secondary | 2515 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004771 | PD-02142020-00087 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3926 | 833926 | 2020-02-14 08:54 | 2020-02-14 10:38 | 104.5 | 1 | 1 | 64.6665 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6716 WEDGEWOOD CIR BLDG 26 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 168350 | 148508 | 7852 | 1359 | 7.5004e-05 | 1.1599e-06 | 64.6665 | 1 | 310 | Customer | 49291 | Load | Tran1phPad | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.004783 | PD-02142020-00097 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3629 | 833629 | 2020-02-14 08:57 | 2020-02-14 13:15 | 257.78 | 16 | 18 | 4067.7333 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | THE VILLAGE | 2505 CARLTON WY | CMI_NORMAL | NO | NO | NO | 862173 | 168350 | 148508 | 8790 | 1399 | 0.004718 | 1.8558e-05 | 254.2333 | 1 | 310 | Load | 11953 | Load | Tran1phOH | TOMMY D ROBERTSON | 405-696-6476 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004780 | PD-02142020-00091 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2225 | 832225 | 2020-02-14 09:03 | 2020-02-14 09:57 | 53.52 | 1 | 2 | 41.9226 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2332 CASHION PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 168350 | 148508 | 9181 | 2040 | 4.8624e-05 | 1.1599e-06 | 41.9226 | 1 | 310 | Customer | 15919 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | OK - 2021
J2002.004779 | PD-02142020-00094 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3021 | 743021 | 2020-02-14 09:04 | 2020-02-14 09:33 | 29.4 | 1 | 1 | 29.4 | 13 | PREMATURE FAILURE | 15 | METER - SECONDARY | SHAWNEE | 716 N.HOBSON | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862173 | 114515 | 22141 | 6654 | 1702 | 3.41e-05 | 1.1599e-06 | 29.4 | 1 | 310 | Customer | 4510 | Load | Tran1phOH | ADAM CLARK | 580-310-8924 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2021
J2002.004784 | PD-02142020-00098 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6522 | 836522 | 2020-02-14 09:08 | 2020-02-14 11:09 | 120.65 | 1 | 1 | 7.2674 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6808 DECON AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 128984 | 116193 | 7424 | 1863 | 8.4291e-06 | 1.1599e-06 | 7.2674 | 1 | 310 | Customer | 47372 | Load | Tran1phPad | BRANDON H SMITH | 405-371-4294 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2021
J2002.004785 | PD-02142020-00105 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5021 | 865021 | 2020-02-14 09:16 | 2020-02-14 10:16 | 60.43 | 1 | 1 | 60.4333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 1110-2 S AIR DEPOT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 114515 | 71267 | 8634 | 1294 | 7.0094e-05 | 1.1599e-06 | 60.4333 | 1 | 310 | Customer | 72790 | Load | Tran3phWye | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004786 |  | NORTHEAST | SAPULPA | 7605:DRUMRIGHT | DRUMRIGHT_544 | 760544 | 2020-02-14 09:18 | 2020-02-14 13:30 | 251.8 | 1 | 1 | 218.95 | 4 | DETERIORATION | 12 | POLE | JENNINGS | 2N JENNINGS ON HWY 99 300'E | CMI_PLANNED | YES | NO | NO | 862173 | 74141 | 40822 | 1694 | 1114 | 0.00025395 | 1.1599e-06 | 218.95 | 1 | 308 | Load | 148903 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | #N/A
J2002.004789 | PD-02142020-00120 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_524 | 510524 | 2020-02-14 09:21 | 2020-02-14 11:59 | 157.77 | 1 | 1 | 157.7667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ARDMORE | 77/OAKLEY RD: .1S, WS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 77710 | 23606 | 4778 | 1434 | 0.00018299 | 1.1599e-06 | 157.7667 | 1 | 310 | Customer | 30677 | Load | Tran1phOH | GARRETT YOUNG | 580-276-6194 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | OK - 2021
J2002.004797 | PD-02142020-00114 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7424 | 847424 | 2020-02-14 09:23 | 2020-02-14 11:28 | 125.33 | 10 | 6 | 1238.3333 | 15 | SQUIRREL | 20 | FUSE BARREL | OKLAHOMA CITY | 1408 NE.40 | CMI_NORMAL | NO | NO | NO | 862173 | 168350 | 148508 | 6172 | 2199 | 0.0014363 | 1.1599e-05 | 123.8333 | 1 | 310 | Load | 13326 | Load | Tran1phOH | CAMERON PITTS | 405-537-6633 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2020
J2002.004790 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7424 | 847424 | 2020-02-14 09:23 | 2020-02-14 09:23 | 0.03 | 2199 | 0 | 73.3 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 1131 NE 33RD ST | CMI_MOMENTARY | YES | NO | NO | 862173 | 168350 | 148508 | 6172 | 2199 | 8.5018e-05 | 0.0025505 | 0.033333 | 1 | 0 | Feeder | STONEWALL_7424 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-14 | 2020 |  | OK - 2020
J2002.004792 |  | METRO NORTH | NORTH | 8506:PARK PLACE | PARK_PLACE_623 | 850623 | 2020-02-14 09:25 | 2020-02-14 09:28 | 2.95 | 1 | 1 | 2.95 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 617 NE.16 | CMI_MOMENTARY | YES | NO | NO | 862173 | 168350 | 148508 | 829 | 265 | 3.4216e-06 | 1.1599e-06 | 2.95 | 1 | 310 | Customer | 1438 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004793 | PD-02142020-00109 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7029 | 817029 | 2020-02-14 09:27 | 2020-02-14 10:34 | 66.8 | 1 | 1 | 49.7 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MOORE | 2856 N.MOORE AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 159282 | 102245 | 9937 | 1756 | 5.7645e-05 | 1.1599e-06 | 49.7 | 1 | 310 | Customer | 17456 | Load | TranOpenDelta | GARY A DUNCAN | 405-474-9336 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.004794 | PD-02142020-00110 | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2729 | 872729 | 2020-02-14 09:29 | 2020-02-14 10:35 | 66.48 | 1 | 1 | 66.4833 | 3 | DAMAGED BY PUBLIC | 15 | METER - SECONDARY | NORMAN | 609 Blue Fish Rd. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 159282 | 57037 | 6499 | 1270 | 7.7111e-05 | 1.1599e-06 | 66.4833 | 1 | 310 | Customer | 392168 | Load | Tran1phPad | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004805 | PD-02142020-00134 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_524 | 510524 | 2020-02-14 09:54 | 2020-02-14 16:20 | 386.25 | 1 | 2 | 75.4167 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | MARIETTA | Lake Murray - about 400'' SSE of Buzzard Loop | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862173 | 77710 | 23606 | 4778 | 1434 | 8.7473e-05 | 1.1599e-06 | 75.4167 | 1 | 310 | Load | 345082 | Load | Tran1phPad | RANDAL G CALLAWAY | 580-220-8449 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | OK - 2021
J2002.004806 |  | SOUTHERN | DURANT | 5504:BUTTERFIELD | BUTTERFIELD_422 | 550422 | 2020-02-14 09:55 | 2020-02-14 12:43 | 168.52 | 7 | 3 | 404.3667 | 4 | DETERIORATION | 12 | POLE | ACHILLE | 3BS 78 FROM PO | CMI_PLANNED | YES | NO | NO | 862173 | 77710 | 15520 | 3488 | 561 | 0.00046901 | 8.119e-06 | 57.7667 | 1 | 308 | Load | 21643 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004809 | PD-02142020-00140 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2023 | 822023 | 2020-02-14 09:58 | 2020-02-14 11:22 | 84.02 | 1 | 1 | 82.3833 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 3204 NW.26 | CMI_NORMAL | NO | NO | NO | 862173 | 168350 | 148508 | 6039 | 1028 | 9.5553e-05 | 1.1599e-06 | 82.3833 | 1 | 310 | Customer | 15675 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.004811 | PD-02142020-00141 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6521 | 836521 | 2020-02-14 10:00 | 2020-02-14 10:47 | 46.5 | 1 | 1 | 23.1444 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4535 NW 63 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 128984 | 116193 | 7424 | 1646 | 2.6844e-05 | 1.1599e-06 | 23.1444 | 1 | 320 | Customer | 84975 | Load | Tran3phWye | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.004812 |  | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-02-14 10:04 | 2020-02-14 10:07 | 3.15 | 1 | 1 | 3.15 | 1 | CANCELLED | 57 | CANCELLED | DEL CITY | 2504 EPPERLY DR | CMI_MOMENTARY | YES | NO | NO | 862173 | 159282 | 102245 | 7424 | 2240 | 3.6536e-06 | 1.1599e-06 | 3.15 | 1 | 310 | Customer | 6050 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.004817 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2122 | 822122 | 2020-02-14 10:15 | 2020-02-14 13:01 | 165.95 | 17 | 12 | 2735.3 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 4124 NW.16 | CMI_PLANNED | YES | NO | NO | 862173 | 168350 | 148508 | 9250 | 1837 | 0.0031726 | 1.9718e-05 | 160.9 | 1 | 310 | Load | 6280 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2020
J2002.004815 | PD-02142020-00147 | METRO NORTH | NORTH | 8209:CLASSEN | CLASSEN_921 | 820921 | 2020-02-14 10:21 | 2020-02-14 11:24 | 62.77 | 1 | 1 | 62.7667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1108.5 NW 11--OKC | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 168350 | 148508 | 3889 | 452 | 7.2801e-05 | 1.1599e-06 | 62.7667 | 1 | 320 | Customer | 5669 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004827 | PD-02142020-00167 | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1623 | 581623 | 2020-02-14 10:39 | 2020-02-14 11:11 | 31.65 | 1 | 1 | 31.65 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ADA | MAIN + RENNIE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 77710 | 11524 | 3465 | 1654 | 3.671e-05 | 1.1599e-06 | 31.65 | 1 | 310 | Customer | 483 | Load | Tran3phWye | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004830 |  | SOUTHERN | SULPHUR | 5706:LAKE ARBUCKLE | LAKE ARBUCKLE 46 | 570646 | 2020-02-14 10:49 | 2020-02-14 13:13 | 143.9 | 1 | 0 | 36.1667 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | DOUGHERTY | NE CRNR 1ST AVE & 1ST ST NORTH | CMI_PLANNED | YES | NO | NO | 862173 | 77710 | 6819 | 366 | 239 | 4.1948e-05 | 1.1599e-06 | 36.1667 | 1 | 0 | Load | 4907 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | #N/A
J2002.004833 |  | METRO EAST | EAST | 8542:RENO | RENO_4229 | 854229 | 2020-02-14 10:52 | 2020-02-14 11:00 | 8.3 | 1 | 1 | 8.3 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DEL CITY | 4824 VERA PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 114515 | 71267 | 5218 | 1347 | 9.6268e-06 | 1.1599e-06 | 8.3 | 1 | 310 | Customer | 32583 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.004834 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-02-14 10:56 | 2020-02-14 11:25 | 28.58 | 9 | 0 | 208.05 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | JESSE TRAIL & SE 76TH PL | CMI_PLANNED | YES | NO | NO | 862173 | 159282 | 57037 | 4238 | 1005 | 0.00024131 | 1.0439e-05 | 23.1167 | 1 | 0 | Load | 234177 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004835 | PD-02142020-00177 | ARKANSAS | FORT SMITH | 9115:BATTLEFIELD | BATTLEFIELD_1524 | 911524 | 2020-02-14 10:56 | 2020-02-14 11:59 | 62.63 | 1 | 1 | 62.6333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 5900 COMMERCE RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 82344 | 61271 | 1186 | 29 | 7.2646e-05 | 1.1599e-06 | 62.6333 | 1 | 310 | Customer | 169704 | Load | Tran1phOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-14 | 2020 |  | #N/A
J2002.004839 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7022 | 817022 | 2020-02-14 11:16 | 2020-02-14 12:48 | 91.65 | 12 | 9 | 807.8 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | 12 CORONA NR | CMI_PLANNED | YES | NO | NO | 862173 | 159282 | 102245 | 9937 | 2103 | 0.00093693 | 1.3918e-05 | 67.3167 | 1 | 308 | Load | 62248 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004843 | PD-02142020-00244 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6921 | 846921 | 2020-02-14 11:26 | 2020-02-14 12:31 | 65.33 | 1 | 1 | 65.3333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | Lot 7 block 4 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 168350 | 148508 | 7732 | 1358 | 7.5778e-05 | 1.1599e-06 | 65.3333 | 1 | 310 | Customer | 386071 | Load | Tran1phPad | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004859 | PD-02142020-00262 | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3721 | 913721 | 2020-02-14 11:36 | 2020-02-14 12:53 | 76.92 | 4 | 4 | 288.4333 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 21 | FUSE - TRANSFORMER | FORT SMITH | 443 N.48 | CMI_NORMAL | NO | NO | NO | 862173 | 82344 | 61271 | 4575 | 1500 | 0.00033454 | 4.6394e-06 | 72.1083 | 1 | 310 | Load | 9657 | Load | Tran1phOH | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | Ark - Series 3
J2002.004857 | PD-02142020-00264 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_863 | 830863 | 2020-02-14 11:40 | 2020-02-14 13:02 | 82.5 | 1 | 1 | 82.5 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | .5MW OF PENN + NW.142 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 168350 | 148508 | 19421 | 1673 | 9.5688e-05 | 1.1599e-06 | 82.5 | 1 | 310 | Customer | 69766 | Load | Tran1phPad | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004860 | PD-02142020-00261 | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2524 | 512524 | 2020-02-14 11:41 | 2020-02-14 13:29 | 108.12 | 1 | 1 | 99.3 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | ARDMORE | 1.9 S.PLNVW SCH .1W | CMI_NORMAL | NO | NO | NO | 862173 | 77710 | 23606 | 3308 | 1001 | 0.00011517 | 1.1599e-06 | 99.3 | 1 | 310 | Load | 27861 | Load | Tran1phPad | GARRETT YOUNG | 580-276-6194 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004865 |  | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2721 | 872721 | 2020-02-14 11:52 | 2020-02-14 12:14 | 22.02 | 1 | 1 | 22.0167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | NORMAN | 505 TELSTAR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 159282 | 57037 | 6499 | 960 | 2.5536e-05 | 1.1599e-06 | 22.0167 | 1 | 310 | Customer | 62775 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004866 | PD-02142020-00267 | METRO WEST | WEST | 8359:YUKON | YUKON_5923 | 835923 | 2020-02-14 11:55 | 2020-02-14 13:09 | 74.22 | 1 | 1 | 74.2167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | YUKON | 813 Maple Ave | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 128984 | 116193 | 6438 | 1152 | 8.6081e-05 | 1.1599e-06 | 74.2167 | 1 | 310 | Customer | 19399 | Load | Tran1phOH | JOSH BLACK | 405-403-9382 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | #N/A
J2002.004867 | PD-02142020-00270 | SOUTHERN | HEALDTON | 5319:FOX | FOX 22 | 531922 | 2020-02-14 11:56 | 2020-02-14 13:40 | 104.27 | 1 | 1 | 104.2667 | 5 | ELECTRICAL TRACKING | 23 | FUSE - PRIMARY | FOX | GRAHAM DEESE UNIT (MOBIL) | CMI_NORMAL | NO | NO | NO | 862173 | 77710 | 6810 | 709 | 215 | 0.00012093 | 1.1599e-06 | 104.2667 | 1 | 320 | Load | 90055 | Load | 0 | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004869 |  | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1722 | 911722 | 2020-02-14 12:06 | 2020-02-14 12:24 | 17.52 | 1 | 1 | 17.5167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 9711 MOODY RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 82344 | 61271 | 4247 | 1475 | 2.0317e-05 | 1.1599e-06 | 17.5167 | 1 | 310 | Customer | 3789 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-14 | 2020 |  | #N/A
J2002.004873 |  | ARKANSAS | POTEAU | 3505:POTEAU | POTEAU_529 | 350529 | 2020-02-14 12:19 | 2020-02-14 14:25 | 125.72 | 11 | 10 | 1261.5167 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | POTEAU | 1004.5 S.HARPER | CMI_PLANNED | YES | NO | NO | 862173 | 82344 | 13520 | 2307 | 442 | 0.0014632 | 1.2758e-05 | 114.6833 | 1 | 310 | Load | 6799 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | #N/A
J2002.004877 | PD-02142020-00283 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3924 | 833924 | 2020-02-14 12:28 | 2020-02-14 12:54 | 25.72 | 1 | 1 | 14.8744 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3808 NW.66 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 168350 | 148508 | 7852 | 793 | 1.7252e-05 | 1.1599e-06 | 14.8744 | 1 | 310 | Customer | 21314 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.004879 | PD-02142020-00284 | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_521 | 530521 | 2020-02-14 12:32 | 2020-02-14 14:35 | 122.5 | 1 | 1 | 122.5 | 12 | POOR CONNECTION | 50 | CONNECTOR | HEALDTON | 609 ROCKLAND | CMI_NORMAL | NO | NO | NO | 862173 | 77710 | 6810 | 2132 | 1263 | 0.00014208 | 1.1599e-06 | 122.5 | 1 | 320 | Customer | 8679 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | OK - 2020
J2002.004883 | PD-02142020-00288 | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_422 | 510422 | 2020-02-14 12:39 | 2020-02-14 14:46 | 127.2 | 1 | 2 | 123.85 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | ARDMORE | GA 3.3S WS | CMI_NORMAL | NO | NO | NO | 862173 | 77710 | 23606 | 2320 | 1058 | 0.00014365 | 1.1599e-06 | 123.85 | 1 | 310 | Load | 4575 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004882 | PD-02142020-00299 | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5221 | 835221 | 2020-02-14 12:40 | 2020-02-14 13:55 | 75.1 | 1 | 1 | 30.4578 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4400 FOXGLOVE LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 168350 | 148508 | 6519 | 1500 | 3.5327e-05 | 1.1599e-06 | 30.4578 | 1 | 320 | Customer | 53102 | Load | Tran1phPad | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004885 |  | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_524 | 510524 | 2020-02-14 12:44 | 2020-02-14 13:08 | 24.17 | 1 | 1 | 24.1667 | 1 | CANCELLED | 57 | CANCELLED | ARDMORE | 77/OAKLEY RD: .1S, WS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 77710 | 23606 | 4778 | 1434 | 2.803e-05 | 1.1599e-06 | 24.1667 | 1 | 310 | Customer | 30677 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | OK - 2021
J2002.004887 | PD-02142020-00289 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2229 | 852229 | 2020-02-14 12:48 | 2020-02-14 13:42 | 54.12 | 1 | 1 | 54.1167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | CHOCTAW | N. OF NE 10, ES IND. MER. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 114515 | 71267 | 11645 | 1391 | 6.2768e-05 | 1.1599e-06 | 54.1167 | 1 | 310 | Load | 176382 | Load | Tran1phOH | CHRIS PROCELL | 405-831-2791 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004890 | PD-02142020-00293 | METRO EAST | SHAWNEE | 7430:INGLEWOOD | INGLEWOOD_3022 | 743022 | 2020-02-14 12:52 | 2020-02-14 14:15 | 82.88 | 1 | 1 | 75.3 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | SHAWNEE | 639 W BENEDICT | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862173 | 114515 | 22141 | 6654 | 2171 | 8.7337e-05 | 1.1599e-06 | 75.3 | 1 | 310 | Customer | 4131 | Load | Tran1phOH | ADAM CLARK | 580-310-8924 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2020
J2002.004894 | PD-02142020-00308 | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-02-14 13:01 | 2020-02-14 14:18 | 76.6 | 6 | 9 | 238.05 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | MUSTANG | 717 W.FORSTER DR | CMI_NORMAL | NO | NO | NO | 862173 | 128984 | 116193 | 18284 | 4430 | 0.0002761 | 6.9592e-06 | 39.675 | 1 | 310 | Secondary | 58390 | Load | Tran1phOH | BRANDON H SMITH | 405-371-4294 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.004895 | PD-02142020-00320 | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2524 | 512524 | 2020-02-14 13:07 | 2020-02-14 14:06 | 58.98 | 1 | 1 | 58.9833 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | ARDMORE | 77/BUSSELL RD .5W .2N.1E .1N | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862173 | 77710 | 23606 | 3308 | 1001 | 6.8412e-05 | 1.1599e-06 | 58.9833 | 1 | 310 | Customer | 29587 | Load | Tran1phOH | JOE LOFTIS | 918-884-5349 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004898 | PD-02142020-00316 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-02-14 13:14 | 2020-02-14 14:45 | 91.1 | 1 | 1 | 91.1 | 13 | PREMATURE FAILURE | 15 | METER - SECONDARY | DEL CITY | 2504 EPPERLY DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862173 | 159282 | 102245 | 7424 | 2240 | 0.00010566 | 1.1599e-06 | 91.1 | 1 | 310 | Customer | 6050 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.004899 | PD-02142020-00323 | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1421 | 911421 | 2020-02-14 13:15 | 2020-02-14 15:15 | 119.97 | 1 | 2 | 4.0167 | 12 | POOR CONNECTION | 50 | CONNECTOR | FORT SMITH | 1813 N.34 CT | CMI_NORMAL | NO | NO | NO | 862173 | 82344 | 61271 | 4742 | 1751 | 4.6588e-06 | 1.1599e-06 | 4.0167 | 1 | 310 | Customer | 12805 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-14 | 2020 |  | Ark - Series 1
J2002.004900 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-14 13:18 | 2020-02-14 16:37 | 198.77 | 2 | 3 | 391.8333 | 4 | DETERIORATION | 12 | POLE | POCOLA | OKLA RURAL | CMI_PLANNED | YES | NO | NO | 862173 | 82344 | 61271 | 1458 | 1240 | 0.00045447 | 2.3197e-06 | 195.9167 | 1 | 310 | Load | 11255 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | Ark - Series 2
J2002.004908 |  | ARKANSAS | FORT SMITH | 9512:ADABELL ROAD | ADABELL_ROAD_1224 | 951224 | 2020-02-14 13:41 | 2020-02-14 16:36 | 174.88 | 1 | 0 | 54.3667 | 4 | DETERIORATION | 50 | CONNECTOR | VAN BUREN | 15 MT-VISTA AV, VAN BUREN | CMI_PLANNED | YES | NO | NO | 862173 | 82344 | 61271 | 3125 | 939 | 6.3058e-05 | 1.1599e-06 | 54.3667 | 1 | 0 | Load | 3901 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-14 | 2020 |  | Ark - Series 1, Ark - Series 2
J2002.004920 |  | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2924 | 812924 | 2020-02-14 14:00 | 2020-02-14 14:15 | 14.98 | 1 | 1 | 14.9833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2839 SW.64 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 159282 | 102245 | 6392 | 2130 | 1.7379e-05 | 1.1599e-06 | 14.9833 | 1 | 310 | Customer | 17260 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | #N/A
J2002.004951 | PD-02142020-00396 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6524 | 836524 | 2020-02-14 15:06 | 2020-02-14 16:13 | 66.77 | 1 | 1 | 66.7667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6389 NW.63 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 128984 | 116193 | 7424 | 1651 | 7.744e-05 | 1.1599e-06 | 66.7667 | 1 | 320 | Customer | 34575 | Load | Tran1phPad | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004954 | PD-02142020-00410 | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3821 | 913821 | 2020-02-14 15:07 | 2020-02-14 16:01 | 54.17 | 1 | 1 | 54.1667 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 23 | FUSE - PRIMARY | FORT SMITH | POST OFFICE PADMOUNT | CMI_NORMAL | NO | NO | NO | 862173 | 82344 | 61271 | 2944 | 210 | 6.2826e-05 | 1.1599e-06 | 54.1667 | 1 | 310 | Customer | 18198 | Load | Tran3phPadWye | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Animals | N | DISTRIBUTION | 161kV | 2020-02-14 | 2020 |  | Ark - Series 2
J2002.004953 | PD-02142020-00402 | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_923 | 910923 | 2020-02-14 15:07 | 2020-02-14 17:52 | 164.92 | 1 | 2 | 164.9167 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | FORT SMITH | 5302 WHEELER AV | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862173 | 82344 | 61271 | 5015 | 902 | 0.00019128 | 1.1599e-06 | 164.9167 | 1 | 320 | Load | 12348 | Load | Tran1phOH | CONTRACTOR 5 DAVID ELLIOT INC | 918-639-5055 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | Ark - Series 3
J2002.004955 | PD-02142020-00397 | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5423 | 865423 | 2020-02-14 15:10 | 2020-02-14 15:32 | 22.37 | 1 | 1 | 22.3667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MOORE | L7B4 MADISON PL SEC.2 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 159282 | 102245 | 9811 | 1722 | 2.5942e-05 | 1.1599e-06 | 22.3667 | 1 | 310 | Customer | 205537 | Load | Tran1phPad | JACOB SHANDY | 918-623-6369 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004966 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-14 15:18 | 2020-02-14 16:38 | 79.97 | 1 | 1 | 73.3333 | 4 | DETERIORATION | 12 | POLE | LAMAR | 1000 E-HWY 64 ON E MAIN,LAMAR | CMI_PLANNED | YES | NO | NO | 862173 | 82344 | 7553 | 730 | 0 | 8.5056e-05 | 1.1599e-06 | 73.3333 | 1 | 308 | Load | 2436 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | #N/A
J2002.004975 | PD-02142020-00438 | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1729 | 831729 | 2020-02-14 16:02 | 2020-02-14 21:57 | 355.35 | 1 | 2 | 256.1667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | W Memorial Road and Pawnee Dr | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862173 | 168350 | 148508 | 6649 | 649 | 0.00029712 | 1.1599e-06 | 256.1667 | 1 | 310 | Load | 405364 | Load | Tran3phWye | TOMMY D ROBERTSON | 405-696-6476 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004976 | PD-02142020-00441 | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3421 | 843421 | 2020-02-14 16:02 | 2020-02-14 17:10 | 67.78 | 1 | 1 | 67.7833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1716 NE.51 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 168350 | 148508 | 1228 | 499 | 7.8619e-05 | 1.1599e-06 | 67.7833 | 1 | 310 | Customer | 18518 | Load | Tran1phOH | PETER BILICKI | 619-726-8332 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | #N/A
J2002.004982 | PD-02142020-00452 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2022 | 862022 | 2020-02-14 16:26 | 2020-02-14 17:20 | 53.93 | 1 | 1 | 11.5224 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 4420 S.HIGH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 159282 | 102245 | 4759 | 1555 | 1.3364e-05 | 1.1599e-06 | 11.5224 | 1 | 310 | Customer | 10810 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004983 |  | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_621 | 880621 | 2020-02-14 16:26 | 2020-02-14 16:51 | 24.87 | 1 | 1 | 24.8667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | GUTHRIE | Triple Crown Meadow Lot 24 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 168350 | 19842 | 5175 | 1882 | 2.8842e-05 | 1.1599e-06 | 24.8667 | 1 | 310 | Customer | 246552 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004984 |  | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6022 | 836022 | 2020-02-14 16:27 | 2020-02-14 16:46 | 18.5 | 1 | 1 | 18.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BETHANY | 3037 N ROCKWELL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 128984 | 116193 | 5509 | 1234 | 2.1457e-05 | 1.1599e-06 | 18.5 | 1 | 310 | Customer | 34500 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.004989 | PD-02142020-00459 | METRO EAST | CHANDLER | 7119:WARWICK | WARWICK_1942 | 711942 | 2020-02-14 16:45 | 2020-02-14 19:19 | 154.35 | 1 | 1 | 67.6435 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | TRYON | sherwood forrest | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 114515 | 7481 | 2424 | 958 | 7.8457e-05 | 1.1599e-06 | 67.6435 | 1 | 310 | Load | 357624 | Load | Tran1phOH | BRAD WRIGHT | 918-629-1747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.004990 |  | METRO NORTH | GUTHRIE | 8807:CRESCENT | CRESCENT_721 | 880721 | 2020-02-14 16:52 | 2020-02-14 17:11 | 18.95 | 1 | 1 | 18.95 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | CRESCENT | 315 E.VANBUREN - CRESCENT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 168350 | 19842 | 1768 | 874 | 2.1979e-05 | 1.1599e-06 | 18.95 | 1 | 310 | Load | 49372 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004993 | PD-02142020-00477 | METRO WEST | WEST | 8321:PIEDMONT | PIEDMONT_2162 | 832162 | 2020-02-14 17:17 | 2020-02-14 18:15 | 58.4 | 2 | 2 | 269.65 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 11740 NW 130th ST | CMI_NORMAL | NO | NO | NO | 862173 | 128984 | 116193 | 6308 | 1631 | 0.00031276 | 2.3197e-06 | 134.825 | 1 | 310 | Secondary | 391775 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.004994 |  | METRO NORTH | NORTH | 8317:SKYLINE | SKYLINE_1722 | 831722 | 2020-02-14 17:21 | 2020-02-14 17:25 | 3.32 | 1 | 1 | 3.3167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 213 NW.120 | CMI_MOMENTARY | YES | NO | NO | 862173 | 168350 | 148508 | 6649 | 1203 | 3.8469e-06 | 1.1599e-06 | 3.3167 | 1 | 310 | Customer | 59557 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.005000 | PD-02142020-00478 | NORTHEAST | SAPULPA | 3220:KELLYVILLE | KELLYVILLE_2029 | 322029 | 2020-02-14 17:31 | 2020-02-15 02:07 | 515.55 | 17 | 12 | 8238.2 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | KELLYVILLE | REAMES TR PK | CMI_NORMAL | NO | NO | NO | 862173 | 74141 | 40822 | 2554 | 972 | 0.0095552 | 1.9718e-05 | 484.6 | 1 | 310 | Load | 47207 | Load | Tran1phPad | DWAYNE FOX | 405-695-8501 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.005002 |  | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_621 | 880621 | 2020-02-14 17:51 | 2020-02-14 18:01 | 10.35 | 1 | 1 | 10.35 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | GUTHRIE | Triple Crown Meadow Lot 24 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 168350 | 19842 | 5175 | 1882 | 1.2005e-05 | 1.1599e-06 | 10.35 | 1 | 310 | Customer | 246552 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.005005 |  | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6022 | 836022 | 2020-02-14 18:07 | 2020-02-14 18:19 | 12.13 | 1 | 1 | 12.1333 | 1 | CANCELLED | 57 | CANCELLED | BETHANY | 3037 N ROCKWELL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 129015 | 116216 | 5510 | 1235 | 1.4073e-05 | 1.1599e-06 | 12.1333 | 1 | 310 | Customer | 34500 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.005007 | PD-02142020-00479 | METRO EAST | SEMINOLE | 7312:JUMPER CREEK | JUMPER_CREEK_1227 | 731227 | 2020-02-14 18:10 | 2020-02-14 20:02 | 112.18 | 1 | 1 | 81.1833 | 22 | WIND | 21 | FUSE - TRANSFORMER | KONAWA | 313 W.SOUTH ST | CMI_NORMAL | NO | NO | NO | 862173 | 114528 | 13626 | 1217 | 885 | 9.4161e-05 | 1.1599e-06 | 81.1833 | 1 | 310 | Load | 17491 | Load | TranOpenDelta | KEVIN M RICH | 405-802-2121 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | OK - 2021
J2002.005011 |  | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2223 | 832223 | 2020-02-14 18:49 | 2020-02-14 18:55 | 5.57 | 1 | 1 | 5.5667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2930 NW.32 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 168371 | 148528 | 9181 | 1444 | 6.4566e-06 | 1.1599e-06 | 5.5667 | 1 | 310 | Customer | 4908 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | OK - 2021
J2002.005012 |  | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_621 | 880621 | 2020-02-14 18:56 | 2020-02-14 19:09 | 13.6 | 1 | 1 | 13.6 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | GUTHRIE | Triple Crown Meadow Lot 24 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 168371 | 19843 | 5175 | 1882 | 1.5774e-05 | 1.1599e-06 | 13.6 | 1 | 310 | Customer | 246552 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.005013 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7029 | 817029 | 2020-02-14 19:08 | 2020-02-14 19:45 | 36.62 | 59 | 43 | 1277.35 | 1 | CANCELLED | 57 | CANCELLED | MOORE | HILLCRST DR+CASS AVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 159301 | 102255 | 9938 | 1756 | 0.0014815 | 6.8432e-05 | 21.65 | 1 | 310 | Mainline | 7970 | Fuse | FuseOH | OGE | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.005016 | PD-02142020-00481 | METRO EAST | CHANDLER | 7118:KEY WEST | KEY_WEST_1846 | 711846 | 2020-02-14 19:16 | 2020-02-14 22:27 | 191.4 | 1 | 1 | 153.3833 | 11 | OVERLOAD | 23 | FUSE - PRIMARY | CHANDLER | STROUD PSU | CMI_NORMAL | NO | NO | NO | 862173 | 114528 | 7482 | 1216 | 470 | 0.0001779 | 1.1599e-06 | 153.3833 | 1 | 310 | Load | 90138 | Load | 0 | KELLEY D WATSON | 405-763-8148 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2021
J2002.005025 | PD-02142020-00486 | NORTHWEST | ALVA | 4707:KNOBHILL | KNOBHILL_730 | 470730 | 2020-02-14 19:53 | 2020-02-14 21:25 | 92.38 | 1 | 1 | 92.3833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ALVA | 63O LOGAN--ALVA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 53606 | 5524 | 1742 | 525 | 0.00010715 | 1.1599e-06 | 92.3833 | 1 | 310 | Customer | 9082 | Load | Tran1phOH | PATRICK LYONS | 580-395-4171 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | #N/A
J2002.005026 |  | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2821 | 312821 | 2020-02-14 19:57 | 2020-02-14 20:06 | 8.67 | 1 | 1 | 8.6667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 827 S.YORK 23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 74153 | 33323 | 5285 | 1153 | 1.0052e-05 | 1.1599e-06 | 8.6667 | 1 | 310 | Customer | 14089 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-14 | 2020 |  | #N/A
J2002.005029 | PD-02142020-00495 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6124 | 836124 | 2020-02-14 20:29 | 2020-02-14 21:50 | 80.73 | 1 | 1 | 80.7333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1709 NW.31 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 168371 | 148528 | 11118 | 1768 | 9.3639e-05 | 1.1599e-06 | 80.7333 | 1 | 320 | Customer | 1301 | Load | Tran1phOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2020
J2002.005033 |  | SOUTHERN | PAULS VALLEY | 5619:RUSH CREEK | RUSH_CREEK_1922 | 561922 | 2020-02-14 20:46 | 2020-02-14 21:00 | 13.35 | 1 | 1 | 13.35 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | PAULS VALLEY | S OF CITY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862173 | 77721 | 6231 | 2078 | 1195 | 1.5484e-05 | 1.1599e-06 | 13.35 | 1 | 310 | Customer | 1417 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | OK - 2021
J2002.005034 | PD-02142020-00500 | METRO WEST | WEST | 8158:SARA | SARA_5864 | 815864 | 2020-02-14 20:51 | 2020-02-14 22:38 | 106.7 | 1 | 2 | 106.7 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | TORRE PINES-HWY 92,SW 15 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862173 | 129015 | 116216 | 18290 | 4820 | 0.00012376 | 1.1599e-06 | 106.7 | 1 | 310 | Customer | 87411 | Load | Tran1phOH | JESSE PHILLER | 405-512-8086 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.005036 |  | METRO EAST | EAST | 8542:RENO | RENO_4224 | 854224 | 2020-02-14 21:14 | 2020-02-14 21:15 | 0.02 | 1223 | 0 | 20.3833 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 300 S SUNNYLAND RD | CMI_MOMENTARY | YES | NO | NO | 862173 | 114528 | 71274 | 5218 | 1223 | 2.3642e-05 | 0.0014185 | 0.016667 | 1 | 0 | Feeder | RENO_4224 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.005042 |  | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2022 | 822022 | 2020-02-14 21:41 | 2020-02-15 00:03 | 142.17 | 12 | 12 | 811.6 | 4 | DETERIORATION | 28 | CROSSARM | OKLAHOMA CITY | 2729 NW.PARK | CMI_NORMAL | NO | NO | NO | 862173 | 168371 | 148528 | 6039 | 2121 | 0.00094134 | 1.3918e-05 | 67.6333 | 1 | 310 | Load | 889 | Load | Tran1phOH | Ties | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-14 | 2020 |  | OK - 2020
J2002.005063 | PD-02152020-00001 | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5022 | 865022 | 2020-02-14 22:47 | 2020-02-15 04:13 | 326.25 | 1 | 1 | 324.0667 | 4 | DETERIORATION | 27 | CUTOUT | MIDWEST CITY | 1520 OCAMA BLVD | CMI_NORMAL | NO | NO | NO | 862173 | 114528 | 71274 | 8634 | 1662 | 0.00037587 | 1.1599e-06 | 324.0667 | 1 | 308 | Customer | 55184 | Load | TranOH3phDelta | JEREMIAH D WALKER | 405-974-0464 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.005052 |  | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5022 | 865022 | 2020-02-14 22:47 | 2020-02-14 22:48 | 1 | 1661 | 1 | 1661 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MIDWEST CITY | 8346 SE 15TH | CMI_MOMENTARY | YES | NO | NO | 862173 | 114528 | 71274 | 8634 | 1662 | 0.0019265 | 0.0019265 | 1 | 1 | 310 | Feeder | GLENDALE_5022 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-14 | 2020 |  | OK - 2022
J2002.005055 | PD-02142020-00512 | METRO NORTH | GUTHRIE | 8819:LIBERTY LAKE | LIBERTY_LAKE_1923 | 881923 | 2020-02-14 22:56 | 2020-02-15 00:01 | 64.98 | 3 | 3 | 173.15 | 4 | DETERIORATION | 21 | FUSE - TRANSFORMER | GUTHRIE | 9726 STACI LANE | CMI_NORMAL | NO | NO | NO | 862173 | 168371 | 19843 | 3355 | 1828 | 0.00020083 | 3.4796e-06 | 57.7167 | 1 | 310 | Load | 68414 | Load | Tran1phOH | KELLEY D WATSON | 405-763-8148 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | #N/A
J2002.005057 | PD-02142020-00515 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1222 | 831222 | 2020-02-14 23:07 | 2020-02-15 02:26 | 199.12 | 7 | 10 | 1320.0833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 2317 NW.56 | CMI_NORMAL | NO | NO | NO | 862173 | 168371 | 148528 | 7757 | 1008 | 0.0015311 | 8.119e-06 | 188.5833 | 1 | 310 | Load | 13298 | Load | TranOpenDelta | TOMMY D ROBERTSON | 405-696-6476 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-14 | 2020 |  | OK - 2021
J2002.005080 | PD-02152020-00011 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1228 | 831228 | 2020-02-15 02:37 | 2020-02-15 03:40 | 62.88 | 5 | 4 | 214.9167 | 22 | WIND | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 5433 N.MILITARY | CMI_NORMAL | NO | NO | NO | 862173 | 168371 | 148528 | 7757 | 522 | 0.00024927 | 5.7993e-06 | 42.9833 | 1 | 310 | Load | 10951 | Load | Tran1phOH | COLTON RACKLEY | 405-779-5033 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | OK - 2021
J2002.005083 |  | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_621 | 770621 | 2020-02-15 03:19 | 2020-02-15 03:20 | 0.77 | 1575 | 5 | 1207.5 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | BRISTOW | JAYCEE AVE AND S CEDAR STREET | CMI_MOMENTARY | YES | NO | NO | 862173 | 74153 | 40830 | 3786 | 1576 | 0.0014005 | 0.0018268 | 0.76667 | 1 | 310 | Feeder | BRISTOW_621 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-15 | 2020 |  | OK - 2021
J2002.005107 | PD-02152020-00012 | NORTHWEST | ENID | 4123:KREMLIN TAP | KREMLIN TAP 21 | 412321 | 2020-02-15 07:20 | 2020-02-15 09:15 | 114.97 | 1 | 1 | 112.8833 | 28 | OTHER (DESCRIBE) | 17 | JUMPER | KREMLIN | 123E KEOWEE | CMI_NORMAL | NO | NO | NO | 862220 | 53606 | 37642 | 432 | 414 | 0.00013092 | 1.1598e-06 | 112.8833 | 1 | 310 | Load | 316703 | Load | Tran1phOH | [7 empty] | Other | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | #N/A
J2002.005108 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7031 | 817031 | 2020-02-15 07:25 | 2020-02-15 08:01 | 35.07 | 1 | 1 | 35.0667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 9004 S.SHARTEL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 159301 | 102255 | 9938 | 1892 | 4.067e-05 | 1.1598e-06 | 35.0667 | 1 | 310 | Customer | 2515 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005110 |  | SOUTHERN | ADA | 5809:VANOSS | VANOSS_922 | 580922 | 2020-02-15 07:27 | 2020-02-15 07:40 | 13.23 | 1 | 1 | 13.2333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | STRATFORD | BETWEEN SYCAMORE & MAPLE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 77721 | 11525 | 979 | 979 | 1.5348e-05 | 1.1598e-06 | 13.2333 | 1 | 310 | Customer | 181892 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | OK - 2021
J2002.005119 | PD-02152020-00014 | SOUTHERN | ADA | 5809:VANOSS | VANOSS_922 | 580922 | 2020-02-15 07:52 | 2020-02-15 08:32 | 39.63 | 1 | 1 | 39.6333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | STRATFORD | BETWEEN SYCAMORE & MAPLE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 77721 | 11525 | 979 | 979 | 4.5967e-05 | 1.1598e-06 | 39.6333 | 1 | 310 | Customer | 181892 | Load | Tran1phPad | GARRID H BROWN | 405-207-3948 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | OK - 2021
J2002.005118 | PD-02152020-00015 | NORTHEAST | MUSKOGEE | 3325:WELLS | WELLS_2549 | 332549 | 2020-02-15 07:53 | 2020-02-15 09:02 | 69.3 | 1 | 1 | 63.3833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | CHECOTAH | 1MN OF RDO GR | CMI_NORMAL | NO | NO | NO | 862220 | 74153 | 33323 | 2383 | 1054 | 7.3512e-05 | 1.1598e-06 | 63.3833 | 1 | 310 | Load | 14689 | Load | Tran1phOH | NICHOLAS SELVIDGE | 918-652-1986 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | OK - 2021
J2002.005117 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3829 | 913829 | 2020-02-15 07:53 | 2020-02-15 11:49 | 236.43 | 10 | 7 | 2301 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 1904 S.W | CMI_PLANNED | YES | NO | NO | 862220 | 82360 | 61281 | 2945 | 1191 | 0.0026687 | 1.1598e-05 | 230.1 | 1 | 308 | Load | 6626 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-15 | 2020 |  | Ark - Series 2
J2002.005124 | PD-02152020-00018 | METRO EAST | SHAWNEE | 7412:PEARSON | PEARSON 21 | 741221 | 2020-02-15 08:28 | 2020-02-15 09:56 | 88.22 | 1 | 1 | 85.7 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ASHER | 1.5BN CH OF CHR | CMI_NORMAL | NO | NO | NO | 862220 | 114528 | 22146 | 678 | 678 | 9.9395e-05 | 1.1598e-06 | 85.7 | 1 | 310 | Load | 6156 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | OK - 2021
J2002.005127 | PD-02152020-00019 | ARKANSAS | POTEAU | 3505:POTEAU | POTEAU_522 | 350522 | 2020-02-15 08:30 | 2020-02-15 10:09 | 99.07 | 3 | 3 | 289.7 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | POTEAU | ARNALL ACRES TRAILER PARK | CMI_NORMAL | NO | NO | NO | 862220 | 82360 | 13525 | 2308 | 358 | 0.00033599 | 3.4794e-06 | 96.5667 | 1 | 310 | Load | 17216 | Load | Tran1phOH | BRANDON K BRYAN | 479-831-3888 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | #N/A
J2002.005132 | PD-02152020-00020 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2024 | 822024 | 2020-02-15 08:50 | 2020-02-15 09:51 | 61.2 | 8 | 13 | 406 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2338 NW.22 | CMI_NORMAL | NO | NO | NO | 862220 | 168371 | 148528 | 6039 | 1777 | 0.00047088 | 9.2784e-06 | 50.75 | 1 | 310 | Load | 28205 | Load | Tran1phOH | PETER BILICKI | 619-726-8332 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | OK - 2020
J2002.005142 | PD-02152020-00023 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6328 | 816328 | 2020-02-15 09:31 | 2020-02-15 12:48 | 196.58 | 6 | 7 | 1143.9 | 22 | WIND | 17 | JUMPER | MOORE | 207 KELLEY DR | CMI_NORMAL | NO | NO | NO | 862220 | 159301 | 102255 | 11849 | 1188 | 0.0013267 | 6.9588e-06 | 190.65 | 1 | 310 | Load | 20455 | Load | Tran1phOH | DUSTY STEJSKAL | 405-249-3863 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005154 | PD-02152020-00025 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-02-15 10:02 | 2020-02-15 11:28 | 86.12 | 1 | 1 | 74.0833 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | SE 103RD ST | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862220 | 114528 | 71274 | 11648 | 3539 | 8.5922e-05 | 1.1598e-06 | 74.0833 | 1 | 310 | Customer | 231134 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005156 |  | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4024 | 914024 | 2020-02-15 10:06 | 2020-02-15 12:57 | 171.32 | 2 | 3 | 275.9 | 11 | OVERLOAD | 1 | TRANSFORMER UG | FORT SMITH | N.-PHOENIX W. S. 16 ST | CMI_PLANNED | YES | NO | NO | 862220 | 82360 | 61281 | 4724 | 1167 | 0.00031999 | 2.3196e-06 | 137.95 | 1 | 308 | Mainline | 2446 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-15 | 2020 |  | Ark - Series 2
J2002.005157 | PD-02152020-00026 | METRO NORTH | NORTH | 8347:WILSHIRE | WILSHIRE_4721 | 834721 | 2020-02-15 10:07 | 2020-02-15 11:20 | 72.82 | 1 | 1 | 72.8167 | 28 | OTHER (DESCRIBE) | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6205 BELLE DR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862220 | 168371 | 148528 | 4624 | 927 | 8.4453e-05 | 1.1598e-06 | 72.8167 | 1 | 310 | Customer | 27417 | Load | TranOpenDelta | PETER BILICKI | 619-726-8332 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | OK - 2022
J2002.005159 | PD-02152020-00028 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2024 | 822024 | 2020-02-15 10:10 | 2020-02-15 10:48 | 37.97 | 1 | 1 | 37.9667 | 28 | OTHER (DESCRIBE) | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2338 NW.22 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862220 | 168371 | 148528 | 6039 | 1777 | 4.4034e-05 | 1.1598e-06 | 37.9667 | 1 | 310 | Customer | 28205 | Load | Tran1phOH | PETER BILICKI | 619-726-8332 | [5 empty] | Other | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | OK - 2020
J2002.005160 | PD-02152020-00027 | METRO WEST | WEST | 8150:HOBBY LOBBY | HOBBY_LOBBY_5062 | 815062 | 2020-02-15 10:11 | 2020-02-15 12:18 | 126.82 | 1 | 2 | 124.2333 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 2917 S.MAGERUS | CMI_NORMAL | NO | NO | NO | 862220 | 129015 | 116216 | 2511 | 853 | 0.00014409 | 1.1598e-06 | 124.2333 | 1 | 320 | Customer | 7160 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005164 | PD-02152020-00031 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4123 | 814123 | 2020-02-15 10:28 | 2020-02-15 14:11 | 223.48 | 1 | 1 | 54.7686 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 832 SE.68 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 159301 | 102255 | 5814 | 1323 | 6.352e-05 | 1.1598e-06 | 54.7686 | 1 | 320 | Customer | 17566 | Load | Tran1phOH | GERARDO D SOTO | 405-758-6334 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | #N/A
J2002.005166 | PD-02152020-00032 | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-02-15 10:32 | 2020-02-15 12:10 | 97.83 | 1 | 1 | 23.95 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 11300 RYAN DR | CMI_NORMAL | NO | NO | NO | 862220 | 159301 | 57046 | 4239 | 3070 | 2.7777e-05 | 1.1598e-06 | 23.95 | 1 | 310 | Load | 83329 | Load | Tran1phOH | GERARDO D SOTO | 405-758-6334 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005167 | PD-02152020-00033 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4022 | 834022 | 2020-02-15 10:37 | 2020-02-15 13:21 | 163.97 | 1 | 1 | 163.9667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 9109 SALSBURY LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 129015 | 116216 | 10846 | 1369 | 0.00019017 | 1.1598e-06 | 163.9667 | 1 | 310 | Customer | 53727 | Load | Tran1phPad | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005168 |  | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4024 | 914024 | 2020-02-15 10:39 | 2020-02-15 16:08 | 328.83 | 1 | 2 | 328.25 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 4422 S.16 | CMI_PLANNED | YES | NO | NO | 862220 | 82360 | 61281 | 4724 | 1167 | 0.0003807 | 1.1598e-06 | 328.25 | 1 | 310 | Load | 2458 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-15 | 2020 |  | Ark - Series 2
J2002.005172 | PD-02152020-00034 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6021 | 836021 | 2020-02-15 10:54 | 2020-02-15 12:41 | 106.8 | 1 | 1 | 106.8 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2621 N.BRENDA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 129015 | 116216 | 5510 | 1452 | 0.00012387 | 1.1598e-06 | 106.8 | 1 | 310 | Customer | 27887 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | #N/A
J2002.005176 | PD-02152020-00035 | NORTHWEST | ENID | 4230:THREE SANDS | THREE_SANDS_3021 | 423021 | 2020-02-15 11:03 | 2020-02-15 12:50 | 107.2 | 1 | 1 | 107.2 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | TONKAWA | 2S 2E 3S 3/4E TONK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 53606 | 37642 | 48 | 48 | 0.00012433 | 1.1598e-06 | 107.2 | 1 | 310 | Load | 2475 | Load | Tran1phOH | PATRICK LYONS | 580-395-4171 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | #N/A
J2002.005181 | PD-02152020-00036 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7029 | 817029 | 2020-02-15 11:04 | 2020-02-15 15:28 | 263.87 | 3 | 3 | 755.25 | 4 | DETERIORATION | 17 | JUMPER | OKLAHOMA CITY | NS BROOKSIDETR+SHIELDS | CMI_NORMAL | NO | NO | NO | 862220 | 159301 | 102255 | 9938 | 1756 | 0.00087594 | 3.4794e-06 | 251.75 | 1 | 310 | Tap | 9993 | Fuse | FuseOH | DUSTY STEJSKAL | 405-249-3863 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | OK - 2022
J2002.005175 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7029 | 817029 | 2020-02-15 11:04 | 2020-02-15 11:04 | 0 | 259 | 0 | 0 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | SW CORNER OF SHIELDS AND SW 89TH ST | CMI_MOMENTARY | YES | NO | NO | 862220 | 159301 | 102255 | 9938 | 1756 | 0 | 0.00030039 | 0 | 1 | 0 | Mainline | 348050 | Recloser | Rec3phElectronic | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | OK - 2022
J2002.005177 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7029 | 817029 | 2020-02-15 11:04 | 2020-02-15 11:04 | 0 | 278 | 0 | 0 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | SW CORNER OF SHIELDS AND SW 89TH ST | CMI_MOMENTARY | YES | NO | NO | 862220 | 159301 | 102255 | 9938 | 1756 | 0 | 0.00032242 | 0 | 1 | 0 | Mainline | 348050 | Recloser | Rec3phElectronic | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | OK - 2022
J2002.005178 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7029 | 817029 | 2020-02-15 11:04 | 2020-02-15 11:04 | 0 | 260 | 0 | 0 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | SW CORNER OF SHIELDS AND SW 89TH ST | CMI_MOMENTARY | YES | NO | NO | 862220 | 159301 | 102255 | 9938 | 1756 | 0 | 0.00030155 | 0 | 1 | 0 | Mainline | 348050 | Recloser | Rec3phElectronic | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | OK - 2022
J2002.005182 | PD-02152020-00038 | SOUTHERN | PAULS VALLEY | 5608:SHELL ELMORE C | SHELL ELMORE 21 | 560821 | 2020-02-15 11:30 | 2020-02-15 13:00 | 90.3 | 13 | 4 | 1149.85 | 12 | POOR CONNECTION | 50 | CONNECTOR | HENNEPIN | 2N 2W HY7 + IND.MERIDN | CMI_NORMAL | NO | NO | NO | 862220 | 77721 | 6231 | 114 | 114 | 0.0013336 | 1.5077e-05 | 88.45 | 1 | 310 | Mainline | 4002 | Recloser | Rec3phHydralic | GARRID H BROWN | 405-207-3948 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | #N/A
J2002.005198 | PD-02152020-00046 | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-02-15 11:54 | 2020-02-15 17:19 | 325.07 | 1 | 2 | 319.1333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MUSTANG | 318 S.MONOCOUPE LN | CMI_NORMAL | NO | NO | NO | 862220 | 129015 | 116216 | 18290 | 4433 | 0.00037013 | 1.1598e-06 | 319.1333 | 1 | 310 | Load | 53445 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | OK - 2022
J2002.005197 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-15 12:05 | 2020-02-15 15:10 | 185.27 | 3 | 3 | 545.55 | 4 | DETERIORATION | 12 | POLE | POCOLA | STANFIELD RD E OF HWY 112 | CMI_PLANNED | YES | NO | NO | 862220 | 82360 | 61281 | 1458 | 1240 | 0.00063273 | 3.4794e-06 | 181.85 | 1 | 308 | Load | 7815 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | Ark - Series 2
J2002.005204 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6328 | 816328 | 2020-02-15 12:22 | 2020-02-15 12:45 | 23.45 | 4 | 4 | 80.2667 | 4 | DETERIORATION | 17 | JUMPER | MOORE | 200 EBERLE DR | CMI_NORMAL | NO | NO | NO | 862220 | 159301 | 102255 | 11849 | 1188 | 9.3093e-05 | 4.6392e-06 | 20.0667 | 1 | 308 | Load | 39549 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005206 |  | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4122 | 814122 | 2020-02-15 12:30 | 2020-02-15 12:30 | 0.1 | 1274 | 0 | 127.4 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 5203 S SAGE AVE | CMI_MOMENTARY | YES | NO | NO | 862220 | 159301 | 102255 | 5814 | 1274 | 0.00014776 | 0.0014776 | 0.1 | 1 | 0 | Feeder | SAGE_4122 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-15 | 2020 |  | #N/A
J2002.005213 | PD-02152020-00049 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3629 | 833629 | 2020-02-15 12:40 | 2020-02-15 15:58 | 198.33 | 1 | 1 | 198.3333 | 22 | WIND | 17 | JUMPER | THE VILLAGE | 10812 GREYSTONE AV | CMI_NORMAL | NO | NO | NO | 862220 | 168371 | 148528 | 8791 | 1399 | 0.00023003 | 1.1598e-06 | 198.3333 | 1 | 320 | Load | 87629 | Load | Tran3phWye | JESSE PHILLER | 405-512-8086 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005217 | PD-02152020-00051 | METRO NORTH | NORTH | 8339:TULSA AVE | TULSA_AVE_3928 | 833928 | 2020-02-15 12:51 | 2020-02-15 13:46 | 55.08 | 1 | 1 | 55.0833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 5555 NW GRAND BLVD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168371 | 148528 | 7853 | 8 | 6.3885e-05 | 1.1598e-06 | 55.0833 | 1 | 310 | Load | 69193 | Load | Tran3phPadWye | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005219 | PD-02152020-00054 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4122 | 814122 | 2020-02-15 13:00 | 2020-02-15 14:40 | 99.93 | 2 | 2 | 186 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 238 SE.47 | CMI_NORMAL | NO | NO | NO | 862220 | 159301 | 102255 | 5814 | 1274 | 0.00021572 | 2.3196e-06 | 93 | 1 | 310 | Secondary | 14030 | Load | Tran1phOH | GERARDO D SOTO | 405-758-6334 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | #N/A
J2002.005221 | PD-02152020-00055 | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 22 | 570822 | 2020-02-15 13:11 | 2020-02-15 13:35 | 23.82 | 1 | 1 | 23.8167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DAVIS | 309 W.MAIN DAVIS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 77721 | 6819 | 1859 | 955 | 2.7622e-05 | 1.1598e-06 | 23.8167 | 1 | 320 | Customer | 9167 | Load | Tran1phOH | GARRID H BROWN | 405-207-3948 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | OK - 2021
J2002.005228 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5923 | 835923 | 2020-02-15 13:45 | 2020-02-15 13:45 | 0 | 1152 | 0 | 0 | 1 | CANCELLED | 57 | CANCELLED | YUKON | 4323 N CZECH HALL RD | CMI_MOMENTARY | YES | NO | NO | 862220 | 129015 | 116216 | 6438 | 1152 | 0 | 0.0013361 | 0 | 1 | 0 | Feeder | YUKON_5923 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | #N/A
J2002.005230 | PD-02152020-00059 | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2821 | 312821 | 2020-02-15 13:53 | 2020-02-15 14:54 | 60.98 | 1 | 1 | 60.9833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 2305 AUGUSTA - YORKSHIRE APTS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 74153 | 33323 | 5285 | 1153 | 7.0728e-05 | 1.1598e-06 | 60.9833 | 1 | 310 | Customer | 16478 | Load | Tran1phPad | JAMES C EVANS | 918-869-1174 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-15 | 2020 |  | #N/A
J2002.005233 | PD-02152020-00061 | NORTHEAST | MUSKOGEE | 3316:WARNER | WARNER_1621 | 331621 | 2020-02-15 14:01 | 2020-02-15 15:11 | 70.4 | 1 | 1 | 68.5833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | WARNER | 2 MI N WARNER SUB .5MI E HWY64 | CMI_NORMAL | NO | NO | NO | 862220 | 74153 | 33323 | 884 | 424 | 7.9543e-05 | 1.1598e-06 | 68.5833 | 1 | 310 | Load | 10450 | Load | Tran1phOH | NICHOLAS SELVIDGE | 918-652-1986 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | #N/A
J2002.005234 |  | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4122 | 814122 | 2020-02-15 14:06 | 2020-02-15 14:12 | 5.97 | 1 | 1 | 5.9667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 728 SE.41 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 159301 | 102255 | 5814 | 1274 | 6.9201e-06 | 1.1598e-06 | 5.9667 | 1 | 310 | Customer | 7860 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-15 | 2020 |  | #N/A
J2002.005236 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3631 | 833631 | 2020-02-15 14:28 | 2020-02-15 16:05 | 96.68 | 2 | 0 | 166.4333 | 4 | DETERIORATION | 17 | JUMPER | THE VILLAGE | 2400 W Hefner Rd | CMI_NORMAL | NO | NO | NO | 862220 | 168371 | 148528 | 8791 | 1336 | 0.00019303 | 2.3196e-06 | 83.2167 | 1 | 0 | Tap | 335088 | Fuse | FuseRiser | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | OK - 2021
J2002.005242 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9921 | 829921 | 2020-02-15 15:03 | 2020-02-15 15:10 | 7.28 | 1 | 1 | 7.2833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BETHANY | 7001 NW.16 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 129015 | 116216 | 9242 | 1637 | 8.4472e-06 | 1.1598e-06 | 7.2833 | 1 | 310 | Customer | 34735 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005243 | PD-02152020-00068 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4022 | 834022 | 2020-02-15 15:04 | 2020-02-15 16:26 | 81.73 | 1 | 1 | 81.7333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 9109 SALSBURY LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 129015 | 116216 | 10846 | 1369 | 9.4794e-05 | 1.1598e-06 | 81.7333 | 1 | 310 | Customer | 53727 | Load | Tran1phPad | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005247 | PD-02152020-00071 | METRO EAST | SHAWNEE | 7433:ROCK CREEK | ROCK_CREEK_3328 | 743328 | 2020-02-15 15:06 | 2020-02-15 16:27 | 81.48 | 1 | 2 | 76.2667 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | SHAWNEE | 3/4N GROVE SCH E.SD | CMI_NORMAL | NO | NO | NO | 862220 | 114528 | 22146 | 1806 | 769 | 8.8454e-05 | 1.1598e-06 | 76.2667 | 1 | 310 | Load | 8050 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005245 | PD-02152020-00070 | ARKANSAS | POTEAU | 3608:MULDROW | MULDROW 21 | 360821 | 2020-02-15 15:11 | 2020-02-15 15:59 | 48.07 | 1 | 1 | 35.8 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MULDROW | MULDROW OK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 82360 | 13525 | 2279 | 1228 | 4.1521e-05 | 1.1598e-06 | 35.8 | 1 | 310 | Customer | 4907 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | #N/A
J2002.005255 | PD-02152020-00074 | SOUTHERN | SULPHUR | 5708:DAVIS | DAVIS 21 | 570821 | 2020-02-15 15:28 | 2020-02-15 16:42 | 73.78 | 5 | 5 | 334.5417 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | DAVIS | 905 E MAIN | CMI_NORMAL | NO | NO | NO | 862220 | 77721 | 6819 | 1859 | 904 | 0.000388 | 5.799e-06 | 66.9083 | 1 | 310 | Load | 4362 | Load | Tran1phOH | GARRID H BROWN | 405-207-3948 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | OK - 2021
J2002.005250 | PD-02152020-00072 | NORTHEAST | SAPULPA | 3208:TIBBENS ROAD | TIBBENS_RD_824 | 320824 | 2020-02-15 15:29 | 2020-02-15 16:46 | 76.57 | 1 | 1 | 76.5667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SAPULPA | 11004 S 33RD W AVE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 74153 | 40830 | 3146 | 1403 | 8.8802e-05 | 1.1598e-06 | 76.5667 | 1 | 320 | Customer | 46455 | Load | Tran1phOH | CGI ADMIN | 918-261-6802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | OK - 2020
J2002.005259 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9921 | 829921 | 2020-02-15 15:55 | 2020-02-15 16:04 | 8.43 | 1 | 1 | 8.4333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BETHANY | 7001 NW.16 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 129015 | 116216 | 9242 | 1637 | 9.781e-06 | 1.1598e-06 | 8.4333 | 1 | 310 | Customer | 34735 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005262 | PD-02152020-00077 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1935 | 851935 | 2020-02-15 16:23 | 2020-02-15 17:14 | 51.03 | 1 | 1 | 18.1401 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 308 W.SILVERWOOD DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 114528 | 71274 | 12470 | 2171 | 2.1039e-05 | 1.1598e-06 | 18.1401 | 1 | 310 | Customer | 40465 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005263 | PD-02152020-00078 | NORTHEAST | MUSKOGEE | 3114:TENNYSON | TENNYSON_1421 | 311421 | 2020-02-15 16:24 | 2020-02-15 17:11 | 47.42 | 1 | 1 | 47.4167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 34TH + BREWER-MUSKOGEE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 74153 | 33323 | 4576 | 1104 | 5.4994e-05 | 1.1598e-06 | 47.4167 | 1 | 310 | Customer | 16737 | Load | Tran1phPad | JAMES C EVANS | 918-869-1174 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | #N/A
J2002.005264 | PD-02152020-00079 | METRO EAST | EAST | 8542:RENO | RENO_4222 | 854222 | 2020-02-15 16:27 | 2020-02-15 21:05 | 277.75 | 1 | 1 | 138.0382 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 6339 E.RENO | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 114528 | 71274 | 5218 | 1688 | 0.0001601 | 1.1598e-06 | 138.0382 | 1 | 310 | Customer | 40979 | Load | Tran1phPad | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005265 |  | METRO WEST | WEST | 8155:WILL ROGERS | WILL_ROGERS_5523 | 815523 | 2020-02-15 16:30 | 2020-02-15 16:56 | 25.98 | 3 | 2 | 77.95 | 23 | CUSTOMER EQUIPMENT | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 6412 SW 64th | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 129015 | 116216 | 45 | 3 | 9.0406e-05 | 3.4794e-06 | 25.9833 | 1 | 310 | Feeder | WILL RG_5523 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-15 | 2020 |  | #N/A
J2002.005268 | PD-02152020-00080 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2223 | 832223 | 2020-02-15 16:31 | 2020-02-15 18:27 | 115.75 | 1 | 1 | 115.75 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 3812 N.LINDA | CMI_NORMAL | NO | NO | NO | 862220 | 168371 | 148528 | 9181 | 1444 | 0.00013425 | 1.1598e-06 | 115.75 | 1 | 321 | Customer | 8132 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | OK - 2021
J2002.005271 | PD-02152020-00081 | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1024 | 311024 | 2020-02-15 16:37 | 2020-02-15 21:00 | 263.3 | 36 | 30 | 9345 | 3 | DAMAGED BY PUBLIC | 36 | CONDUCTOR PRIMARY - UG | MUSKOGEE | NORTH ST @ HIDDEN VALL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 74153 | 33323 | 2907 | 1397 | 0.010838 | 4.1753e-05 | 259.5833 | 1 | 310 | Mainline | 26282 | Fuse | FuseRiser | STEVE K HIGHFILL | 918-869-2785 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | OK - 2020
J2002.005269 |  | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1024 | 311024 | 2020-02-15 16:37 | 2020-02-15 16:37 | 0 | 1397 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MUSKOGEE | 1541 COUNTRY CLUB PLACE | CMI_MOMENTARY | YES | NO | NO | 862220 | 74153 | 33323 | 2907 | 1397 | 0 | 0.0016202 | 0 | 1 | 0 | Feeder | RIVERSIDE_1024 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-15 | 2020 |  | OK - 2020
J2002.005275 | PD-02152020-00084 | NORTHWEST | ALVA | 4707:KNOBHILL | KNOBHILL_729 | 470729 | 2020-02-15 16:45 | 2020-02-15 21:21 | 275.47 | 1 | 1 | 163.3833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | AVARD | KOCH P/L (HOPETON)-TR 15401 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 53606 | 5524 | 1742 | 429 | 0.00018949 | 1.1598e-06 | 163.3833 | 1 | 310 | Load | 90193 | Load | 0 | PATRICK LYONS | 580-395-4171 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | #N/A
J2002.005280 |  | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6024 | 836024 | 2020-02-15 17:06 | 2020-02-15 18:40 | 93.88 | 10 | 8 | 865.6667 | 4 | DETERIORATION | 12 | POLE | BETHANY | 8313 NW.36 TR | CMI_NORMAL | NO | NO | NO | 862220 | 129015 | 116216 | 5510 | 1342 | 0.001004 | 1.1598e-05 | 86.5667 | 1 | 310 | Load | 23643 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | OK - 2022
J2002.005281 |  | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6024 | 836024 | 2020-02-15 17:07 | 2020-02-15 18:40 | 92.83 | 9 | 0 | 835.5807 | 4 | DETERIORATION | 12 | POLE | BETHANY | 3700 SHANNON AV | CMI_NORMAL | NO | NO | NO | 862220 | 129015 | 116216 | 5510 | 1342 | 0.0009691 | 1.0438e-05 | 92.8423 | 1 | 0 | Load | 23645 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | OK - 2022
J2002.005286 | PD-02152020-00087 | NORTHWEST | ENID | 4153:IMO | IMO_5322 | 415322 | 2020-02-15 17:13 | 2020-02-15 18:08 | 54.7 | 1 | 1 | 54.7 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ENID | 1001 S OAKWOOD--ENID | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 53606 | 37642 | 1178 | 506 | 6.3441e-05 | 1.1598e-06 | 54.7 | 1 | 310 | Customer | 1013 | Load | Tran1phPad | WILLIAM R PETHICK | 580-278-8129 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005288 | PD-02152020-00089 | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_621 | 770621 | 2020-02-15 17:17 | 2020-02-15 18:24 | 66.9 | 1 | 1 | 66.9 | 4 | DETERIORATION | 21 | FUSE - TRANSFORMER | BRISTOW | S.W. CORNER OF 1ST + CHESTNUT | CMI_NORMAL | NO | NO | NO | 862220 | 74153 | 40830 | 3786 | 1576 | 7.759e-05 | 1.1598e-06 | 66.9 | 1 | 310 | Load | 23053 | Load | Tran3phWye | CGI ADMIN | 918-261-6802 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | OK - 2021
J2002.005289 | PD-02152020-00090 | METRO NORTH | NORTH | 8434:DEEP FORK | DEEP_FORK_3422 | 843422 | 2020-02-15 17:18 | 2020-02-15 17:56 | 37.67 | 1 | 1 | 11.6352 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1800 NE.67 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168371 | 148528 | 1229 | 730 | 1.3495e-05 | 1.1598e-06 | 11.6352 | 1 | 320 | Customer | 8139 | Load | TranOHDeltaSplitBank | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | #N/A
J2002.005294 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9921 | 829921 | 2020-02-15 17:37 | 2020-02-15 17:42 | 5.2 | 1 | 1 | 5.2 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BETHANY | 7001 NW.16 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 129015 | 116216 | 9242 | 1637 | 6.0309e-06 | 1.1598e-06 | 5.2 | 1 | 310 | Customer | 34735 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005293 | PD-02152020-00091 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5127 | 815127 | 2020-02-15 17:37 | 2020-02-15 18:50 | 73.25 | 1 | 1 | 55.2595 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2300 SW.102 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 159301 | 102255 | 13943 | 1995 | 6.409e-05 | 1.1598e-06 | 55.2595 | 1 | 310 | Customer | 62746 | Load | Tran1phPad | GERARDO D SOTO | 405-758-6334 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005298 | PD-02152020-00092 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2123 | 822123 | 2020-02-15 17:52 | 2020-02-15 18:52 | 60.17 | 1 | 1 | 60.1667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3745 NW.LIBERTY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168371 | 148528 | 9254 | 1666 | 6.9781e-05 | 1.1598e-06 | 60.1667 | 1 | 310 | Customer | 23468 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | OK - 2020
J2002.005300 | PD-02152020-00093 | NORTHWEST | ENID | 4135:SO 4TH ST | SO_4TH_ST_3524 | 413524 | 2020-02-15 17:56 | 2020-02-15 18:59 | 63.18 | 1 | 1 | 15.8667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ENID | 1401 W WABASH AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 53606 | 37642 | 3099 | 1614 | 1.8402e-05 | 1.1598e-06 | 15.8667 | 1 | 320 | Customer | 6046 | Load | TranOpenDelta | WILLIAM R PETHICK | 580-278-8129 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005305 |  | SOUTHERN | PAULS VALLEY | 5611:MAYSVILLE | MAYSVILLE 22 | 561122 | 2020-02-15 18:09 | 2020-02-15 21:08 | 178.85 | 3 | 4 | 106.2 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | MAYSVILLE | 307 3RD STREET | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862220 | 77728 | 6232 | 947 | 453 | 0.00012317 | 3.4794e-06 | 35.4 | 1 | 310 | Secondary | 4950 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | OK - 2021
J2002.005304 |  | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_924 | 910924 | 2020-02-15 18:21 | 2020-02-15 18:37 | 16.1 | 1 | 1 | 16.1 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 1701 S.FRESNO 37 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 82368 | 61287 | 5016 | 1725 | 1.8673e-05 | 1.1598e-06 | 16.1 | 1 | 310 | Customer | 9271 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | Ark - Series 3
J2002.005312 | PD-02152020-00095 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_769 | 870769 | 2020-02-15 19:05 | 2020-02-15 21:58 | 172.57 | 1 | 3 | 27.7699 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | NORMAN | 1712 Oriole Drive | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862220 | 159309 | 57047 | 11838 | 2300 | 3.2207e-05 | 1.1598e-06 | 27.7699 | 1 | 310 | Customer | 74499 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005318 | PD-02152020-00097 | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2224 | 882224 | 2020-02-15 19:27 | 2020-02-15 21:41 | 133.82 | 13 | 9 | 1397.5 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | EDMOND | .4MN S.H.#77 + CO.LN. | CMI_NORMAL | NO | NO | NO | 862220 | 168372 | 19843 | 5389 | 1853 | 0.0016208 | 1.5077e-05 | 107.5 | 1 | 310 | Mainline | 6041 | Fuse | FuseRiser | DERICK WINSETT | 405-650-6102 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005323 | PD-02152020-00102 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3062 | 933062 | 2020-02-15 20:15 | 2020-02-15 20:56 | 40.57 | 1 | 1 | 40.5667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DYER | DYER, 1 POLE N-LINE ST ON MAIN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 82368 | 61287 | 3793 | 1207 | 4.7049e-05 | 1.1598e-06 | 40.5667 | 1 | 310 | Customer | 4907 | Load | Tran1phOH | KRIS L HALMES | 479-430-9447 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-15 | 2020 |  | Ark - Series 2
J2002.005331 | PD-02152020-00105 | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_723 | 510723 | 2020-02-15 21:09 | 2020-02-15 21:51 | 41.88 | 1 | 1 | 41.8833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ARDMORE | 230 13 NW. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 77728 | 23612 | 4517 | 1217 | 4.8576e-05 | 1.1598e-06 | 41.8833 | 1 | 310 | Customer | 3087 | Load | Tran1phOH | DAVID TAYLOR | 580-574-4517 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-15 | 2020 |  | #N/A
J2002.005333 | PD-02152020-00106 | METRO WEST | EL RENO | 8921:JENSEN RD | JENSEN_ROAD_2161 | 892161 | 2020-02-15 21:55 | 2020-02-15 23:15 | 79.92 | 1 | 1 | 69.6167 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | EL RENO | 4301 N GREGORY RD | CMI_NORMAL | NO | NO | NO | 862220 | 129031 | 12801 | 3209 | 741 | 8.0741e-05 | 1.1598e-06 | 69.6167 | 1 | 310 | Load | 221882 | Load | Tran1phOH | MICHAEL T MAHEN | 405-210-6029 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005346 |  | METRO SOUTH | SOUTH CENTRAL | 8194:WESTMOORE | WESTMOORE_9429 | 819429 | 2020-02-15 23:46 | 2020-02-15 23:55 | 8.38 | 1 | 1 | 8.3833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | OAK GROVE DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 159309 | 102262 | 8106 | 1135 | 9.723e-06 | 1.1598e-06 | 8.3833 | 1 | 310 | Customer | 259618 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-15 | 2020 |  | #N/A
J2002.005352 | PD-02162020-00003 | ARKANSAS | FORT SMITH | 9126:OAK PARK | OAK_PARK_2623 | 912623 | 2020-02-16 02:17 | 2020-02-16 03:39 | 81.98 | 1 | 1 | 75.9333 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | FORT SMITH | 3409 SHORT-WILMA | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862220 | 82368 | 61287 | 2288 | 1995 | 8.8067e-05 | 1.1598e-06 | 75.9333 | 1 | 321 | Customer | 4203 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-16 | 2020 |  | Ark - Series 1
J2002.005358 | PD-02162020-00004 | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5822 | 845822 | 2020-02-16 04:12 | 2020-02-16 08:50 | 277.97 | 1 | 1 | 275.2333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | SPENCER | 4206 N.POST RD | CMI_NORMAL | NO | NO | NO | 862220 | 114534 | 71278 | 2988 | 937 | 0.00031921 | 1.1598e-06 | 275.2333 | 1 | 310 | Load | 19814 | Load | Tran1phOH | JEREMIAH D WALKER | 405-974-0464 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-16 | 2020 |  | #N/A
J2002.005404 | PD-02162020-00006 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_722 | 870722 | 2020-02-16 06:11 | 2020-02-16 11:17 | 305.93 | 6 | 4 | 1534.5 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | NORMAN | HALLBROOKE DR & HALLBROOKE CT | CMI_NORMAL | NO | NO | NO | 862220 | 159309 | 57047 | 11838 | 1582 | 0.0017797 | 6.9588e-06 | 255.75 | 1 | 310 | Load | 242507 | Load | Tran1phPad | DERICK WINSETT | 405-650-6102 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | #N/A
J2002.005371 | PD-02162020-00008 | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3723 | 913723 | 2020-02-16 07:42 | 2020-02-16 08:56 | 74.4 | 1 | 1 | 74.4 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 5900 KINKEAD AV 446 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 82368 | 61287 | 4576 | 737 | 8.6289e-05 | 1.1598e-06 | 74.4 | 1 | 310 | Customer | 64 | Load | Tran1phPad | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-16 | 2020 |  | Ark - Series 3
J2002.005372 | PD-02162020-00010 | ARKANSAS | FORT SMITH | 9104:J STREET | J_STREET_429 | 910429 | 2020-02-16 07:45 | 2020-02-16 09:41 | 115.65 | 1 | 1 | 115.65 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 17 N.6 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 82368 | 61287 | 2003 | 425 | 0.00013413 | 1.1598e-06 | 115.65 | 1 | 310 | Customer | 257 | Load | Tran3phWye | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-16 | 2020 |  | Ark - Series 2
J2002.005373 | PD-02162020-00011 | NORTHEAST | MUSKOGEE | 3326:JAMESVILLE | JAMESVILLE_2623 | 332623 | 2020-02-16 07:53 | 2020-02-16 10:13 | 140.05 | 64 | 43 | 8754.1333 | 22 | WIND | 37 | CONDUCTOR PRIMARY - OH | HASKELL | 2MW of Hwy.64 on Skelly Rd | CMI_NORMAL | NO | NO | NO | 862220 | 74156 | 33323 | 1555 | 403 | 0.010153 | 7.4227e-05 | 136.7833 | 1 | 310 | Mainline | 342810 | Fuse | FuseOH | NICHOLAS SELVIDGE | 918-652-1986 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-16 | 2020 |  | #N/A
J2002.005385 | PD-02162020-00012 | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5821 | 845821 | 2020-02-16 08:07 | 2020-02-16 09:08 | 60.92 | 1 | 1 | 60.9167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 13000 N E 82ND | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 114534 | 71278 | 2988 | 1189 | 7.0651e-05 | 1.1598e-06 | 60.9167 | 1 | 310 | Customer | 72467 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-16 | 2020 |  | OK - 2020
J2002.005392 |  | NORTHEAST | SAPULPA | 3209:BIXBY | BIXBY 29 | 320929 | 2020-02-16 08:36 | 2020-02-16 11:48 | 192.08 | 28 | 16 | 5274.7333 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | BIXBY | CABANISS + NEEDLES LITE | CMI_PLANNED | YES | NO | NO | 862220 | 74156 | 40833 | 2757 | 1444 | 0.0061176 | 3.2474e-05 | 188.3833 | 1 | 308 | Load | 40994 | Load | Tran3phWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-16 | 2020 |  | OK - 2021
J2002.005393 | PD-02162020-00016 | ARKANSAS | POTEAU | 3505:POTEAU | POTEAU_531 | 350531 | 2020-02-16 08:38 | 2020-02-16 09:06 | 28.07 | 1 | 1 | 27.0667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | POTEAU | PAUL MATHAS AVE, POTEAU | CMI_NORMAL | NO | NO | NO | 862220 | 82368 | 13527 | 2308 | 781 | 3.1392e-05 | 1.1598e-06 | 27.0667 | 1 | 310 | Customer | 14533 | Load | Tran1phOH | BRANDON K BRYAN | 479-831-3888 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-16 | 2020 |  | #N/A
J2002.005394 | PD-02162020-00017 | SOUTHERN | ARDMORE | 5108:WOLF CREEK | WOLF CREEK 22 | 510822 | 2020-02-16 08:38 | 2020-02-16 09:56 | 78 | 1 | 1 | 78 | 3 | DAMAGED BY PUBLIC | 15 | METER - SECONDARY | WILSON | CONOCO/O L GRAY RD .1S .1W | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 77728 | 23612 | 450 | 238 | 9.0464e-05 | 1.1598e-06 | 78 | 1 | 310 | Load | 198600 | Load | Tran1phOH | JUSTIN B MARSHALL | 580-221-5051 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | #N/A
J2002.005397 | PD-02162020-00021 | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_624 | 730624 | 2020-02-16 08:40 | 2020-02-16 12:46 | 245.95 | 1 | 2 | 133.3333 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | SEMINOLE | MORNING GLORY LN: LAKEWOOD EST | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862220 | 114534 | 13627 | 4074 | 1227 | 0.00015464 | 1.1598e-06 | 133.3333 | 1 | 310 | Customer | 193044 | Load | Tran1phPad | CONTRACT 1 KENS CONSTRUCTION | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | OK - 2020
J2002.005395 | PD-02162020-00018 | METRO EAST | EAST | 8692:AIR DEPOT | AIR_DEPOT_9223 | 869223 | 2020-02-16 08:41 | 2020-02-16 13:47 | 305.85 | 16 | 3 | 4544.5333 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | L16,B9 CAMBRIDGE PARK SEC 2 | CMI_NORMAL | NO | NO | NO | 862220 | 114534 | 71278 | 1906 | 1476 | 0.0052707 | 1.8557e-05 | 284.0333 | 1 | 310 | Load | 82017 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | #N/A
J2002.005396 | PD-02162020-00019 | NORTHEAST | MUSKOGEE | 3326:JAMESVILLE | JAMESVILLE_2623 | 332623 | 2020-02-16 08:45 | 2020-02-16 10:19 | 94.45 | 1 | 1 | 85.1667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | HASKELL | 2 1/10W ON SKELLY RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 74156 | 33323 | 1555 | 403 | 9.8776e-05 | 1.1598e-06 | 85.1667 | 1 | 310 | Load | 14877 | Load | Tran1phPad | JAMES C EVANS | 918-869-1174 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-16 | 2020 |  | #N/A
J2002.005398 | PD-02162020-00022 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7424 | 847424 | 2020-02-16 09:04 | 2020-02-16 09:59 | 54.63 | 1 | 1 | 54.6333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 820 NE.50 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168372 | 148529 | 6173 | 2199 | 6.3364e-05 | 1.1598e-06 | 54.6333 | 1 | 320 | Customer | 8347 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | OK - 2020
J2002.005406 |  | METRO EAST | EAST | 8685:TINKER FIELD 4 | TINKER_4_8524 | 868524 | 2020-02-16 09:32 | 2020-02-17 14:38 | 1746.22 | 5 | 0 | 8731.1107 | 28 | OTHER (DESCRIBE) | 3 | SWITCHING CUBICLE | OKLAHOMA CITY | East of Bldg 201; East of "D" Av | CMI_PLANNED | YES | NO | NO | 862220 | 114534 | 71278 | 184 | 21 | 0.010126 | 5.799e-06 | 1746.2222 | 1 | 0 | Mainline | 344762 | Switch | 0 | Crew | [6 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | #N/A
J2002.005409 | PD-02162020-00025 | METRO SOUTH | SOUTH | 8726:NOBLE | NOBLE_2621 | 872621 | 2020-02-16 09:44 | 2020-02-16 15:39 | 354.57 | 1 | 1 | 354.5667 | 4 | DETERIORATION | 50 | CONNECTOR | NOBLE | S-CEDAR ON 3RD | CMI_NORMAL | NO | NO | NO | 862220 | 159309 | 57047 | 2969 | 1448 | 0.00041123 | 1.1598e-06 | 354.5667 | 1 | 320 | Customer | 31569 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | #N/A
J2002.005414 | PD-02162020-00028 | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5229 | 835229 | 2020-02-16 09:58 | 2020-02-16 15:54 | 356.15 | 1 | 1 | 356.15 | 12 | POOR CONNECTION | 50 | CONNECTOR | OKLAHOMA CITY | 2829 NW.117 | CMI_NORMAL | NO | NO | NO | 862220 | 168372 | 148529 | 6521 | 1290 | 0.00041306 | 1.1598e-06 | 356.15 | 1 | 310 | Customer | 28306 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | #N/A
J2002.005417 |  | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1022 | 311022 | 2020-02-16 10:19 | 2020-02-16 10:19 | 0 | 1155 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | MUSKOGEE | 1541 COUNTRY CLUB PLACE | CMI_MOMENTARY | YES | NO | NO | 862220 | 74156 | 33323 | 2907 | 1093 | 0 | 0.0013396 | 0 | 1 | 0 | Feeder | RIVERSIDE_1022 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-16 | 2020 |  | #N/A
J2002.005420 | PD-02162020-00030 | SOUTHERN | HEALDTON | 5306:COUNTY LINE | COUNTY LINE 22 | 530622 | 2020-02-16 10:39 | 2020-02-16 15:47 | 307.97 | 1 | 2 | 139.8333 | 12 | POOR CONNECTION | 27 | CUTOUT | HENNEPIN | HENNEPIN OK | CMI_NORMAL | NO | NO | NO | 862220 | 77728 | 6811 | 757 | 415 | 0.00016218 | 1.1598e-06 | 139.8333 | 1 | 310 | Load | 2667 | Load | Tran1phOH | CHRIS CLOSE | 405-238-0419 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-16 | 2020 |  | #N/A
J2002.005426 | PD-02162020-00034 | ARKANSAS | POTEAU | 3508:SPIRO COAL | SPIRO COAL 21 | 350821 | 2020-02-16 11:05 | 2020-02-16 11:55 | 50.35 | 1 | 2 | 49.9833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | SPIRO | MAYO LOCK+DAM RD ES | CMI_NORMAL | NO | NO | NO | 862220 | 82368 | 13527 | 380 | 377 | 5.7971e-05 | 1.1598e-06 | 49.9833 | 1 | 310 | Customer | 15343 | Load | Tran1phOH | BRANDON K BRYAN | 479-831-3888 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-16 | 2020 |  | #N/A
J2002.005425 | PD-02162020-00033 | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1022 | 311022 | 2020-02-16 11:13 | 2020-02-16 11:52 | 39.48 | 1 | 1 | 36.8167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | MUSKOGEE | 2312 MICHAEL RD | CMI_NORMAL | NO | NO | NO | 862220 | 74156 | 33323 | 2907 | 1093 | 4.27e-05 | 1.1598e-06 | 36.8167 | 1 | 310 | Customer | 12350 | Load | Tran1phOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-16 | 2020 |  | #N/A
J2002.005429 | PD-02162020-00037 | METRO SOUTH | SOUTH | 8708:CEDAR LANE | CEDAR_LANE_823 | 870823 | 2020-02-16 11:32 | 2020-02-16 13:57 | 144.58 | 1 | 1 | 144.5833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | 2026 CHEROKEE LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 159309 | 57047 | 6776 | 2378 | 0.00016769 | 1.1598e-06 | 144.5833 | 1 | 310 | Customer | 33730 | Load | Tran1phOH | ROBERT HALL | 405-757-9640 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | #N/A
J2002.005431 | PD-02162020-00036 | ARKANSAS | POTEAU | 3509:PANAMA | PANAMA 42 | 350942 | 2020-02-16 11:49 | 2020-02-16 12:36 | 46.83 | 1 | 1 | 46.8333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | BOKOSHE | 5BW PO 1BS BW NS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 82368 | 13527 | 1392 | 336 | 5.4317e-05 | 1.1598e-06 | 46.8333 | 1 | 310 | Customer | 10975 | Load | Tran1phOH | BRANDON K BRYAN | 479-831-3888 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-16 | 2020 |  | #N/A
J2002.005436 | PD-02162020-00042 | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-02-16 12:29 | 2020-02-16 13:23 | 54.42 | 5 | 5 | 256.1667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ADA | 901 HOWARD | CMI_NORMAL | NO | NO | NO | 862220 | 77728 | 11525 | 2519 | 1090 | 0.0002971 | 5.799e-06 | 51.2333 | 1 | 310 | Secondary | 10784 | Load | Tran1phOH | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-16 | 2020 |  | #N/A
J2002.005434 |  | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-02-16 12:29 | 2020-02-16 12:29 | 0 | 1090 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ADA | 1806 A ST | CMI_MOMENTARY | YES | NO | NO | 862220 | 77728 | 11525 | 2519 | 1090 | 0 | 0.0012642 | 0 | 1 | 0 | Feeder | VALLEY_VIEW_623 | Recloser | 0 | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-16 | 2020 |  | #N/A
J2002.005437 | PD-02162020-00043 | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4031 | 914031 | 2020-02-16 12:45 | 2020-02-16 13:43 | 57.78 | 1 | 1 | 57.7833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 8715 KENDALL CT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 82368 | 61287 | 4724 | 1083 | 6.7017e-05 | 1.1598e-06 | 57.7833 | 1 | 310 | Customer | 2320 | Load | Tran1phPad | ALLEN SNOWDEN | 479-462-8381 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-16 | 2020 |  | #N/A
J2002.005455 | PD-02162020-00045 | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_721 | 510721 | 2020-02-16 14:00 | 2020-02-16 16:06 | 126.03 | 67 | 55 | 8332.5667 | 5 | ELECTRICAL TRACKING | 23 | FUSE - PRIMARY | ARDMORE | ALY N 7TH ON O NW | CMI_NORMAL | NO | NO | NO | 862220 | 77728 | 23612 | 4517 | 684 | 0.0096641 | 7.7706e-05 | 124.3667 | 1 | 310 | Mainline | 5415 | Fuse | FuseOH | JUSTIN B MARSHALL | 580-221-5051 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-16 | 2020 |  | #N/A
J2002.005459 |  | METRO NORTH | NORTH | 8464:BRYANT | BRYANT_6422 | 846422 | 2020-02-16 14:29 | 2020-02-16 15:44 | 74.6 | 3 | 1 | 51 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | 8320 N. Eastern | CMI_NORMAL | NO | NO | NO | 862220 | 168372 | 148529 | 1893 | 629 | 5.915e-05 | 3.4794e-06 | 17 | 1 | 308 | Load | 326883 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | #N/A
J2002.005461 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6121 | 836121 | 2020-02-16 14:33 | 2020-02-16 14:33 | 0.03 | 1638 | 0 | 54.6 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 1121 NW 30TH ST | CMI_MOMENTARY | YES | NO | NO | 862220 | 168372 | 148529 | 11118 | 1638 | 6.3325e-05 | 0.0018997 | 0.033333 | 1 | 0 | Feeder | WESTR AV_6121 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-16 | 2020 |  | OK - 2021
J2002.005463 | PD-02162020-00048 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6121 | 836121 | 2020-02-16 14:42 | 2020-02-16 16:28 | 106.1 | 1 | 1 | 106.1 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1115 NW.34 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168372 | 148529 | 11118 | 1638 | 0.00012305 | 1.1598e-06 | 106.1 | 1 | 320 | Customer | 1925 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | OK - 2021
J2002.005467 | PD-02162020-00051 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1924 | 851924 | 2020-02-16 15:01 | 2020-02-16 15:38 | 36.63 | 1 | 1 | 17.1011 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SPENCER | 2912 PAXTON PL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 114534 | 71278 | 12470 | 1609 | 1.9834e-05 | 1.1598e-06 | 17.1011 | 1 | 320 | Customer | 72404 | Load | Tran1phPad | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | #N/A
J2002.005473 | PD-02162020-00055 | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_621 | 770621 | 2020-02-16 15:26 | 2020-02-16 16:47 | 80.97 | 1 | 1 | 80.9667 | 12 | POOR CONNECTION | 50 | CONNECTOR | BRISTOW | 1407 S.OAK | CMI_NORMAL | NO | NO | NO | 862220 | 74156 | 40833 | 3786 | 1576 | 9.3905e-05 | 1.1598e-06 | 80.9667 | 1 | 320 | Customer | 42453 | Load | Tran1phOH | CGI ADMIN | 918-261-6802 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-16 | 2020 |  | OK - 2021
J2002.005476 | PD-02162020-00057 | NORTHWEST | ALVA | 4707:KNOBHILL | KNOBHILL_729 | 470729 | 2020-02-16 15:33 | 2020-02-16 16:17 | 43.67 | 1 | 1 | 43.6667 | 23 | CUSTOMER EQUIPMENT | 23 | FUSE - PRIMARY | AVARD | KOCH P/L (HOPETON)-TR 15401 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 53605 | 5522 | 1741 | 429 | 5.0644e-05 | 1.1598e-06 | 43.6667 | 1 | 310 | Load | 90193 | Load | 0 | PATRICK LYONS | 580-395-4171 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-16 | 2020 |  | #N/A
J2002.005479 |  | ARKANSAS | POTEAU | 3509:PANAMA | PANAMA 21 | 350921 | 2020-02-16 15:42 | 2020-02-16 15:42 | 0 | 315 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | 0 | 24068 OK-31 | CMI_MOMENTARY | YES | NO | NO | 862220 | 82368 | 13527 | 1392 | 822 | 0 | 0.00036534 | 0 | 1 | 0 | Mainline | 401900 | Recloser | Rec3phElectronic | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-16 | 2020 |  | #N/A
J2002.005481 | PD-02162020-00059 | METRO WEST | WEST | 8150:HOBBY LOBBY | HOBBY_LOBBY_5061 | 815061 | 2020-02-16 16:01 | 2020-02-16 17:57 | 116.42 | 1 | 2 | 113.3833 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 8612 SW 36TH ST | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862220 | 129031 | 116230 | 2512 | 1656 | 0.0001315 | 1.1598e-06 | 113.3833 | 1 | 320 | Customer | 364113 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | #N/A
J2002.005480 |  | NORTHWEST | ENID | 4353:OTTER | OTTER_5341 | 435341 | 2020-02-16 16:01 | 2020-02-16 16:02 | 0.12 | 1 | 0 | 0.11667 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | 0 | 7248 HWY 74 | CMI_MOMENTARY | YES | NO | NO | 862220 | 53605 | 37643 | 960 | 792 | 1.3531e-07 | 1.1598e-06 | 0.11667 | 1 | 0 | Tap | 381906 | Recloser | Rec3phElectronic | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-16 | 2020 |  | OK - 2021
J2002.005486 | PD-02162020-00066 | NORTHWEST | ENID | 4353:OTTER | OTTER_5341 | 435341 | 2020-02-16 16:25 | 2020-02-16 17:42 | 77.08 | 1 | 1 | 77.0833 | 28 | OTHER (DESCRIBE) | 23 | FUSE - PRIMARY | GARBER | 1S,1/E,1/8 N GARBER Y | CMI_NORMAL | NO | NO | NO | 862220 | 53605 | 37643 | 960 | 792 | 8.9401e-05 | 1.1598e-06 | 77.0833 | 1 | 310 | Load | 225795 | Load | 0 | WILLIAM R PETHICK | 580-278-8129 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | OK - 2021
J2002.005487 |  | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-02-16 16:27 | 2020-02-16 16:34 | 6.88 | 1 | 1 | 6.8833 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | ADA | 1600 ARLINGTON BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 77728 | 11525 | 2519 | 1090 | 7.9833e-06 | 1.1598e-06 | 6.8833 | 1 | 310 | Customer | 12134 | Load | TranPad3phDelta | [7 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-16 | 2020 |  | #N/A
J2002.005492 | PD-02162020-00079 | METRO NORTH | GUTHRIE | 8807:CRESCENT | CRESCENT_723 | 880723 | 2020-02-16 17:37 | 2020-02-16 19:08 | 91.07 | 1 | 1 | 85.7667 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | CIMARRON CITY | 1/3MS-NILES LAKE ON HWY 74 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862220 | 168372 | 19843 | 1768 | 894 | 9.9472e-05 | 1.1598e-06 | 85.7667 | 1 | 310 | Load | 79029 | Load | Tran1phOH | KELLEY D WATSON | 405-763-8148 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | #N/A
J2002.005493 | PD-02162020-00080 | METRO NORTH | NORTH | 8220:MAY AVE | MAY_AVE_2023 | 822023 | 2020-02-16 17:38 | 2020-02-16 17:57 | 18.65 | 1 | 1 | 18.65 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3112 NW.25 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168372 | 148529 | 6039 | 1028 | 2.163e-05 | 1.1598e-06 | 18.65 | 1 | 310 | Customer | 2855 | Load | Tran1phOH | MONTY WISELEY | 405-471-2592 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-16 | 2020 |  | OK - 2022
J2002.005500 |  | METRO EAST | EAST | 8542:RENO | RENO_4224 | 854224 | 2020-02-16 19:21 | 2020-02-16 19:27 | 6.2 | 1 | 1 | 6.2 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3344 NE.11 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 114534 | 71278 | 5218 | 1223 | 7.1907e-06 | 1.1598e-06 | 6.2 | 1 | 310 | Customer | 14073 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | OK - 2022
J2002.005505 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2222 | 852222 | 2020-02-16 19:55 | 2020-02-16 20:10 | 15.17 | 1 | 1 | 15.1667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | HARRAH | RENO AND LEGACY CROSSING | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 114534 | 71278 | 11649 | 2220 | 1.759e-05 | 1.1598e-06 | 15.1667 | 1 | 310 | Customer | 386617 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | #N/A
J2002.005507 | PD-02162020-00090 | METRO WEST | WEST | 8222:CZECH HALL | CZECH_HALL_2223 | 822223 | 2020-02-16 20:25 | 2020-02-17 02:42 | 376.83 | 1 | 1 | 371.1833 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | YUKON | 212 KINGS CANYON RD | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862220 | 129031 | 116230 | 8615 | 1176 | 0.0004305 | 1.1598e-06 | 371.1833 | 1 | 310 | Customer | 65208 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | #N/A
J2002.005509 | PD-02162020-00093 | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_626 | 550626 | 2020-02-16 20:44 | 2020-02-17 09:06 | 742.35 | 1 | 1 | 742.35 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DURANT | 1902 W MISSISSIPPI | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 77728 | 15524 | 6752 | 1006 | 0.00086098 | 1.1598e-06 | 742.35 | 1 | 310 | Customer | 15628 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | #N/A
J2002.005510 | PD-02162020-00094 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_871 | 830871 | 2020-02-16 20:53 | 2020-02-16 22:05 | 71.52 | 1 | 1 | 71.5167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | Viento Dr S of NW 182nd in Valencia II | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168372 | 148529 | 19430 | 4256 | 8.2945e-05 | 1.1598e-06 | 71.5167 | 1 | 320 | Customer | 250605 | Load | Tran1phPad | PETER BILICKI | 619-726-8332 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | OK - 2021
J2002.005512 |  | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2229 | 852229 | 2020-02-16 21:27 | 2020-02-16 22:12 | 44.92 | 1 | 1 | 44.9167 | 1 | CANCELLED | 57 | CANCELLED | HARRAH | 5/8MS NE 23RD 900 W DOBBS RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 114534 | 71278 | 11649 | 1391 | 5.2094e-05 | 1.1598e-06 | 44.9167 | 1 | 310 | Load | 13028 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | #N/A
J2002.005516 | PD-02162020-00096 | METRO WEST | WEST | 8359:YUKON | YUKON_5923 | 835923 | 2020-02-16 21:37 | 2020-02-17 05:25 | 468.08 | 32 | 15 | 4486.6667 | 5 | ELECTRICAL TRACKING | 1 | TRANSFORMER UG | YUKON | 1105 First Place Blvd | CMI_NORMAL | NO | NO | NO | 862220 | 129031 | 116230 | 6438 | 1152 | 0.0052036 | 3.7113e-05 | 140.2083 | 1 | 310 | Mainline | 385948 | Fuse | FuseOH | JESSE PHILLER | 405-512-8086 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-16 | 2020 |  | #N/A
J2002.005521 |  | ARKANSAS | FORT SMITH | 9112:BELLE AVE | BELLE_AVE_1223 | 911223 | 2020-02-16 21:53 | 2020-02-16 21:59 | 6.4 | 1 | 1 | 6.4 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 1322 N.ALBERTPIKE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 82368 | 61287 | 6614 | 1772 | 7.4227e-06 | 1.1598e-06 | 6.4 | 1 | 310 | Customer | 14376 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-16 | 2020 |  | Ark - Series 1
J2002.005527 | PD-02162020-00104 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5132 | 815132 | 2020-02-16 23:09 | 2020-02-16 23:55 | 45.65 | 1 | 1 | 22.0286 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2508 FRONTAGE RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 159309 | 102262 | 13944 | 2002 | 2.5549e-05 | 1.1598e-06 | 22.0286 | 1 | 320 | Customer | 46801 | Load | Tran1phPad | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-16 | 2020 |  | #N/A
J2002.005530 |  | METRO WEST | WEST | 8359:YUKON | YUKON_5923 | 835923 | 2020-02-16 23:38 | 2020-02-16 23:51 | 12.95 | 16 | 0 | 74.6667 | 1 | CANCELLED | 57 | CANCELLED | YUKON | 1105 First Place Blvd | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 129031 | 116230 | 6438 | 1152 | 8.6598e-05 | 1.8557e-05 | 4.6667 | 1 | 0 | Mainline | 385948 | Fuse | FuseOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-16 | 2020 |  | #N/A
J2002.005546 | PD-02172020-00004 | METRO EAST | SEMINOLE | 7512:CROMWELL | CROMWELL 47 | 751247 | 2020-02-17 04:06 | 2020-02-17 09:22 | 315.65 | 1 | 1 | 306.3333 | 4 | DETERIORATION | 8 | SPLICE - UG | CROMWELL | N CROMWELL | CMI_NORMAL | NO | NO | NO | 862220 | 114534 | 13627 | 310 | 310 | 0.00035528 | 1.1598e-06 | 306.3333 | 1 | 310 | Customer | 6945 | Load | Tran1phOH | JEREMIAH D WALKER | 405-974-0464 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005554 | PD-02172020-00006 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7429 | 847429 | 2020-02-17 06:10 | 2020-02-17 09:38 | 207.83 | 1 | 3 | 207.8333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2114 HARDEN DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168372 | 148529 | 6173 | 682 | 0.00024104 | 1.1598e-06 | 207.8333 | 1 | 310 | Customer | 911 | Load | Tran1phOH | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2022
J2002.005555 | PD-02172020-00007 | METRO NORTH | NORTH | 8536:WASHINGTON PAR | WASHINGTON_PA_3621 | 853621 | 2020-02-17 06:13 | 2020-02-17 09:50 | 216.68 | 1 | 1 | 216.6833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 1720 NE 23RD, OKC | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168372 | 148529 | 5936 | 2174 | 0.00025131 | 1.1598e-06 | 216.6833 | 1 | 310 | Customer | 404703 | Load | Tran3phWye | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2022
J2002.005560 | PD-02172020-00012 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_530 | 510530 | 2020-02-17 07:03 | 2020-02-17 08:19 | 75.6 | 1 | 1 | 75.6 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ARDMORE | E BROADWAY + "A"ST NE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 77728 | 23612 | 4780 | 601 | 8.7681e-05 | 1.1598e-06 | 75.6 | 1 | 310 | Customer | 74 | Load | Tran1phOH | JAMES WAYNE TOW | 580-768-4227 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005561 |  | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5223 | 835223 | 2020-02-17 07:06 | 2020-02-17 11:22 | 256.03 | 395 | 205 | 74322.2688 | 3 | DAMAGED BY PUBLIC | 12 | POLE | OKLAHOMA CITY | 4600 W MEMORIAL RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168372 | 148529 | 6521 | 868 | 0.086199 | 0.00045812 | 188.1576 | 1 | 310 | Mainline | 107423 | Switch | SwitchRiser | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005563 | PD-02172020-00003 | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5223 | 835223 | 2020-02-17 07:07 | 2020-02-17 10:46 | 219.08 | 1 | 3 | 187.6333 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 0 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 0 | 0 | 0 | 0 | 0.00021762 | 1.1598e-06 | 187.6333 | 1 | 310 | Customer |  | 0 | 0 | TOMMY D ROBERTSON | 405-696-6476 |  |  |  |  | 06/10/2020 note from burchamc. Reference J2002.005563 in iDashboard report OSI_Job_Detail_Viewer. Used meter # in SAP to identify transformer and/or circuit number. Emailed Brent Miller with blank transformer and circuit #'s. Manually completed blank Job Region, Job Area, etc. | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005564 |  | METRO WEST | WEST | 8150:HOBBY LOBBY | HOBBY_LOBBY_5062 | 815062 | 2020-02-17 07:17 | 2020-02-17 09:14 | 116.47 | 1 | 0 | 60.35 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 2000 S MERIDIAN | CMI_PLANNED | YES | NO | NO | 862220 | 129031 | 116230 | 2512 | 854 | 6.9994e-05 | 1.1598e-06 | 60.35 | 1 | 0 | Load | 74363 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005567 | PD-02172020-00015 | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6221 | 866221 | 2020-02-17 07:27 | 2020-02-17 09:10 | 102.57 | 1 | 1 | 100.7833 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | MIDWEST CITY | 9225 SE.15 | CMI_NORMAL | NO | NO | NO | 862220 | 114534 | 71278 | 7214 | 1294 | 0.00011689 | 1.1598e-06 | 100.7833 | 1 | 310 | Load | 2808 | Load | Tran1phOH | ADAM CLARK | 580-310-8924 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005570 |  | NORTHEAST | MUSKOGEE | 3128:HANCOCK | HANCOCK_2821 | 312821 | 2020-02-17 07:34 | 2020-02-17 08:05 | 31.5 | 1 | 1 | 31.5 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 3300 E.HANCOCK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 74156 | 33323 | 5285 | 1153 | 3.6534e-05 | 1.1598e-06 | 31.5 | 1 | 310 | Customer | 15537 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-17 | 2020 |  | #N/A
J2002.005574 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-02-17 07:58 | 2020-02-17 08:34 | 35.57 | 1 | 2 | 29.7841 | 28 | OTHER (DESCRIBE) | 31 | CONDUCTOR SERVICE - OH | CHARLESTON | 26510 HWY 22 | CMI_PLANNED | YES | NO | NO | 862220 | 82368 | 61287 | 2331 | 2129 | 3.4544e-05 | 1.1598e-06 | 29.7841 | 1 | 310 | Load | 419332 | Load | Tran1phOH | Crew | [6 empty] | Other | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | Ark - Series 2
J2002.005577 | PD-02172020-00046 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-02-17 08:04 | 2020-02-17 10:26 | 142.13 | 1 | 1 | 131.6 | 4 | DETERIORATION | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 2027 NW.16 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862220 | 168372 | 148529 | 11118 | 2056 | 0.00015263 | 1.1598e-06 | 131.6 | 1 | 321 | Customer | 15038 | Load | Tran1phOH | REX R WILSON | 405-535-4507 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2021
J2002.005582 |  | ARKANSAS | POTEAU | 3608:MULDROW | MULDROW 21 | 360821 | 2020-02-17 08:25 | 2020-02-17 13:34 | 309.07 | 2 | 2 | 618.1333 | 28 | OTHER (DESCRIBE) | 15 | METER - SECONDARY | MULDROW | 303 E.BROADWAY | CMI_PLANNED | YES | NO | NO | 862220 | 82368 | 13527 | 2280 | 1229 | 0.00071691 | 2.3196e-06 | 309.0667 | 1 | 310 | Secondary | 4836 | Load | TranOpenDelta | [7 empty] | Other | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005587 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-17 08:40 | 2020-02-17 10:24 | 103.65 | 99 | 3 | 7206.017 | 28 | OTHER (DESCRIBE) | 2 | TRANSFORMER OH | LAMAR | CABIN CK & CUMBERLAND | CMI_PLANNED | YES | NO | NO | 862220 | 82368 | 7554 | 731 | 0 | 0.0083575 | 0.00011482 | 72.788 | 1 | 310 | Mainline | 177550 | Fuse | FuseOH | Crew | [6 empty] | Other | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005590 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-17 08:46 | 2020-02-17 13:06 | 260.42 | 3 | 1 | 812.05 | 4 | DETERIORATION | 28 | CROSSARM | STONE HILL | 1/4E BLOOMER ON HWY 22 | CMI_PLANNED | YES | NO | NO | 862220 | 82368 | 61287 | 962 | 491 | 0.00094181 | 3.4794e-06 | 270.6833 | 1 | 308 | Tap | 7251 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-17 | 2020 |  | Ark - Series 2
J2002.005593 | PD-02172020-00075 | METRO EAST | SHAWNEE | 7409:MCLOUD | MCLOUD_922 | 740922 | 2020-02-17 08:50 | 2020-02-17 09:55 | 65.3 | 1 | 1 | 65.3 | 22 | WIND | 23 | FUSE - PRIMARY | MCLOUD | mcloud public schools baseball field | CMI_NORMAL | NO | NO | NO | 862220 | 114534 | 22147 | 2036 | 1213 | 7.5735e-05 | 1.1598e-06 | 65.3 | 1 | 320 | Load | 356629 | Load | Tran3phPadWye | BRYAN K TATUM | 405-659-0746 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | OK - 2021
J2002.005594 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-17 08:50 | 2020-02-17 12:18 | 207.65 | 3 | 0 | 622.9566 | 4 | DETERIORATION | 2 | TRANSFORMER OH | LAMAR | LAMAR AR | CMI_PLANNED | YES | NO | NO | 862220 | 82368 | 7554 | 731 | 0 | 0.0007225 | 3.4794e-06 | 207.6522 | 1 | 0 | Load | 596 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005598 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-17 08:56 | 2020-02-17 09:19 | 23.38 | 4 | 5 | 87.6197 | 11 | OVERLOAD | 2 | TRANSFORMER OH | LAMAR | 100 FT S OF CUMBERLAND ST ON CABIN CREEK AV | CMI_PLANNED | YES | NO | NO | 862220 | 82368 | 7554 | 731 | 0 | 0.00010162 | 4.6392e-06 | 21.9049 | 1 | 310 | Load | 966 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005605 |  | METRO EAST | EAST | 8685:TINKER FIELD 4 | TINKER_4_8531 | 868531 | 2020-02-17 09:18 | 2020-02-17 10:31 | 73.05 | 1 | 0 | 73.0641 | 23 | CUSTOMER EQUIPMENT | 1 | TRANSFORMER UG | OKLAHOMA CITY | East side of bldg 280 | CMI_PLANNED | YES | NO | NO | 862220 | 114534 | 71278 | 184 | 72 | 8.474e-05 | 1.1598e-06 | 73.0641 | 1 | 0 | Load | 344869 | Load | Tran3phPadWye | Crew | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005609 | PD-02172020-00105 | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-02-17 09:21 | 2020-02-17 10:33 | 72.2 | 1 | 1 | 65.7 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | TISHOMINGO | S BULLET PRAIRIE RD BTW HWY2 AND S ROCK CREEK RD | CMI_NORMAL | NO | NO | NO | 862220 | 77728 | 7204 | 2191 | 1672 | 7.6199e-05 | 1.1598e-06 | 65.7 | 1 | 310 | Load | 26157 | Load | Tran1phOH | DAVID TAYLOR | 580-574-4517 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005625 | PD-02172020-00128 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3724 | 833724 | 2020-02-17 09:25 | 2020-02-17 10:17 | 52.18 | 3 | 4 | 149.95 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 6914 N CLASSEN BL | CMI_NORMAL | NO | NO | NO | 862220 | 168372 | 148529 | 5769 | 303 | 0.00017391 | 3.4794e-06 | 49.9833 | 1 | 310 | Secondary | 85031 | Load | TranOpenDelta | KIRK REILLEY | 405-550-3062 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005617 | PD-02172020-00115 | METRO EAST | SHAWNEE | 7432:ST GREGORY | ST_GREGORY_3231 | 743231 | 2020-02-17 09:33 | 2020-02-17 14:36 | 303.35 | 1 | 2 | 293.0167 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | SHAWNEE | 2202 Air port Dr | CMI_NORMAL | NO | NO | NO | 862220 | 114534 | 22147 | 4101 | 1209 | 0.00033984 | 1.1598e-06 | 293.0167 | 1 | 310 | Load | 399473 | Load | Tran3phWye | JEREMIAH D WALKER | 405-974-0464 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005618 | PD-02172020-00125 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1522 | 811522 | 2020-02-17 09:34 | 2020-02-17 10:21 | 47.42 | 1 | 1 | 50.4918 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 2439 SW.28 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 159309 | 102262 | 6073 | 1947 | 5.856e-05 | 1.1598e-06 | 50.4918 | 1 | 310 | Customer | 6175 | Load | Tran1phOH | GERARDO D SOTO | 405-758-6334 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | OK - 2022
J2002.005619 |  | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1421 | 911421 | 2020-02-17 09:35 | 2020-02-17 10:52 | 77.02 | 2 | 0 | 153.9739 | 4 | DETERIORATION | 1 | TRANSFORMER UG | FORT SMITH | 3700 Kelley Hwy | CMI_PLANNED | YES | NO | NO | 862220 | 82368 | 61287 | 4743 | 1752 | 0.00017858 | 2.3196e-06 | 76.9869 | 1 | 0 | Load | 412864 | Load | Tran3phPadWye | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-17 | 2020 |  | Ark - Series 1
J2002.005621 | PD-02172020-00130 | NORTHEAST | SAPULPA | 7632:OAK GROVE | OAK_GROVE_3221 | 763221 | 2020-02-17 09:36 | 2020-02-17 13:09 | 212.82 | 1 | 1 | 115.8667 | 13 | PREMATURE FAILURE | 21 | FUSE - TRANSFORMER | DRUMRIGHT | 1/4W OLD SHAMROCK HWY & 131, 660'S | CMI_NORMAL | NO | NO | NO | 862220 | 74156 | 40833 | 1021 | 1021 | 0.00013438 | 1.1598e-06 | 115.8667 | 1 | 310 | Load | 208067 | Load | Tran3phWye | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | OK - 2021
J2002.005627 | PD-02172020-00129 | SOUTHERN | ARDMORE | 5109:ARDMORE WEST | ARDMORE_WEST_931 | 510931 | 2020-02-17 09:45 | 2020-02-17 18:51 | 545.72 | 1 | 2 | 7.0333 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | ARDMORE | PLAINVIEW SCHOOL BB PARK | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862220 | 77728 | 23612 | 1318 | 702 | 8.1572e-06 | 1.1598e-06 | 7.0333 | 1 | 320 | Load | 31881 | Load | Tran1phOH | CHRIS CLOSE | 405-238-0419 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005632 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7029 | 817029 | 2020-02-17 09:51 | 2020-02-17 10:50 | 59.22 | 12 | 10 | 627 | 4 | DETERIORATION | 2 | TRANSFORMER OH | MOORE | 1025 NW.28 | CMI_PLANNED | YES | NO | NO | 862220 | 159309 | 102262 | 9938 | 1756 | 0.00072719 | 1.3918e-05 | 52.25 | 1 | 310 | Load | 31061 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2022
J2002.005636 | PD-02172020-00139 | SOUTHERN | SULPHUR | 5705:SULPHUR | SULPHUR_531 | 570531 | 2020-02-17 09:55 | 2020-02-17 12:26 | 151.4 | 1 | 1 | 151.4 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | SULPHUR | Sulphur Golf Course | CMI_NORMAL | NO | NO | NO | 862220 | 77728 | 6820 | 3636 | 602 | 0.00017559 | 1.1598e-06 | 151.4 | 1 | 310 | Customer | 384590 | Load | Tran1phOH | CHAD A DOTSON | 405-488-5658 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005638 |  | NORTHEAST | MUSKOGEE | 3321:ROSS LAKE | ROSS_LAKE_2129 | 332129 | 2020-02-17 09:59 | 2020-02-17 10:15 | 16.08 | 1 | 1 | 16.08 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | FORT GIBSON | FT GIBSON,203 GLAD STR. | CMI_PLANNED | YES | NO | NO | 862220 | 74156 | 33323 | 3339 | 943 | 1.8649e-05 | 1.1598e-06 | 16.08 | 1 | 310 | Customer | 13622 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-17 | 2020 |  | #N/A
J2002.005640 | PD-02172020-00157 | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1621 | 581621 | 2020-02-17 10:01 | 2020-02-17 11:16 | 74.7 | 1 | 1 | 69.6833 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ADA | 902 W.4 | CMI_NORMAL | NO | NO | NO | 862220 | 77728 | 11525 | 3466 | 1812 | 8.0819e-05 | 1.1598e-06 | 69.6833 | 1 | 310 | Load | 10579 | Load | Tran1phOH | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005644 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1521 | 921521 | 2020-02-17 10:06 | 2020-02-17 15:06 | 299.47 | 1 | 2 | 234.0142 | 4 | DETERIORATION | 12 | POLE | STONE HILL | STONE HILL | CMI_PLANNED | YES | NO | NO | 862220 | 82368 | 61287 | 962 | 491 | 0.00027141 | 1.1598e-06 | 234.0142 | 1 | 310 | Load | 13589 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-17 | 2020 |  | Ark - Series 2
J2002.005645 |  | SOUTHERN | PAULS VALLEY | 5619:RUSH CREEK | RUSH_CREEK_1921 | 561921 | 2020-02-17 10:06 | 2020-02-17 11:18 | 71.42 | 1 | 1 | 69.5 | 4 | DETERIORATION | 12 | POLE | PAULS VALLEY | 408 S MILDRED | CMI_PLANNED | YES | NO | NO | 862220 | 77728 | 6232 | 2078 | 827 | 8.0606e-05 | 1.1598e-06 | 69.5 | 1 | 308 | Load | 3373 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005647 | PD-02172020-00155 | NORTHWEST | ALVA | 4707:KNOBHILL | KNOBHILL_729 | 470729 | 2020-02-17 10:09 | 2020-02-17 12:38 | 148.9 | 1 | 1 | 128.3167 | 28 | OTHER (DESCRIBE) | 23 | FUSE - PRIMARY | AVARD | KOCH P/L (HOPETON)-TR 15401 | CMI_NORMAL | NO | NO | NO | 862220 | 53605 | 5522 | 1741 | 429 | 0.00014882 | 1.1598e-06 | 128.3167 | 1 | 310 | Load | 90193 | Load | 0 | PATRICK LYONS | 580-395-4171 | [5 empty] | Other | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005656 |  | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2024 | 862024 | 2020-02-17 10:09 | 2020-02-17 10:40 | 30.5 | 4 | 3 | 111 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 2312 S.BROADWAY | CMI_PLANNED | YES | NO | NO | 862220 | 159309 | 102262 | 4762 | 773 | 0.00012874 | 4.6392e-06 | 27.75 | 1 | 308 | Load | 17602 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005663 | PD-02172020-00174 | SOUTHERN | ADA | 5804:SOUTH ADA | SOUTH_ADA_424 | 580424 | 2020-02-17 10:10 | 2020-02-17 14:04 | 233.72 | 2 | 2 | 412.5333 | 29 | TREES : GROW IN | 21 | FUSE - TRANSFORMER | STONEWALL | STONEWALL OK 74871 | CMI_NORMAL | NO | NO | NO | 862220 | 77728 | 11525 | 3417 | 436 | 0.00047845 | 2.3196e-06 | 206.2667 | 1 | 310 | Secondary | 5254 | Load | Tran1phOH | GARRID H BROWN | 405-207-3948 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2021
J2002.005653 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-02-17 10:19 | 2020-02-17 10:58 | 39.03 | 10 | 1 | 320 | 4 | DETERIORATION | 2 | TRANSFORMER OH | MOUNTAINBURG | E.SIDE OF HWY 71 IN MT.BURG | CMI_PLANNED | YES | NO | NO | 862220 | 82368 | 61287 | 3793 | 2586 | 0.00037113 | 1.1598e-05 | 32 | 1 | 308 | Load | 17405 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-17 | 2020 |  | Ark - Series 2
J2002.005654 |  | METRO EAST | SHAWNEE | 7410:MAUD TAP | MAUD_TAP_1021 | 741021 | 2020-02-17 10:21 | 2020-02-17 12:52 | 151.72 | 2 | 1 | 176.65 | 4 | DETERIORATION | 12 | POLE | MAUD | 502 W MAIN | CMI_PLANNED | YES | NO | NO | 862220 | 114534 | 22147 | 1020 | 763 | 0.00020488 | 2.3196e-06 | 88.325 | 1 | 308 | Load | 1580 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005665 |  | METRO EAST | SHAWNEE | 7410:MAUD TAP | MAUD_TAP_1021 | 741021 | 2020-02-17 10:21 | 2020-02-17 12:55 | 154.67 | 1 | 2 | 150.65 | 4 | DETERIORATION | 12 | POLE | MAUD | 309 W MONROE | CMI_PLANNED | YES | NO | NO | 862220 | 114534 | 22147 | 1020 | 763 | 0.00017472 | 1.1598e-06 | 150.65 | 1 | 310 | Customer | 10927 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005657 |  | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1129 | 511129 | 2020-02-17 10:26 | 2020-02-17 11:06 | 40.33 | 3 | 0 | 98.9 | 4 | DETERIORATION | 2 | TRANSFORMER OH | 0 | 3RD AVE 3.3E | CMI_PLANNED | YES | NO | NO | 862220 | 77728 | 23612 | 2210 | 1003 | 0.0001147 | 3.4794e-06 | 32.9667 | 1 | 0 | Load | 6349 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005664 | PD-02172020-00183 | SOUTHERN | DURANT | 5512:COLBERT | COLBERT_1222 | 551222 | 2020-02-17 10:28 | 2020-02-17 11:15 | 46.57 | 1 | 2 | 40.4564 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | CARTWRIGHT | RODGERS MOBILE HOME PARK | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 77728 | 15524 | 2174 | 1276 | 4.6921e-05 | 1.1598e-06 | 40.4564 | 1 | 310 | Customer | 13363 | Load | Tran1phOH | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005676 | PD-02172020-00184 | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_521 | 320521 | 2020-02-17 10:33 | 2020-02-17 12:27 | 113.65 | 6 | 4 | 658.2 | 27 | TREE:NON PREVENTABLE | 23 | FUSE - PRIMARY | SAPULPA | 14001 W. HWY 66 | CMI_NORMAL | NO | NO | NO | 862220 | 74156 | 40833 | 3862 | 1613 | 0.00076338 | 6.9588e-06 | 109.7 | 1 | 310 | Mainline | 404378 | Fuse | FuseOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Vegetation | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | OK - 2022
J2002.005684 | PD-02172020-00198 | NORTHEAST | SAPULPA | 7632:OAK GROVE | OAK_GROVE_3221 | 763221 | 2020-02-17 10:35 | 2020-02-17 13:08 | 153.1 | 5 | 6 | 338.1667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | DRUMRIGHT | 125 E.2ND | CMI_NORMAL | NO | NO | NO | 862220 | 74156 | 40833 | 1021 | 1021 | 0.0003922 | 5.799e-06 | 67.6333 | 1 | 310 | Load | 44195 | Load | Tran1phOH | [7 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | OK - 2021
J2002.005685 |  | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4124 | 814124 | 2020-02-17 10:42 | 2020-02-17 10:54 | 12 | 1 | 1 | 12 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 3404 S SHARTEL AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 159309 | 102262 | 5814 | 2015 | 1.3918e-05 | 1.1598e-06 | 12 | 1 | 310 | Customer | 17848 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005687 | PD-02172020-00200 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-02-17 10:47 | 2020-02-17 11:32 | 44.73 | 1 | 1 | 44.7333 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | MOUNTAINBURG | 1714 PIGEON CREEK RD | CMI_NORMAL | NO | NO | NO | 862220 | 82368 | 61287 | 3793 | 2586 | 5.1882e-05 | 1.1598e-06 | 44.7333 | 1 | 310 | Load | 422974 | Load | Tran1phOH | KRIS L HALMES | 479-430-9447 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-02-17 | 2020 |  | Ark - Series 2
J2002.005686 |  | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2223 | 882223 | 2020-02-17 10:48 | 2020-02-17 10:48 | 0.78 | 40 | 21 | 672 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | EDMOND | 0 | CMI_MOMENTARY | YES | NO | NO | 862220 | 168372 | 19843 | 5389 | 1202 | 0.00077938 | 4.6392e-05 | 16.8 | 1 | 310 | Mainline |  | 0 | 0 | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005690 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-17 10:50 | 2020-02-17 11:33 | 42.45 | 3 | 2 | 103.5821 | 4 | DETERIORATION | 2 | TRANSFORMER OH | LAMAR | LAMAR CUMBERLAND NO.- HIGH SCH | CMI_PLANNED | YES | NO | NO | 862220 | 82368 | 7554 | 731 | 0 | 0.00012013 | 3.4794e-06 | 34.5274 | 1 | 310 | Load | 50 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005695 |  | SOUTHERN | ADA | 5816:PARK LANE | PARK_LANE_1621 | 581621 | 2020-02-17 11:01 | 2020-02-17 12:10 | 68.57 | 1 | 1 | 9.7 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ADA | 830 W.5 | CMI_NORMAL | NO | NO | NO | 862220 | 77728 | 11525 | 3466 | 1812 | 1.125e-05 | 1.1598e-06 | 9.7 | 1 | 310 | Customer | 9722 | Load | Tran1phOH | Wrong Circuit | [6 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005696 |  | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5422 | 865422 | 2020-02-17 11:04 | 2020-02-17 11:32 | 28.38 | 1 | 1 | 28.3833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MOORE | 2950 S. Service Rd I-35, #2500 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 159309 | 102262 | 9811 | 1158 | 3.2919e-05 | 1.1598e-06 | 28.3833 | 1 | 310 | Customer | 389601 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005699 | PD-02172020-00377 | METRO SOUTH | SOUTH | 8706:BOYD | BOYD_623 | 870623 | 2020-02-17 11:04 | 2020-02-17 14:46 | 221.77 | 1 | 1 | 221.7667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | 1420 W.LINDSEY | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 159309 | 57047 | 7375 | 1901 | 0.0002572 | 1.1598e-06 | 221.7667 | 1 | 310 | Customer | 54398 | Load | Tran3phPadWye | GERARDO D SOTO | 405-758-6334 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2021
J2002.005698 | PD-02172020-00214 | METRO SOUTH | SOUTH CENTRAL | 8654:MOORE | MOORE_5424 | 865424 | 2020-02-17 11:06 | 2020-02-17 12:44 | 98.33 | 1 | 1 | 98.3333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MOORE | 829 SE.4 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 159309 | 102262 | 9811 | 2011 | 0.00011405 | 1.1598e-06 | 98.3333 | 1 | 310 | Customer | 64883 | Load | Tran3phPadWye | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005707 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1226 | 831226 | 2020-02-17 11:16 | 2020-02-17 11:32 | 15.67 | 1 | 1 | 15.6667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4400 Hemingway Dr. #118 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168372 | 148529 | 7757 | 1748 | 1.817e-05 | 1.1598e-06 | 15.6667 | 1 | 320 | Customer | 69174 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2021
J2002.005709 | PD-02172020-00222 | SOUTHERN | ARDMORE | 5107:TOWER HEIGHTS | TOWER_HEIGHTS_722 | 510722 | 2020-02-17 11:22 | 2020-02-17 13:16 | 114.45 | 1 | 3 | 111.2167 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | ARDMORE | 42 OVERLAND-ROUTE | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862220 | 77728 | 23612 | 4517 | 986 | 0.00012899 | 1.1598e-06 | 111.2167 | 1 | 320 | Customer | 22311 | Load | Tran1phPad | JOE LOFTIS | 918-884-5349 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005708 |  | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5021 | 865021 | 2020-02-17 11:22 | 2020-02-17 11:34 | 12.32 | 1 | 1 | 12.3167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MIDWEST CITY | 2509 GLENHAVEN DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 114534 | 71278 | 8633 | 1294 | 1.4285e-05 | 1.1598e-06 | 12.3167 | 1 | 310 | Customer | 32834 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005710 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-02-17 11:23 | 2020-02-17 12:04 | 40.82 | 3 | 3 | 112.7866 | 4 | DETERIORATION | 12 | POLE | MOUNTAINBURG | 1 SPAN E-HWY71 ON SIMCO,MTNBRG | CMI_PLANNED | YES | NO | NO | 862220 | 82368 | 61287 | 3793 | 2586 | 0.00013081 | 3.4794e-06 | 37.5956 | 1 | 310 | Load | 4631 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-17 | 2020 |  | Ark - Series 2
J2002.005711 |  | ARKANSAS | FORT SMITH | 9512:ADABELL ROAD | ADABELL_ROAD_1222 | 951222 | 2020-02-17 11:26 | 2020-02-17 13:28 | 121.85 | 7 | 6 | 836.0653 | 4 | DETERIORATION | 1 | TRANSFORMER UG | VAN BUREN | 809 LISA LN | CMI_PLANNED | YES | NO | NO | 862220 | 82368 | 61287 | 3126 | 1089 | 0.00096967 | 8.1186e-06 | 119.4379 | 1 | 310 | Load | 11678 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-17 | 2020 |  | Ark - Series 1, Ark - Series 2
J2002.005714 | PD-02172020-00230 | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2721 | 872721 | 2020-02-17 11:30 | 2020-02-17 16:14 | 283.58 | 1 | 2 | 283.5833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | NORMAN | 800 LEXINGTON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 159309 | 57047 | 6502 | 960 | 0.0003289 | 1.1598e-06 | 283.5833 | 1 | 310 | Customer | 52630 | Load | Tran1phPad | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005723 |  | METRO EAST | EAST | 8618:BARNES | BARNES_1821 | 861821 | 2020-02-17 11:44 | 2020-02-17 14:56 | 192.13 | 2 | 0 | 370.5833 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | 11001 MASSEY TR. | CMI_PLANNED | YES | NO | NO | 862220 | 114534 | 71278 | 953 | 533 | 0.0004298 | 2.3196e-06 | 185.2917 | 1 | 0 | Load | 64825 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005724 |  | NORTHEAST | MUSKOGEE | 3110:RIVERSIDE | RIVERSIDE_1022 | 311022 | 2020-02-17 11:44 | 2020-02-17 11:50 | 5.3 | 1 | 1 | 5.3 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 2809 ROBIN LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 74156 | 33323 | 2907 | 1093 | 6.1469e-06 | 1.1598e-06 | 5.3 | 1 | 310 | Customer | 10299 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005732 |  | METRO EAST | EAST | 8686:GENERAL MOTORS | GENERAL_MOTORS_8641 | 868641 | 2020-02-17 11:53 | 2020-02-17 11:56 | 2.65 | 1 | 0 | 2.65 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 7447 SE 74TH ST | CMI_MOMENTARY | YES | NO | NO | 862220 | 114534 | 71278 | 1 | 1 | 3.0735e-06 | 1.1598e-06 | 2.65 | 1 | 0 | Feeder | GENERAL_MOTORS_8641 | Recloser | 0 | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005733 | PD-02172020-00241 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1221 | 831221 | 2020-02-17 11:55 | 2020-02-17 14:52 | 176.73 | 1 | 1 | 176.7333 | 3 | DAMAGED BY PUBLIC | 30 | CONDUCTOR SERVICE - UG | NICHOLS HILLS | 6518 N.HILLCREST AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168372 | 148529 | 7757 | 995 | 0.00020497 | 1.1598e-06 | 176.7333 | 1 | 310 | Customer | 14125 | Load | TranOpenDelta | JESSE PHILLER | 405-512-8086 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2022
J2002.005738 |  | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_521 | 320521 | 2020-02-17 12:01 | 2020-02-17 12:28 | 27.53 | 1 | 1 | 27.5333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SAPULPA | 1/4S OF TAFT ON MESA RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 74156 | 40833 | 3862 | 1613 | 3.1933e-05 | 1.1598e-06 | 27.5333 | 1 | 310 | Customer | 45236 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | OK - 2022
J2002.005745 |  | ARKANSAS | FORT SMITH | 9104:J STREET | J_STREET_422 | 910422 | 2020-02-17 12:17 | 2020-02-17 13:19 | 62.62 | 9 | 7 | 513.121 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 1113 N.6 | CMI_PLANNED | YES | NO | NO | 862220 | 82368 | 61287 | 2003 | 514 | 0.00059512 | 1.0438e-05 | 57.0134 | 1 | 310 | Load | 173 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-17 | 2020 |  | Ark - Series 2
J2002.005750 |  | ARKANSAS | FORT SMITH | 9104:J STREET | J_STREET_422 | 910422 | 2020-02-17 12:19 | 2020-02-17 13:19 | 59.65 | 3 | 4 | 163.4 | 11 | OVERLOAD | 2 | TRANSFORMER OH | FORT SMITH | 1201 N.6 LOW | CMI_PLANNED | YES | NO | NO | 862220 | 82368 | 61287 | 2003 | 514 | 0.00018951 | 3.4794e-06 | 54.4667 | 1 | 310 | Secondary | 295 | Load | TranOpenDelta | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-17 | 2020 |  | Ark - Series 2
J2002.005754 |  | NORTHEAST | SAPULPA | 3208:TIBBENS ROAD | TIBBENS_RD_824 | 320824 | 2020-02-17 12:43 | 2020-02-17 13:05 | 21.43 | 1 | 1 | 21.4333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | GLENPOOL | 12302 S YUKON AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 74156 | 40833 | 3146 | 1403 | 2.4858e-05 | 1.1598e-06 | 21.4333 | 1 | 310 | Customer | 369026 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2020
J2002.005752 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-02-17 12:44 | 2020-02-17 15:00 | 136.13 | 21 | 10 | 1604.75 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 1844 NW.23 | CMI_PLANNED | YES | NO | NO | 862220 | 168372 | 148529 | 11118 | 2056 | 0.0018612 | 2.4356e-05 | 76.4167 | 1 | 310 | Load | 21851 | Load | TranOpenDelta | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2021
J2002.005769 | PD-02172020-00307 | NORTHWEST | ENID | 4105:ENID | ENID_522 | 410522 | 2020-02-17 12:47 | 2020-02-17 13:55 | 68.33 | 29 | 15 | 1503.1667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | ENID | 318 W PARK--ENID | CMI_NORMAL | NO | NO | NO | 862220 | 53605 | 37643 | 1328 | 308 | 0.0017434 | 3.3634e-05 | 51.8333 | 1 | 310 | Load | 15423 | Load | Tran1phOH | RONALD K GOSE | 580-541-3131 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005755 | PD-02172020-00304 | METRO SOUTH | SOUTH | 5607:ROSEDALE TAP | ROSEDALE_TAP_722 | 560722 | 2020-02-17 12:48 | 2020-02-17 16:59 | 251.25 | 355 | 79 | 82780.0833 | 3 | DAMAGED BY PUBLIC | 31 | CONDUCTOR SERVICE - OH | WAYNE | 31058 ST HWY 59 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 159309 | 57047 | 993 | 653 | 0.096008 | 0.00041173 | 233.1833 | 1 | 310 | Mainline | 8783 | Fuse | FuseOH | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005775 | PD-02172020-00350 | METRO SOUTH | SOUTH | 5606:WALNUT CREEK | WALNUT_CREEK_621 | 560621 | 2020-02-17 13:01 | 2020-02-17 18:34 | 333.45 | 1 | 1 | 333.45 | 3 | DAMAGED BY PUBLIC | 23 | FUSE - PRIMARY | WAYNE | 3/4E I35 + HY 59 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 159309 | 57047 | 1111 | 1111 | 0.00038673 | 1.1598e-06 | 333.45 | 1 | 310 | Load | 18576 | Load | TranOpenDeltaPad | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005772 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6127 | 836127 | 2020-02-17 13:01 | 2020-02-17 14:37 | 96.05 | 136 | 1 | 2649.7333 | 4 | DETERIORATION | 27 | CUTOUT | OKLAHOMA CITY | 2314 N.MCKINLEY AVE | CMI_PLANNED | YES | NO | NO | 862220 | 168372 | 148529 | 11118 | 2056 | 0.0030732 | 0.00015773 | 19.4833 | 1 | 320 | Mainline | 20114 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2021
J2002.005771 |  | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_621 | 770621 | 2020-02-17 13:01 | 2020-02-17 15:41 | 159.98 | 2 | 3 | 276.6547 | 4 | DETERIORATION | 2 | TRANSFORMER OH | BRISTOW | 2.5 NW BRISTOW ES HWY 16 | CMI_PLANNED | YES | NO | NO | 862220 | 74156 | 40833 | 3786 | 1576 | 0.00032086 | 2.3196e-06 | 138.3273 | 1 | 310 | Load | 44657 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | OK - 2021
J2002.005781 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-17 13:10 | 2020-02-17 16:13 | 182.3 | 4 | 3 | 351.3177 | 4 | DETERIORATION | 2 | TRANSFORMER OH | LAMAR | BY LAMAR FOOTBALL STAD | CMI_PLANNED | YES | NO | NO | 862220 | 82368 | 7554 | 731 | 0 | 0.00040746 | 4.6392e-06 | 87.8294 | 1 | 310 | Mainline | 7073 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005783 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7422 | 847422 | 2020-02-17 13:12 | 2020-02-17 17:36 | 263.98 | 1 | 1 | 92.1833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 222 NE.27 | CMI_PLANNED | YES | NO | NO | 862220 | 168372 | 148529 | 6173 | 1215 | 0.00010691 | 1.1598e-06 | 92.1833 | 1 | 308 | Load | 5801 | Load | Tran3phWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2022
J2002.005789 |  | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1822 | 931822 | 2020-02-17 13:19 | 2020-02-17 14:45 | 85.77 | 10 | 4 | 672.3333 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | ALMA | HWY 64 + OLD HWY 64 | CMI_PLANNED | YES | NO | NO | 862220 | 82368 | 61287 | 2851 | 787 | 0.00077977 | 1.1598e-05 | 67.2333 | 1 | 308 | Mainline | 1617 | Fuse | FuseRiser | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | Ark - Series 2
J2002.005802 |  | NORTHWEST | WOODWARD | 4606:CEDAR AVE | CEDAR_AVE_631 | 460631 | 2020-02-17 13:23 | 2020-02-17 14:04 | 40.58 | 1 | 1 | 35.6667 | 4 | DETERIORATION | 12 | POLE | WOODWARD | .5BW-MARTN RD,OILPATCH RD | CMI_PLANNED | YES | NO | NO | 862220 | 53605 | 10440 | 5689 | 1170 | 4.1366e-05 | 1.1598e-06 | 35.6667 | 1 | 308 | Load | 13086 | Load | TranOpenDelta | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005796 | PD-02172020-00367 | NORTHEAST | SAPULPA | 3205:SAPULPA | SAPULPA_521 | 320521 | 2020-02-17 13:30 | 2020-02-17 14:44 | 73.57 | 1 | 1 | 73.5667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SAPULPA | 1/4S OF TAFT ON MESA RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 74156 | 40833 | 3862 | 1613 | 8.5322e-05 | 1.1598e-06 | 73.5667 | 1 | 310 | Customer | 45236 | Load | Tran1phOH | PHIL STICKLER | 918-991-1321 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | OK - 2022
J2002.005798 | PD-02172020-00362 | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_623 | 550623 | 2020-02-17 13:35 | 2020-02-17 13:58 | 23.38 | 1 | 1 | 23.3833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | CADDO | 304 S.MANNING ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 77728 | 15524 | 6752 | 1720 | 2.712e-05 | 1.1598e-06 | 23.3833 | 1 | 310 | Customer | 13228 | Load | Tran1phOH | CONTRACTOR BHI3 DAVID ELLIOT INC | 918-282-1005 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005797 | PD-02172020-00358 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2224 | 832224 | 2020-02-17 13:35 | 2020-02-17 13:59 | 24.17 | 1 | 1 | 24.1667 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 3825 NW.27 | CMI_NORMAL | NO | NO | NO | 862220 | 168372 | 148529 | 9181 | 1433 | 2.8028e-05 | 1.1598e-06 | 24.1667 | 1 | 320 | Customer | 4829 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005808 |  | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3722 | 913722 | 2020-02-17 13:50 | 2020-02-17 14:12 | 22.85 | 1 | 1 | 22.85 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 5801 KINKEAD AV HLD1 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 82368 | 61287 | 4576 | 1441 | 2.6501e-05 | 1.1598e-06 | 22.85 | 1 | 310 | Customer | 20 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | Ark - Series 3
J2002.005809 |  | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_721 | 590721 | 2020-02-17 13:50 | 2020-02-17 16:33 | 163.05 | 1 | 0 | 163.005 | 4 | DETERIORATION | 2 | TRANSFORMER OH | 0 | 23356 Pettijohn Rd | CMI_PLANNED | YES | NO | NO | 862220 | 77728 | 7204 | 2191 | 505 | 0.00018905 | 1.1598e-06 | 163.005 | 1 | 0 | Load | 414424 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2021
J2002.005810 | PD-02172020-00375 | SOUTHERN | DURANT | 5508:BROWN OG AND E | BROWN_OGE_861 | 550861 | 2020-02-17 13:52 | 2020-02-17 14:43 | 51.47 | 1 | 1 | 38.7 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | DURANT | E2030 Rd and Pecan Ridge .1N | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862220 | 77728 | 15524 | 1106 | 483 | 4.4884e-05 | 1.1598e-06 | 38.7 | 1 | 320 | Customer | 403304 | Load | Tran1phPad | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005811 | PD-02172020-00386 | METRO WEST | WEST | 8158:SARA | SARA_5862 | 815862 | 2020-02-17 13:52 | 2020-02-17 16:15 | 143.42 | 1 | 2 | 43.681 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 3804 Paliside Ln | CMI_NORMAL | NO | NO | NO | 862220 | 129031 | 116230 | 18297 | 3620 | 5.0661e-05 | 1.1598e-06 | 43.681 | 1 | 320 | Customer | 401228 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2022
J2002.005817 |  | METRO SOUTH | SOUTH | 5607:ROSEDALE TAP | ROSEDALE_TAP_722 | 560722 | 2020-02-17 14:09 | 2020-02-17 15:30 | 80.7 | 1 | 1 | 76.0667 | 1 | CANCELLED | 57 | CANCELLED | WAYNE | 1.5E WAYNE 2.5N SH59-LYMDELL W | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 159309 | 57047 | 993 | 653 | 8.8222e-05 | 1.1598e-06 | 76.0667 | 1 | 310 | Load | 22815 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005826 | PD-02172020-00408 | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_624 | 410624 | 2020-02-17 14:37 | 2020-02-17 15:29 | 51.65 | 1 | 1 | 51.65 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | ENID | 222.5 E.WALNUT | CMI_NORMAL | NO | NO | NO | 862220 | 53605 | 37643 | 6033 | 1861 | 5.9904e-05 | 1.1598e-06 | 51.65 | 1 | 310 | Load | 8059 | Load | Tran1phOH | WILLIAM R PETHICK | 580-278-8129 | [5 empty] | Other | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005831 |  | ARKANSAS | POTEAU | 3516:TARBY | TARBY_1625 | 351625 | 2020-02-17 14:42 | 2020-02-17 14:42 | 0 | 1197 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | POTEAU | 82845 N 470TH ST | CMI_MOMENTARY | YES | NO | NO | 862220 | 82368 | 13527 | 1678 | 1197 | 0 | 0.0013883 | 0 | 1 | 0 | Feeder | TARBY_1625 | Breaker | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-02-17 | 2020 |  | #N/A
J2002.005832 | PD-02172020-00409 | METRO EAST | SHAWNEE | 7407:REMINGTON | REMINGTON 22 | 740722 | 2020-02-17 14:42 | 2020-02-17 15:26 | 44.08 | 1 | 1 | 3.4 | 22 | WIND | 31 | CONDUCTOR SERVICE - OH | SHAWNEE | 1402 SHERRY LN | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862220 | 114534 | 22147 | 3671 | 1645 | 3.9433e-06 | 1.1598e-06 | 3.4 | 1 | 320 | Customer | 9088 | Load | Tran1phOH | KEVIN M RICH | 405-802-2121 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005840 | PD-02172020-00451 | METRO NORTH | GUTHRIE | 8814:PINE STREET | PINE_STREET_1429 | 881429 | 2020-02-17 15:05 | 2020-02-17 17:04 | 119.35 | 1 | 2 | 114.95 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | GUTHRIE | N OF HWY 105 3/4M E OF VET COR | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862220 | 168372 | 19843 | 3106 | 1715 | 0.00013332 | 1.1598e-06 | 114.95 | 1 | 310 | Customer | 72607 | Load | Tran1phPad | 1337: NOT FOUND 1337: NOT FOUND | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005841 | PD-02172020-00442 | METRO EAST | EAST | 8542:RENO | RENO_4229 | 854229 | 2020-02-17 15:08 | 2020-02-17 17:31 | 143.17 | 1 | 1 | 143.1667 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | DEL CITY | 4801 SE 15th St | CMI_NORMAL | NO | NO | NO | 862220 | 114534 | 71278 | 5218 | 1347 | 0.00016604 | 1.1598e-06 | 143.1667 | 1 | 310 | Load | 407443 | Load | Tran3phPadWye | REX R WILSON | 405-535-4507 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2022
J2002.005851 | PD-02172020-00497 | METRO SOUTH | SOUTH | 5606:WALNUT CREEK | WALNUT_CREEK_621 | 560621 | 2020-02-17 15:33 | 2020-02-17 18:45 | 191.63 | 1 | 1 | 120.95 | 3 | DAMAGED BY PUBLIC | 23 | FUSE - PRIMARY | WAYNE | 1.5W WAYNE ON SH59 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 159309 | 57047 | 1111 | 1111 | 0.00014028 | 1.1598e-06 | 120.95 | 1 | 310 | Load | 24840 | Load | Tran3phWye | TONY J ILG | 405-714-7441 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005852 | PD-02172020-00444 | METRO NORTH | NORTH | 8248:SW 5TH ST | SW_5TH_ST_4864 | 824864 | 2020-02-17 15:38 | 2020-02-17 18:43 | 185.37 | 1 | 1 | 185.3667 | 5 | ELECTRICAL TRACKING | 15 | METER - SECONDARY | OKLAHOMA CITY | 3929 SW.29 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862220 | 168372 | 148529 | 4203 | 2035 | 0.00021499 | 1.1598e-06 | 185.3667 | 1 | 310 | Customer | 12186 | Load | TranOpenDelta | KYLE L GOODIN | 405-426-9802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2021
J2002.005853 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-17 15:43 | 2020-02-17 17:38 | 114.08 | 2 | 1 | 221.5333 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | POCOLA | 2300 NORTH OF BEATY RD | CMI_PLANNED | YES | NO | NO | 862220 | 82368 | 61287 | 1458 | 1240 | 0.00025693 | 2.3196e-06 | 110.7667 | 1 | 308 | Load | 13959 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | Ark - Series 2
J2002.005858 |  | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_626 | 550626 | 2020-02-17 15:55 | 2020-02-17 15:55 | 0.03 | 1006 | 0 | 33.5333 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | DURANT | 1998 CHUCKWA DR | CMI_MOMENTARY | YES | NO | NO | 862220 | 77728 | 15524 | 6752 | 1006 | 3.8892e-05 | 0.0011668 | 0.033333 | 1 | 0 | Feeder | BODLE_STREET_626 | Recloser | 0 | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005862 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2123 | 822123 | 2020-02-17 15:59 | 2020-02-17 19:56 | 236.68 | 174 | 105 | 39071.7 | 3 | DAMAGED BY PUBLIC | 12 | POLE | OKLAHOMA CITY | 2220 N QUAPAH AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168372 | 148529 | 9254 | 1666 | 0.045315 | 0.0002018 | 224.55 | 1 | 310 | Mainline | 320352 | Fuse | FuseRiser | Ties | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2020
J2002.005867 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1229 | 831229 | 2020-02-17 16:13 | 2020-02-17 18:16 | 123.17 | 1 | 1 | 123.1667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 2229 NW.52 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168372 | 148529 | 7757 | 787 | 0.00014285 | 1.1598e-06 | 123.1667 | 1 | 310 | Customer | 10537 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2022
J2002.005869 | PD-02172020-00480 | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1721 | 861721 | 2020-02-17 16:17 | 2020-02-17 17:22 | 64.97 | 1 | 1 | 64.9667 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 4601 ROYAL OAK DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 114534 | 71278 | 6958 | 1508 | 7.5348e-05 | 1.1598e-06 | 64.9667 | 1 | 310 | Customer | 62439 | Load | Tran1phPad | KYLE L GOODIN | 405-426-9802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005870 | PD-02172020-00514 | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2222 | 832222 | 2020-02-17 16:21 | 2020-02-17 19:44 | 203.38 | 1 | 1 | 146.8882 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4201A N.YOUNGS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168372 | 148529 | 9181 | 1557 | 0.00017036 | 1.1598e-06 | 146.8882 | 1 | 320 | Customer | 49094 | Load | Tran1phPad | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | OK - 2022
J2002.005875 |  | METRO EAST | EAST | 8650:GLENDALE | GLENDALE_5021 | 865021 | 2020-02-17 16:29 | 2020-02-17 17:47 | 78.35 | 1 | 1 | 78.35 | 1 | CANCELLED | 57 | CANCELLED | MIDWEST CITY | 2509 GLENHAVEN DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 114534 | 71278 | 8633 | 1294 | 9.087e-05 | 1.1598e-06 | 78.35 | 1 | 310 | Customer | 32834 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005879 | PD-02172020-00485 | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2921 | 812921 | 2020-02-17 16:38 | 2020-02-17 18:31 | 112.82 | 1 | 1 | 34.0136 | 5 | ELECTRICAL TRACKING | 15 | METER - SECONDARY | OKLAHOMA CITY | 3312 S.STULTS | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862220 | 159309 | 102262 | 6393 | 1484 | 3.9449e-05 | 1.1598e-06 | 34.0136 | 1 | 310 | Customer | 7016 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005886 |  | NORTHEAST | SAPULPA | 3210:HICKORY HILL | HICKORY_HILL_1024 | 321024 | 2020-02-17 16:47 | 2020-02-17 17:34 | 47.62 | 8 | 1 | 295.2 | 4 | DETERIORATION | 1 | TRANSFORMER UG | SAPULPA | L5 B6 VALLEY RIDGE | CMI_PLANNED | YES | NO | NO | 862220 | 74156 | 40833 | 2684 | 1247 | 0.00034237 | 9.2784e-06 | 36.9 | 1 | 308 | Load | 48316 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2022
J2002.005888 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-02-17 16:50 | 2020-02-17 16:50 | 0 | 573 | 0 | 0 | 28 | OTHER (DESCRIBE) | 16 | LINE RECLOSER | 0 | 11441 US HWY 71 | CMI_MOMENTARY | YES | NO | NO | 862220 | 82368 | 61287 | 3793 | 2586 | 0 | 0.00066456 | 0 | 1 | 0 | Mainline | 351790 | Recloser | Rec3phElectronic | Circuit Operation | [6 empty] | Other | N | DISTRIBUTION | 161kV | 2020-02-17 | 2020 |  | Ark - Series 2
J2002.005890 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-02-17 16:50 | 2020-02-17 16:50 | 0 | 429 | 0 | 0 | 28 | OTHER (DESCRIBE) | 16 | LINE RECLOSER | 0 | 11441 US HWY 71 | CMI_MOMENTARY | YES | NO | NO | 862220 | 82368 | 61287 | 3793 | 2586 | 0 | 0.00049755 | 0 | 1 | 0 | Mainline | 351790 | Recloser | Rec3phElectronic | Circuit Operation | [6 empty] | Other | N | DISTRIBUTION | 161kV | 2020-02-17 | 2020 |  | Ark - Series 2
J2002.005891 | PD-02172020-00498 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-02-17 16:54 | 2020-02-17 17:52 | 58.5 | 1 | 1 | 58.5 | 5 | ELECTRICAL TRACKING | 47 | ARRESTOR OH | WINSLOW | WINSLOW RURAL DIST | CMI_NORMAL | NO | NO | NO | 862220 | 82368 | 61287 | 3793 | 2586 | 6.7848e-05 | 1.1598e-06 | 58.5 | 1 | 310 | Load | 15428 | Load | Tran1phOH | KRIS L HALMES | 479-430-9447 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-17 | 2020 |  | Ark - Series 2
J2002.005895 | PD-02172020-00511 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2126 | 822126 | 2020-02-17 16:59 | 2020-02-17 20:03 | 184.38 | 1 | 1 | 104.9131 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1008 FARRA DR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168372 | 148529 | 9254 | 679 | 0.00012168 | 1.1598e-06 | 104.9131 | 1 | 310 | Customer | 36279 | Load | Tran1phOH | JERRY CASNER | 405-620-0772 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005898 |  | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1522 | 811522 | 2020-02-17 17:03 | 2020-02-17 17:34 | 31.47 | 1 | 1 | 31.4667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 2531 SW.29 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 159309 | 102262 | 6073 | 1947 | 3.6495e-05 | 1.1598e-06 | 31.4667 | 1 | 310 | Customer | 984 | Load | TranOHDeltaSplitBank | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | OK - 2022
J2002.005901 | PD-02172020-00513 | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1222 | 831222 | 2020-02-17 17:07 | 2020-02-17 19:24 | 136.8 | 6 | 7 | 778.1 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 2209 NW.59 CIR | CMI_NORMAL | NO | NO | NO | 862220 | 168372 | 148529 | 7757 | 1008 | 0.00090244 | 6.9588e-06 | 129.6833 | 1 | 310 | Load | 15001 | Load | TranOpenDelta | JERRY CASNER | 405-620-0772 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2021
J2002.005910 | PD-02172020-00510 | SOUTHERN | DURANT | 5511:BOKCHITO | BOKCHITO 21 | 551121 | 2020-02-17 17:44 | 2020-02-17 19:25 | 101.27 | 29 | 15 | 2898.0667 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | BOKCHITO | N STEAKLEY ON WALKER | CMI_NORMAL | NO | NO | NO | 862220 | 77728 | 15524 | 675 | 675 | 0.0033612 | 3.3634e-05 | 99.9333 | 1 | 310 | Tap | 5637 | Fuse | FuseOH | MICHAEL N STROHL | 903-821-1619 | [5 empty] | Weather | N | DISTRIBUTION | 34.5/19.9kv | 2020-02-17 | 2020 |  | #N/A
J2002.005913 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6128 | 836128 | 2020-02-17 17:48 | 2020-02-17 18:56 | 68.17 | 2 | 0 | 127.4667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 4608 N.COOPER | CMI_PLANNED | YES | NO | NO | 862220 | 168372 | 148529 | 11118 | 958 | 0.00014784 | 2.3196e-06 | 63.7333 | 1 | 0 | Load | 9150 | Load | TranOH3phDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2021
J2002.005916 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2123 | 822123 | 2020-02-17 17:55 | 2020-02-17 19:55 | 120.57 | 3 | 0 | 326.95 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 2301 N PORTLAND AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168372 | 148529 | 9254 | 1666 | 0.0003792 | 3.4794e-06 | 108.9833 | 1 | 0 | Mainline | 36399 | Switch | SwitchOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2020
J2002.005920 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1226 | 831226 | 2020-02-17 18:03 | 2020-02-17 18:19 | 15.47 | 1 | 1 | 15.4667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 806 NW.45 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168375 | 148532 | 7757 | 1748 | 1.7938e-05 | 1.1598e-06 | 15.4667 | 1 | 310 | Customer | 13574 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2021
J2002.005923 | PD-02172020-00516 | METRO WEST | WEST | 8323:RICHARDS | RICHARDS_2323 | 832323 | 2020-02-17 18:14 | 2020-02-17 21:59 | 224.97 | 2 | 3 | 348.6167 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 11317 EAGLE LN | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862220 | 129031 | 116230 | 5025 | 1671 | 0.00040432 | 2.3196e-06 | 174.3083 | 1 | 310 | Secondary | 65238 | Load | Tran1phOH | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005922 | PD-02172020-00517 | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2521 | 512521 | 2020-02-17 18:14 | 2020-02-17 19:43 | 88.52 | 1 | 1 | 73.45 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | LONE GROVE | E OF MELH CH | CMI_NORMAL | NO | NO | NO | 862220 | 77728 | 23612 | 3309 | 784 | 8.5187e-05 | 1.1598e-06 | 73.45 | 1 | 310 | Load | 20135 | Load | Tran1phOH | JUSTIN B MARSHALL | 580-221-5051 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005928 | PD-02172020-00519 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4024 | 834024 | 2020-02-17 18:17 | 2020-02-17 21:09 | 172.37 | 2 | 3 | 254.1 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6801 NW 122nd St,* DEERWOOD APTS. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 129031 | 116230 | 10846 | 1678 | 0.0002947 | 2.3196e-06 | 127.05 | 1 | 310 | Secondary | 73962 | Load | Tran1phPad | PETER BILICKI | 619-726-8332 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005929 | PD-02172020-00522 | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2124 | 822124 | 2020-02-17 18:26 | 2020-02-18 01:20 | 414.05 | 1 | 1 | 414.05 | 22 | WIND | 17 | JUMPER | OKLAHOMA CITY | 4700 NW.10 | CMI_NORMAL | NO | NO | NO | 862220 | 168375 | 148532 | 9255 | 428 | 0.00048021 | 1.1598e-06 | 414.05 | 1 | 310 | Load | 50289 | Load | TranPad3phDelta | JESSE PHILLER | 405-512-8086 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2021
J2002.005934 | PD-02172020-00520 | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6221 | 866221 | 2020-02-17 18:38 | 2020-02-18 00:09 | 330.77 | 2 | 3 | 649.6833 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | MIDWEST CITY | 1720 ALBERT DR | CMI_NORMAL | NO | NO | NO | 862220 | 114534 | 71277 | 7214 | 1294 | 0.0007535 | 2.3196e-06 | 324.8417 | 1 | 310 | Secondary | 61233 | Load | Tran1phPad | JEREMIAH D WALKER | 405-974-0464 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005933 | PD-02172020-00518 | METRO EAST | EAST | 8617:SUNNYLANE | SUNNYLANE_1723 | 861723 | 2020-02-17 18:42 | 2020-02-17 20:03 | 80.95 | 1 | 1 | 72.9167 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | DEL CITY | 3609 VICKIE DR | CMI_NORMAL | NO | NO | NO | 862220 | 114534 | 71277 | 6957 | 1600 | 8.4569e-05 | 1.1598e-06 | 72.9167 | 1 | 310 | Customer | 46669 | Load | Tran1phOH | KYLE L GOODIN | 405-426-9802 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005937 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6128 | 836128 | 2020-02-17 19:00 | 2020-02-17 20:15 | 75.15 | 1 | 1 | 46.1 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 4526 N.SEWELL AV | CMI_PLANNED | YES | NO | NO | 862220 | 168375 | 148532 | 11118 | 958 | 5.3467e-05 | 1.1598e-06 | 46.1 | 1 | 308 | Load | 19908 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2021
J2002.005941 |  | METRO WEST | WEST | 8342:BRADEN PARK | BRADEN_PARK_4223 | 834223 | 2020-02-17 19:22 | 2020-02-17 20:04 | 41.73 | 2 | 2 | 36.6 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1/2MN NW.122 + MAC ARTHUR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 129031 | 116230 | 3402 | 1783 | 4.2449e-05 | 2.3196e-06 | 18.3 | 1 | 310 | Secondary | 70873 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2022
J2002.005942 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2128 | 822128 | 2020-02-17 19:41 | 2020-02-17 20:12 | 30.95 | 1 | 1 | 30.95 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 5722 NW.23 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168375 | 148532 | 9255 | 1940 | 3.5896e-05 | 1.1598e-06 | 30.95 | 1 | 310 | Customer | 35029 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2021
J2002.005946 |  | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3221 | 813221 | 2020-02-17 20:23 | 2020-02-17 20:28 | 4.92 | 1 | 1 | 4.9167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1120 SW.51 | CMI_MOMENTARY | YES | NO | NO | 862220 | 159311 | 102264 | 7610 | 2077 | 5.7023e-06 | 1.1598e-06 | 4.9167 | 1 | 320 | Customer | 8143 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-17 | 2020 |  | #N/A
J2002.005948 | PD-02172020-00536 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2029 | 862029 | 2020-02-17 20:30 | 2020-02-17 21:30 | 59.55 | 1 | 1 | 59.55 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 736 SE 32ND ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 159311 | 102264 | 4763 | 987 | 6.9066e-05 | 1.1598e-06 | 59.55 | 1 | 320 | Customer | 17417 | Load | Tran1phOH | KYLE L GOODIN | 405-426-9802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | #N/A
J2002.005959 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6123 | 836123 | 2020-02-17 22:15 | 2020-02-17 22:25 | 9.62 | 1 | 1 | 9.6167 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 3340 N.WALKER | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862220 | 168375 | 148532 | 11118 | 942 | 1.1153e-05 | 1.1598e-06 | 9.6167 | 1 | 310 | Customer | 2050 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-17 | 2020 |  | OK - 2020
J2002.005990 |  | SOUTHERN | ARDMORE | 5117:MARIETTA | MARIETTA_1721 | 511721 | 2020-02-18 06:09 | 2020-02-18 08:18 | 128.92 | 1 | 2 | 92.85 | 28 | OTHER (DESCRIBE) | 21 | FUSE - TRANSFORMER | MARIETTA | RANDOLPH ST | CMI_NORMAL | NO | NO | NO | 862209 | 77728 | 23612 | 1595 | 637 | 0.00010769 | 1.1598e-06 | 92.85 | 1 | 310 | Load | 12471 | Load | Tran1phOH | [7 empty] | Other | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | #N/A
J2002.005996 | PD-02182020-00020 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6024 | 836024 | 2020-02-18 06:50 | 2020-02-18 09:47 | 176.97 | 1 | 1 | 7.1724 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | BETHANY | 2924 N.MCMILLAN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 129031 | 116230 | 5509 | 1342 | 8.3187e-06 | 1.1598e-06 | 7.1724 | 1 | 310 | Customer | 34176 | Load | Tran1phOH | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | OK - 2022
J2002.006002 |  | SOUTHERN | HEALDTON | 5122:DILLARD | DILLARD_2222 | 512222 | 2020-02-18 07:55 | 2020-02-18 07:55 | 0 | 700 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | WILSON | 7460 DILLARD RD | CMI_MOMENTARY | YES | NO | NO | 862209 | 77728 | 6811 | 1191 | 700 | 0 | 0.00081187 | 0 | 1 | 0 | Feeder | DILLARD_2222 | Breaker | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006003 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1226 | 831226 | 2020-02-18 07:57 | 2020-02-18 09:24 | 86.68 | 7 | 6 | 363.0583 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 1410 NW.49 | CMI_PLANNED | YES | NO | NO | 862209 | 168375 | 148532 | 7757 | 1748 | 0.00042108 | 8.1187e-06 | 51.8655 | 1 | 310 | Load | 13857 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2021
J2002.006006 |  | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2225 | 832225 | 2020-02-18 08:18 | 2020-02-18 08:44 | 26.85 | 11 | 0 | 197.0833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 3020 N.PENN | CMI_PLANNED | YES | NO | NO | 862209 | 168375 | 148532 | 9181 | 2040 | 0.00022858 | 1.2758e-05 | 17.9167 | 1 | 0 | Load | 2983 | Load | TranOpenDelta | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | OK - 2021
J2002.006007 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3829 | 913829 | 2020-02-18 08:21 | 2020-02-18 11:39 | 198.03 | 10 | 8 | 1846.9167 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 1620 S.S | CMI_PLANNED | YES | NO | NO | 862209 | 82366 | 61285 | 2945 | 1191 | 0.0021421 | 1.1598e-05 | 184.6917 | 1 | 308 | Load | 10278 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-18 | 2020 |  | Ark - Series 2
J2002.006013 | PD-02182020-00102 | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8123 | 838123 | 2020-02-18 08:25 | 2020-02-18 10:55 | 150.23 | 2 | 2 | 188.65 | 3 | DAMAGED BY PUBLIC | 14 | PEDESTAL/J-BOX | OKLAHOMA CITY | 7420 NW 84TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 129031 | 116230 | 8966 | 1217 | 0.0002188 | 2.3196e-06 | 94.325 | 1 | 310 | Load | 133556 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006009 |  | NORTHWEST | ENID | 4158:FAIRMONT | FAIRMONT_5829 | 415829 | 2020-02-18 08:30 | 2020-02-18 14:06 | 336.57 | 1 | 1 | 309.7667 | 4 | DETERIORATION | 12 | POLE | FAIRMONT | 1E, 1 S FOSTERS CORNER | CMI_PLANNED | YES | NO | NO | 862209 | 53606 | 37643 | 1643 | 1625 | 0.00035927 | 1.1598e-06 | 309.7667 | 1 | 308 | Load | 14389 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2021
J2002.006010 |  | NORTHWEST | ENID | 4158:FAIRMONT | FAIRMONT_5829 | 415829 | 2020-02-18 08:30 | 2020-02-18 14:06 | 336.08 | 1 | 1 | 311.2 | 4 | DETERIORATION | 12 | POLE | FAIRMONT | 1S,7/8 E FOSTERS CR. SS | CMI_PLANNED | YES | NO | NO | 862209 | 53606 | 37643 | 1643 | 1625 | 0.00036093 | 1.1598e-06 | 311.2 | 1 | 308 | Load | 4403 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2021
J2002.006018 | PD-02182020-00122 | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7022 | 817022 | 2020-02-18 08:44 | 2020-02-18 11:08 | 143.72 | 1 | 1 | 143.7167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MOORE | 940 NW.22 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 159311 | 102264 | 9938 | 2103 | 0.00016668 | 1.1598e-06 | 143.7167 | 1 | 310 | Customer | 20674 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006019 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1229 | 831229 | 2020-02-18 08:45 | 2020-02-18 09:05 | 20.42 | 1 | 1 | 20.4167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2229 NW.52 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 168375 | 148532 | 7757 | 787 | 2.3679e-05 | 1.1598e-06 | 20.4167 | 1 | 310 | Customer | 10537 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2022
J2002.006017 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1229 | 831229 | 2020-02-18 08:46 | 2020-02-18 09:22 | 36.03 | 5 | 3 | 159.5833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 2212 NW.43 | CMI_PLANNED | YES | NO | NO | 862209 | 168375 | 148532 | 7757 | 787 | 0.00018509 | 5.7991e-06 | 31.9167 | 1 | 308 | Load | 13495 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2022
J2002.006024 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6121 | 836121 | 2020-02-18 08:59 | 2020-02-18 10:01 | 62.22 | 13 | 12 | 748.3667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 717 NW.33 | CMI_PLANNED | YES | NO | NO | 862209 | 168375 | 148532 | 11118 | 1638 | 0.00086796 | 1.5078e-05 | 57.5667 | 1 | 310 | Load | 19235 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2021
J2002.006026 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1226 | 831226 | 2020-02-18 09:00 | 2020-02-18 09:26 | 25.55 | 11 | 10 | 257.7667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 1430 NW.49 | CMI_PLANNED | YES | NO | NO | 862209 | 168375 | 148532 | 7757 | 1748 | 0.00029896 | 1.2758e-05 | 23.4333 | 1 | 310 | Load | 7093 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2021
J2002.006033 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7023 | 817023 | 2020-02-18 09:06 | 2020-02-18 10:33 | 87.22 | 5 | 4 | 380.9583 | 4 | DETERIORATION | 1 | TRANSFORMER UG | OKLAHOMA CITY | 649 CITY-VIEW DR | CMI_PLANNED | YES | NO | NO | 862209 | 159311 | 102264 | 9938 | 646 | 0.00044184 | 5.7991e-06 | 76.1917 | 1 | 308 | Load | 33416 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006030 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7431 | 847431 | 2020-02-18 09:06 | 2020-02-18 10:17 | 70.22 | 8 | 10 | 524 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 636 E.HILL | CMI_PLANNED | YES | NO | NO | 862209 | 168375 | 148532 | 6173 | 374 | 0.00060774 | 9.2785e-06 | 65.5 | 1 | 310 | Load | 24306 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2022
J2002.006034 | PD-02182020-00149 | METRO EAST | SEMINOLE | 7508:EMAHAKA | EMAHAKA 21 | 750821 | 2020-02-18 09:14 | 2020-02-18 10:28 | 74.38 | 1 | 1 | 63 | 25 | LIGHTNING | 21 | FUSE - TRANSFORMER | WEWOKA | 36596 E 131 RD | CMI_NORMAL | NO | NO | NO | 862209 | 114534 | 13627 | 253 | 253 | 7.3068e-05 | 1.1598e-06 | 63 | 1 | 310 | Load | 22871 | Load | TranOpenDelta | DELBERT HISAW | 405-683-1721 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | #N/A
J2002.006035 | PD-02182020-00164 | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6922 | 846922 | 2020-02-18 09:14 | 2020-02-18 10:22 | 68.32 | 1 | 1 | 68.3167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1024 NW.105 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 168375 | 148532 | 7733 | 1490 | 7.9234e-05 | 1.1598e-06 | 68.3167 | 1 | 310 | Customer | 49079 | Load | Tran1phPad | KIRK REILLEY | 405-550-3062 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006039 | PD-02182020-00160 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6324 | 816324 | 2020-02-18 09:22 | 2020-02-18 10:33 | 70.98 | 1 | 1 | 65.1667 | 12 | POOR CONNECTION | 50 | CONNECTOR | MOORE | 756 W.MAIN | CMI_NORMAL | NO | NO | NO | 862209 | 159311 | 102264 | 11849 | 2049 | 7.5581e-05 | 1.1598e-06 | 65.1667 | 1 | 310 | Customer | 20367 | Load | Tran1phOH | MIKE MITCHELL | 405-996-8178 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2021
J2002.006042 | PD-02182020-00159 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6326 | 816326 | 2020-02-18 09:24 | 2020-02-18 09:59 | 35.3 | 1 | 1 | 35.3 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | LOT 6 LUCA LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 159311 | 102264 | 11849 | 1270 | 4.0941e-05 | 1.1598e-06 | 35.3 | 1 | 320 | Load | 401653 | Load | Tran1phPad | GERARDO D SOTO | 405-758-6334 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006048 |  | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4024 | 914024 | 2020-02-18 09:30 | 2020-02-18 12:43 | 193.03 | 6 | 7 | 1136.5 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 1613 S.QUINCY | CMI_PLANNED | YES | NO | NO | 862209 | 82366 | 61285 | 4724 | 1167 | 0.0013181 | 6.9589e-06 | 189.4167 | 1 | 310 | Load | 12206 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-18 | 2020 |  | Ark - Series 2
J2002.006050 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1226 | 831226 | 2020-02-18 09:38 | 2020-02-18 13:00 | 201.2 | 4 | 3 | 166 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 1819 NW.42 | CMI_PLANNED | YES | NO | NO | 862209 | 168375 | 148532 | 7757 | 1748 | 0.00019253 | 4.6392e-06 | 41.5 | 1 | 308 | Load | 21568 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2021
J2002.006060 | PD-02182020-00233 | SOUTHERN | ADA | 5808:HARDEN CITY | HARDEN_CITY_823 | 580823 | 2020-02-18 10:01 | 2020-02-18 12:15 | 134.47 | 1 | 1 | 134.4667 | 13 | PREMATURE FAILURE | 47 | ARRESTOR OH | FITTSTOWN | SOUTH OF PHOTO STUDIO | CMI_NORMAL | NO | NO | NO | 862209 | 77728 | 11525 | 106 | 104 | 0.00015596 | 1.1598e-06 | 134.4667 | 1 | 310 | Load | 21096 | Load | Tran1phOH | GARRID H BROWN | 405-207-3948 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006061 |  | ARKANSAS | POTEAU | 3516:TARBY | TARBY_1670 | 351670 | 2020-02-18 10:03 | 2020-02-18 10:03 | 0 | 475 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | POTEAU | 82845 N 470TH ST | CMI_MOMENTARY | YES | NO | NO | 862209 | 82366 | 13527 | 1678 | 480 | 0 | 0.00055091 | 0 | 1 | 0 | Feeder | TARBY_1670 | Breaker | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 161kV | 2020-02-18 | 2020 |  | #N/A
J2002.006063 | PD-02182020-00255 | METRO WEST | WEST | 8359:YUKON | YUKON_5924 | 835924 | 2020-02-18 10:05 | 2020-02-18 12:25 | 140.48 | 1 | 1 | 111.1586 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | YUKON | 513 LINDA LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 129031 | 116230 | 6438 | 1826 | 0.00012892 | 1.1598e-06 | 111.1586 | 1 | 310 | Customer | 47635 | Load | Tran1phPad | STEVEN GILES | 405-227-2802 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | #N/A
J2002.006064 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1225 | 831225 | 2020-02-18 10:07 | 2020-02-18 11:28 | 81.23 | 4 | 3 | 294.4667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 2505 NW.49 | CMI_PLANNED | YES | NO | NO | 862209 | 168375 | 148532 | 7757 | 888 | 0.00034153 | 4.6392e-06 | 73.6167 | 1 | 308 | Load | 35773 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2022
J2002.006066 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7431 | 847431 | 2020-02-18 10:19 | 2020-02-18 11:12 | 52.97 | 5 | 6 | 226.6667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 3308 N.LINDSAY | CMI_PLANNED | YES | NO | NO | 862209 | 168375 | 148532 | 6173 | 374 | 0.00026289 | 5.7991e-06 | 45.3333 | 1 | 310 | Load | 12516 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2022
J2002.006067 | PD-02182020-00279 | METRO WEST | WEST | 8150:HOBBY LOBBY | HOBBY_LOBBY_5061 | 815061 | 2020-02-18 10:23 | 2020-02-18 11:54 | 90.77 | 1 | 1 | 35.4035 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 7649 SW 34 | CMI_NORMAL | NO | NO | NO | 862209 | 129031 | 116230 | 2512 | 1656 | 4.1061e-05 | 1.1598e-06 | 35.4035 | 1 | 310 | Customer | 53606 | Load | TranOpenDelta | STEVEN GILES | 405-227-2802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006068 | PD-02182020-00274 | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-02-18 10:28 | 2020-02-18 12:53 | 145.15 | 1 | 1 | 145.15 | 25 | LIGHTNING | 23 | FUSE - PRIMARY | MOUNTAINBURG | HWY 71 NW OF HL17/6 500 | CMI_NORMAL | NO | NO | NO | 862209 | 82366 | 61285 | 3793 | 2586 | 0.00016835 | 1.1598e-06 | 145.15 | 1 | 310 | Customer | 16542 | Load | Tran3phWye | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Weather | N | DISTRIBUTION | 161kV | 2020-02-18 | 2020 |  | Ark - Series 2
J2002.006081 | PD-02182020-00305 | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6124 | 836124 | 2020-02-18 10:55 | 2020-02-18 13:15 | 140.42 | 1 | 2 | 90.6 | 29 | TREES : GROW IN | 31 | CONDUCTOR SERVICE - OH | OKLAHOMA CITY | 1611 NW.29 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862209 | 168375 | 148532 | 11118 | 1768 | 0.00010508 | 1.1598e-06 | 90.6 | 1 | 310 | Customer | 14145 | Load | Tran1phOH | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2020
J2002.006083 |  | METRO NORTH | GUTHRIE | 8814:PINE STREET | PINE_STREET_1429 | 881429 | 2020-02-18 10:59 | 2020-02-18 11:23 | 23.43 | 1 | 1 | 23.4333 | 1 | CANCELLED | 57 | CANCELLED | GUTHRIE | N OF HWY 105 3/4M E OF VET COR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 168375 | 19843 | 3106 | 1715 | 2.7178e-05 | 1.1598e-06 | 23.4333 | 1 | 310 | Customer | 72607 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006082 |  | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_722 | 870722 | 2020-02-18 10:59 | 2020-02-18 12:18 | 78.32 | 11 | 3 | 734.0667 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | NORMAN | 2112 BOIS-DE-ARC CI | CMI_PLANNED | YES | NO | NO | 862209 | 159311 | 57047 | 11838 | 1582 | 0.00085138 | 1.2758e-05 | 66.7333 | 1 | 308 | Load | 56757 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006087 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6924 | 846924 | 2020-02-18 11:06 | 2020-02-18 11:06 | 0 | 1144 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | OKLAHOMA CITY | 401 NE 122ND ST | CMI_MOMENTARY | YES | NO | NO | 862209 | 168375 | 148532 | 7733 | 1144 | 0 | 0.0013268 | 0 | 1 | 0 | Feeder | MEMORIAL_6924 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006088 | PD-02182020-00317 | METRO EAST | SEMINOLE | 7312:JUMPER CREEK | JUMPER_CREEK_1225 | 731225 | 2020-02-18 11:06 | 2020-02-18 11:29 | 23.22 | 1 | 1 | 23.2167 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | KONAWA | SWAN CAESAR | CMI_NORMAL | NO | NO | NO | 862209 | 114534 | 13627 | 1217 | 332 | 2.6927e-05 | 1.1598e-06 | 23.2167 | 1 | 310 | Load | 7700 | Load | TranOpenDelta | BRADY A HUFF | 405-519-0701 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | OK - 2021
J2002.006089 |  | SOUTHERN | MADILL | 5907:RUSSETT | RUSSETT_764 | 590764 | 2020-02-18 11:07 | 2020-02-18 13:44 | 156.98 | 1 | 1 | 139.2167 | 4 | DETERIORATION | 12 | POLE | TISHOMINGO | S OK HWY 22 | CMI_PLANNED | YES | NO | NO | 862209 | 77728 | 7204 | 2191 | 1672 | 0.00016147 | 1.1598e-06 | 139.2167 | 1 | 308 | Load | 5374 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006096 |  | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3629 | 833629 | 2020-02-18 11:28 | 2020-02-18 12:35 | 67.33 | 78 | 55 | 4134 | 4 | DETERIORATION | 28 | CROSSARM | THE VILLAGE | GREYSTONE+WHITEHAVEN | CMI_PLANNED | YES | NO | NO | 862209 | 168375 | 148532 | 8792 | 1400 | 0.0047947 | 9.0465e-05 | 53 | 1 | 310 | Tap | 21333 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006099 |  | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_626 | 550626 | 2020-02-18 11:34 | 2020-02-18 12:04 | 30.3 | 1 | 1 | 30.3 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DURANT | 1902 W MISSISSIPPI | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 77728 | 15524 | 6752 | 1006 | 3.5142e-05 | 1.1598e-06 | 30.3 | 1 | 310 | Customer | 15628 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006100 | PD-02182020-00357 | METRO WEST | WEST | 8360:WOODLAWN | WOODLAWN_6023 | 836023 | 2020-02-18 11:35 | 2020-02-18 16:31 | 296.28 | 1 | 1 | 296.2833 | 13 | PREMATURE FAILURE | 31 | CONDUCTOR SERVICE - OH | BETHANY | 5414 N.ROCKWELL | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862209 | 129031 | 116230 | 5509 | 1480 | 0.00034363 | 1.1598e-06 | 296.2833 | 1 | 320 | Customer | 30031 | Load | TranOH3phDelta | JESSE PHILLER | 405-512-8086 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | OK - 2022
J2002.006101 | PD-02182020-00360 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2261 | 852261 | 2020-02-18 11:39 | 2020-02-18 17:08 | 329.05 | 1 | 2 | 323.0667 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 3244 SOMERSET FARMS RD | CMI_NORMAL | NO | NO | NO | 862209 | 114534 | 71277 | 11649 | 3539 | 0.0003747 | 1.1598e-06 | 323.0667 | 1 | 310 | Customer | 175758 | Load | Tran1phPad | JEREMIAH D WALKER | 405-974-0464 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006103 |  | METRO EAST | SHAWNEE | 7412:PEARSON | PEARSON 21 | 741221 | 2020-02-18 11:45 | 2020-02-18 17:19 | 334.5 | 5 | 1 | 539.0833 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | ASHER | 3 1/8MW ASHER ON HWY39 | CMI_PLANNED | YES | NO | NO | 862209 | 114534 | 22147 | 678 | 678 | 0.00062524 | 5.7991e-06 | 107.8167 | 1 | 310 | Tap | 2671 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | OK - 2021
J2002.006107 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1522 | 921522 | 2020-02-18 11:50 | 2020-02-18 12:19 | 28.82 | 1 | 1 | 24.9189 | 5 | ELECTRICAL TRACKING | 1 | TRANSFORMER UG | CHARLESTON | EAST GATE DR | CMI_PLANNED | YES | NO | NO | 862209 | 82366 | 61285 | 962 | 471 | 2.8901e-05 | 1.1598e-06 | 24.9189 | 1 | 310 | Customer | 14425 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-18 | 2020 |  | Ark - Series 2
J2002.006112 | PD-02182020-00375 | METRO SOUTH | SOUTH CENTRAL | 8151:PENNSYLVANIA | PENNSYLVANIA_5121 | 815121 | 2020-02-18 11:56 | 2020-02-18 13:47 | 110.68 | 1 | 1 | 13.1888 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 3028 SW 100TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 159311 | 102264 | 13944 | 1998 | 1.5296e-05 | 1.1598e-06 | 13.1888 | 1 | 310 | Customer | 71824 | Load | Tran1phPad | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006116 | PD-02182020-00389 | METRO NORTH | NORTH | 8336:TENNESSEE | TENNESSEE_3629 | 833629 | 2020-02-18 11:58 | 2020-02-18 13:30 | 91.57 | 1 | 1 | 91.5667 | 22 | WIND | 31 | CONDUCTOR SERVICE - OH | THE VILLAGE | 1821 CHURCHILL WAY | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862209 | 168375 | 148532 | 8792 | 1400 | 0.0001062 | 1.1598e-06 | 91.5667 | 1 | 320 | Customer | 8223 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006114 |  | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4024 | 914024 | 2020-02-18 12:00 | 2020-02-18 14:52 | 171.72 | 3 | 3 | 478.05 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 2401 S.TULSA | CMI_PLANNED | YES | NO | NO | 862209 | 82366 | 61285 | 4724 | 1167 | 0.00055445 | 3.4794e-06 | 159.35 | 1 | 308 | Load | 3078 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-18 | 2020 |  | Ark - Series 2
J2002.006120 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-18 12:12 | 2020-02-18 14:52 | 160.02 | 3 | 2 | 470.45 | 4 | DETERIORATION | 2 | TRANSFORMER OH | POCOLA | 8200 STATELINE ROAD | CMI_PLANNED | YES | NO | NO | 862209 | 82366 | 61285 | 1458 | 1240 | 0.00054563 | 3.4794e-06 | 156.8167 | 1 | 308 | Load | 5095 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | Ark - Series 2
J2002.006135 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6128 | 836128 | 2020-02-18 12:50 | 2020-02-18 15:11 | 140.87 | 10 | 7 | 1355.5 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 508 NW.40 | CMI_PLANNED | YES | NO | NO | 862209 | 168375 | 148532 | 11118 | 958 | 0.0015721 | 1.1598e-05 | 135.55 | 1 | 310 | Load | 12506 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2021
J2002.006140 |  | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1122 | 511122 | 2020-02-18 13:14 | 2020-02-18 13:40 | 26.6 | 1 | 1 | 26.5988 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | DICKSON | Dickson Rd & Mockingbird .5W .7N WS | CMI_PLANNED | YES | NO | NO | 862209 | 77728 | 23612 | 2210 | 1207 | 3.085e-05 | 1.1598e-06 | 26.5988 | 1 | 310 | Load | 352516 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006141 | PD-02182020-00495 | SOUTHERN | ADA | 5808:HARDEN CITY | HARDEN_CITY_823 | 580823 | 2020-02-18 13:15 | 2020-02-18 16:24 | 188.67 | 1 | 1 | 188.6667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FITTSTOWN | SOUTH OF PHOTO STUDIO | CMI_NORMAL | NO | NO | NO | 862209 | 77728 | 11525 | 106 | 104 | 0.00021882 | 1.1598e-06 | 188.6667 | 1 | 310 | Load | 21096 | Load | Tran1phOH | CAMERON BRADY | 580-307-7052 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006142 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7422 | 847422 | 2020-02-18 13:16 | 2020-02-18 13:44 | 28.33 | 1 | 1 | 11.65 | 13 | PREMATURE FAILURE | 1 | TRANSFORMER UG | OKLAHOMA CITY | 706 NE.27 | CMI_PLANNED | YES | NO | NO | 862209 | 168375 | 148532 | 6173 | 1215 | 1.3512e-05 | 1.1598e-06 | 11.65 | 1 | 310 | Customer | 23852 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2022
J2002.006143 | PD-02182020-00466 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3721 | 833721 | 2020-02-18 13:17 | 2020-02-18 16:31 | 194.47 | 1 | 2 | 179.5333 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 432 NW.84 | CMI_NORMAL | NO | NO | NO | 862209 | 168375 | 148532 | 5769 | 725 | 0.00020822 | 1.1598e-06 | 179.5333 | 1 | 310 | Customer | 59305 | Load | Tran1phOH | TONY J ILG | 405-714-7441 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2022
J2002.006160 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1223 | 831223 | 2020-02-18 13:18 | 2020-02-18 13:49 | 30.45 | 3 | 4 | 53.5 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 625 NW.54 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 168375 | 148532 | 7757 | 634 | 6.205e-05 | 3.4794e-06 | 17.8333 | 1 | 310 | Load | 8462 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006144 |  | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2134 | 862134 | 2020-02-18 13:19 | 2020-02-18 17:13 | 234.25 | 1 | 1 | 212.1333 | 4 | DETERIORATION | 12 | POLE | OKLAHOMA CITY | .5ME HIWASSEE N SE104 | CMI_PLANNED | YES | NO | NO | 862209 | 159311 | 57047 | 4239 | 1005 | 0.00024603 | 1.1598e-06 | 212.1333 | 1 | 308 | Tap | 14274 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006150 | PD-02182020-00505 | SOUTHERN | ARDMORE | 5111:DRIPPING SPRINGS | DRIPPING_SPRI_1122 | 511122 | 2020-02-18 13:25 | 2020-02-18 17:10 | 225 | 1 | 1 | 221.6167 | 11 | OVERLOAD | 2 | TRANSFORMER OH | DICKSON | 2.75 S OF DICKSON | CMI_NORMAL | NO | NO | NO | 862209 | 77728 | 23612 | 2210 | 1207 | 0.00025703 | 1.1598e-06 | 221.6167 | 1 | 310 | Customer | 21332 | Load | Tran1phOH | CHRIS CLOSE | 405-238-0419 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006162 |  | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_622 | 770622 | 2020-02-18 13:35 | 2020-02-18 14:01 | 25.42 | 11 | 4 | 279.6147 | 11 | OVERLOAD | 23 | FUSE - PRIMARY | BRISTOW | 7.5MN BRSTOW ON HWY48 | CMI_PLANNED | YES | NO | NO | 862209 | 74159 | 40834 | 3786 | 2012 | 0.0003243 | 1.2758e-05 | 25.4195 | 1 | 310 | Tap | 5196 | Fuse | FuseOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | #N/A
J2002.006166 | PD-02182020-00509 | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2223 | 882223 | 2020-02-18 13:42 | 2020-02-18 14:53 | 70.95 | 1 | 1 | 70.95 | 12 | POOR CONNECTION | 50 | CONNECTOR | EDMOND | 6250 INDUSTRAIL BLVD | CMI_NORMAL | NO | NO | NO | 862209 | 168375 | 19843 | 5389 | 1202 | 8.2289e-05 | 1.1598e-06 | 70.95 | 1 | 310 | Load | 304794 | Load | Tran3phWye | KIRK REILLEY | 405-550-3062 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006170 | PD-02182020-00571 | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_622 | 410622 | 2020-02-18 13:49 | 2020-02-18 15:25 | 96.15 | 1 | 2 | 89.2167 | 4 | DETERIORATION | 50 | CONNECTOR | ENID | 2700 N.VANBUREN | CMI_NORMAL | NO | NO | NO | 862209 | 53606 | 37643 | 6033 | 1513 | 0.00010347 | 1.1598e-06 | 89.2167 | 1 | 310 | Customer | 8859 | Load | Tran1phOH | BRANDON T BAIRD | 580-231-7484 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | #N/A
J2002.006169 | PD-02182020-00556 | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-18 13:54 | 2020-02-18 15:20 | 85.7 | 1 | 2 | 73.3333 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | CLARKSVILLE | 1/2MS+1/4MW-EUREKA BRICK PLANT | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 82366 | 7554 | 731 | 0 | 8.5053e-05 | 1.1598e-06 | 73.3333 | 1 | 310 | Load | 3379 | Load | Tran1phOH | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | #N/A
J2002.006171 | PD-02182020-00557 | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6333 | 816333 | 2020-02-18 14:05 | 2020-02-18 14:33 | 27.88 | 1 | 1 | 27.8833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | MOORE | 900 NW.1 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 159311 | 102264 | 11849 | 1230 | 3.2339e-05 | 1.1598e-06 | 27.8833 | 1 | 310 | Customer | 20801 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2022
J2002.006174 | PD-02182020-00581 | METRO WEST | WEST | 8359:YUKON | YUKON_5921 | 835921 | 2020-02-18 14:06 | 2020-02-18 18:29 | 262.52 | 16 | 9 | 4189.6 | 3 | DAMAGED BY PUBLIC | 36 | CONDUCTOR PRIMARY - UG | YUKON | 1029 WALSH LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 129031 | 116230 | 6438 | 1819 | 0.0048591 | 1.8557e-05 | 261.85 | 1 | 310 | Load | 58436 | Load | Tran1phPad | JESSE PHILLER | 405-512-8086 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | #N/A
J2002.006181 | PD-02182020-00610 | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1371 | 831371 | 2020-02-18 14:33 | 2020-02-18 18:43 | 250.18 | 1 | 1 | 247.0667 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | YUKON | .5MN FORMAN .5MWFRISC | CMI_NORMAL | NO | NO | NO | 862209 | 129031 | 116230 | 7923 | 3798 | 0.00028655 | 1.1598e-06 | 247.0667 | 1 | 310 | Load | 53805 | Load | Tran1phOH | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006188 | PD-02182020-00616 | SOUTHERN | MADILL | 5906:TISHOMINGO | TISHOMINGO_621 | 590621 | 2020-02-18 14:40 | 2020-02-18 16:33 | 113 | 1 | 1 | 113 | 27 | TREE:NON PREVENTABLE | 12 | POLE | TISHOMINGO | Refuge Headquarters | CMI_NORMAL | NO | NO | NO | 862209 | 77728 | 7204 | 967 | 916 | 0.00013106 | 1.1598e-06 | 113 | 1 | 310 | Customer | 383687 | Load | Tran1phPad | CHRIS CLOSE | 405-238-0419 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2021
J2002.006272 | PD-02182020-00619 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3731 | 833731 | 2020-02-18 14:46 | 2020-02-18 22:00 | 433.98 | 8 | 5 | 3421.0667 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | THE VILLAGE | 9225 N.PENN PL | CMI_NORMAL | NO | NO | NO | 862209 | 168375 | 148532 | 5769 | 1903 | 0.0039678 | 9.2785e-06 | 427.6333 | 1 | 310 | Mainline | 32133 | Fuse | FuseRiser | TOMMY D ROBERTSON | 405-696-6476 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2020
J2002.006197 | PD-02182020-00643 | SOUTHERN | HEALDTON | 5306:COUNTY LINE | COUNTY LINE 22 | 530622 | 2020-02-18 14:56 | 2020-02-18 18:26 | 210.18 | 1 | 1 | 183.15 | 28 | OTHER (DESCRIBE) | 23 | FUSE - PRIMARY | TATUMS | TM .1E .5N .4E NS | CMI_NORMAL | NO | NO | NO | 862209 | 77728 | 6811 | 757 | 415 | 0.00021242 | 1.1598e-06 | 183.15 | 1 | 310 | Load | 228781 | Load | TranOH3phDelta | JUSTIN B MARSHALL | 580-221-5051 | [5 empty] | Other | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | #N/A
J2002.006201 |  | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_422 | 510422 | 2020-02-18 15:02 | 2020-02-18 15:05 | 2.67 | 1 | 1 | 2.6667 | 1 | CANCELLED | 57 | CANCELLED | ARDMORE | S OF VO-TECH SCH | CMI_MOMENTARY | YES | NO | NO | 862209 | 77728 | 23612 | 2320 | 1058 | 3.0928e-06 | 1.1598e-06 | 2.6667 | 1 | 310 | Load | 15993 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006200 | PD-02182020-00640 | NORTHEAST | MUSKOGEE | 3117:THREE RIVERS | THREE_RIVERS_1721 | 311721 | 2020-02-18 15:02 | 2020-02-18 16:34 | 91.65 | 1 | 2 | 91.65 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | MUSKOGEE | 2220 ELMIRA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 74159 | 33325 | 2835 | 1047 | 0.0001063 | 1.1598e-06 | 91.65 | 1 | 320 | Customer | 3479 | Load | Tran1phOH | JAMES C EVANS | 918-869-1174 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-18 | 2020 |  | #N/A
J2002.006202 | PD-02182020-00655 | METRO EAST | SHAWNEE | 7412:PEARSON | PEARSON 21 | 741221 | 2020-02-18 15:05 | 2020-02-18 16:27 | 82.2 | 1 | 1 | 82.2 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ASHER | 3 3/4MS EMAHAKA SUB ON HWY 56 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 114534 | 22147 | 678 | 678 | 9.5337e-05 | 1.1598e-06 | 82.2 | 1 | 310 | Load | 90413 | Load | 0 | BRYAN K TATUM | 405-659-0746 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | OK - 2021
J2002.006205 | PD-02182020-00657 | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_871 | 830871 | 2020-02-18 15:21 | 2020-02-18 19:14 | 233.02 | 1 | 2 | 218.45 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | NW.192 + SADDLE RIVER DR | CMI_NORMAL | NO | NO | NO | 862209 | 168375 | 148532 | 19430 | 4256 | 0.00025336 | 1.1598e-06 | 218.45 | 1 | 321 | Load | 85586 | Load | Tran1phOH | TOMMY D ROBERTSON | 405-696-6476 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2021
J2002.006221 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7423 | 847423 | 2020-02-18 15:58 | 2020-02-18 16:06 | 8.85 | 1 | 1 | 8.85 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1000 NE.20 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 168375 | 148532 | 6173 | 1296 | 1.0264e-05 | 1.1598e-06 | 8.85 | 1 | 311 | Customer | 899 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2022
J2002.006223 | PD-02182020-00716 | NORTHEAST | SAPULPA | 3210:HICKORY HILL | HICKORY_HILL_1024 | 321024 | 2020-02-18 16:01 | 2020-02-18 17:04 | 62.87 | 7 | 6 | 349.65 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | SAPULPA | 1126 E.DAVIS | CMI_NORMAL | NO | NO | NO | 862209 | 74159 | 40834 | 2684 | 1247 | 0.00040553 | 8.1187e-06 | 49.95 | 1 | 310 | Load | 47362 | Load | Tran1phPad | NORTHEAST BOUG | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2022
J2002.006224 | PD-02182020-00719 | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1822 | 931822 | 2020-02-18 16:09 | 2020-02-18 18:02 | 112.97 | 2 | 3 | 213.05 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | ALMA | 111 COUNTRY LANE DR, ALMA | CMI_NORMAL | NO | NO | NO | 862209 | 82366 | 61285 | 2851 | 787 | 0.0002471 | 2.3196e-06 | 106.525 | 1 | 310 | Secondary | 4318 | Load | Tran1phPad | GEORGE N WORKMAN | 479-459-0918 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | Ark - Series 2
J2002.006222 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-18 16:13 | 2020-02-18 18:42 | 149.02 | 1 | 0 | 149.0322 | 4 | DETERIORATION | 2 | TRANSFORMER OH | POCOLA | ST HWY 112 & REITER LN | CMI_PLANNED | YES | NO | NO | 862209 | 82366 | 61285 | 1458 | 1240 | 0.00017285 | 1.1598e-06 | 149.0322 | 1 | 0 | Load | 13943 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | Ark - Series 2
J2002.006225 |  | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3223 | 813223 | 2020-02-18 16:17 | 2020-02-18 16:49 | 31.83 | 1 | 2 | 31.8333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2345 SW.41 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 159311 | 102264 | 7610 | 2462 | 3.6921e-05 | 1.1598e-06 | 31.8333 | 1 | 310 | Customer | 25614 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | #N/A
J2002.006234 | PD-02182020-00765 | METRO EAST | CHANDLER | 7104:BELLCOW | BELLCOW_421 | 710421 | 2020-02-18 16:26 | 2020-02-19 00:45 | 499.07 | 2 | 4 | 1000.1333 | 4 | DETERIORATION | 28 | CROSSARM | CHANDLER | 1S 2E CHANDLER | CMI_NORMAL | NO | NO | NO | 862209 | 114534 | 7483 | 2828 | 1172 | 0.00116 | 2.3196e-06 | 500.0667 | 1 | 310 | Load | 2819 | Load | Tran1phOH | JEREMIAH D WALKER | 405-974-0464 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2021
J2002.006226 | PD-02182020-00736 | METRO SOUTH | SOUTH | 8707:WILKINSON | WILKINSON_722 | 870722 | 2020-02-18 16:26 | 2020-02-18 18:24 | 117.82 | 1 | 1 | 117.8167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | NORMAN | 1033 E IMHOFF | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 159311 | 57047 | 11838 | 1582 | 0.00013665 | 1.1598e-06 | 117.8167 | 1 | 310 | Customer | 254068 | Load | Tran3phPadWye | THOMAS E COLE | 405-623-9338 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006227 | PD-02182020-00727 | NORTHWEST | ENID | 4106:HEMLOCK | HEMLOCK_622 | 410622 | 2020-02-18 16:26 | 2020-02-18 17:18 | 51.75 | 1 | 1 | 51.75 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ENID | 2213 N.INDEPENDENCE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 53606 | 37643 | 6033 | 1513 | 6.002e-05 | 1.1598e-06 | 51.75 | 1 | 310 | Customer | 5335 | Load | Tran1phOH | WILLIAM R PETHICK | 580-278-8129 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | #N/A
J2002.006230 | PD-02182020-00733 | METRO NORTH | GUTHRIE | 8822:WATERLOO | WATERLOO_2223 | 882223 | 2020-02-18 16:31 | 2020-02-18 20:37 | 245.78 | 1 | 1 | 239.1333 | 15 | SQUIRREL | 23 | FUSE - PRIMARY | EDMOND | TRACT 12 KANALY ADD | CMI_NORMAL | NO | NO | NO | 862209 | 168375 | 19843 | 5389 | 1202 | 0.00027735 | 1.1598e-06 | 239.1333 | 1 | 310 | Load | 32409 | Load | Tran1phOH | PETER BILICKI | 619-726-8332 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006232 | PD-02182020-00732 | METRO WEST | WEST | 8313:HAYMAKER | HAYMAKER_1371 | 831371 | 2020-02-18 16:35 | 2020-02-18 19:47 | 192.08 | 1 | 1 | 186.2667 | 13 | PREMATURE FAILURE | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 11112 fairways ave | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862209 | 129031 | 116230 | 7923 | 3798 | 0.00021603 | 1.1598e-06 | 186.2667 | 1 | 310 | Customer | 247329 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006233 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-18 16:42 | 2020-02-18 21:12 | 270.58 | 2 | 1 | 500.8333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 6705 US HWY 271 | CMI_PLANNED | YES | NO | NO | 862209 | 82366 | 61285 | 1458 | 1240 | 0.00058087 | 2.3196e-06 | 250.4167 | 1 | 308 | Load | 5924 | Load | TranOHDeltaSplitBank | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | Ark - Series 2
J2002.006238 | PD-02182020-00753 | SOUTHERN | DURANT | 5506:BODLE | BODLE_STREET_626 | 550626 | 2020-02-18 16:49 | 2020-02-18 17:52 | 62.97 | 1 | 1 | 61.95 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | DURANT | 1902 W MISSISSIPPI | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 77728 | 15524 | 6752 | 1006 | 7.185e-05 | 1.1598e-06 | 61.95 | 1 | 310 | Customer | 15628 | Load | Tran1phOH | JUSTIN MARSHALL | 580-504-0986 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006241 |  | METRO EAST | SEMINOLE | 7306:FIXICO | FIXICO_629 | 730629 | 2020-02-18 17:06 | 2020-02-18 18:17 | 71.23 | 1 | 1 | 71.2333 | 1 | CANCELLED | 57 | CANCELLED | SEMINOLE | 2215 HWY 9 W(TERRACE VIEW APT) | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 114534 | 13627 | 4074 | 568 | 8.2617e-05 | 1.1598e-06 | 71.2333 | 1 | 310 | Customer | 12376 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2021
J2002.006243 |  | METRO WEST | WEST | 8158:SARA | SARA_5862 | 815862 | 2020-02-18 17:08 | 2020-02-18 17:18 | 9.62 | 1 | 1 | 9.6167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 6613 Bent Wood Villas Dr | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 129031 | 116230 | 18297 | 3620 | 1.1154e-05 | 1.1598e-06 | 9.6167 | 1 | 310 | Customer | 318027 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2022
J2002.006248 | PD-02182020-00754 | NORTHEAST | SAPULPA | 3213:BOWDEN | BOWDEN_1329 | 321329 | 2020-02-18 17:25 | 2020-02-18 18:26 | 60.83 | 1 | 1 | 53.9667 | 12 | POOR CONNECTION | 50 | CONNECTOR | SAPULPA | 13070 W 81ST STREET | CMI_NORMAL | NO | NO | NO | 862209 | 74159 | 40834 | 3379 | 1517 | 6.2591e-05 | 1.1598e-06 | 53.9667 | 1 | 320 | Load | 238910 | Load | Tran1phOH | CGI ADMIN | 918-261-6802 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2020
J2002.006250 | PD-02182020-00756 | METRO WEST | WEST | 8158:SARA | SARA_5862 | 815862 | 2020-02-18 17:32 | 2020-02-18 18:25 | 52.58 | 1 | 1 | 52.5833 | 14 | SEALED OUT/OPEN | 15 | METER - SECONDARY | OKLAHOMA CITY | 6613 Bent Wood Villas Dr | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 129031 | 116230 | 18297 | 3620 | 6.0987e-05 | 1.1598e-06 | 52.5833 | 1 | 310 | Customer | 318027 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2022
J2002.006252 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-02-18 17:42 | 2020-02-18 18:05 | 22.77 | 5 | 3 | 105.5833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | MOUNTAINBURG | 1310 Pidgeon Creek Rd | CMI_PLANNED | YES | NO | NO | 862209 | 82366 | 61285 | 3793 | 2586 | 0.00012246 | 5.7991e-06 | 21.1167 | 1 | 308 | Load | 7838 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-18 | 2020 |  | Ark - Series 2
J2002.006253 |  | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1524 | 811524 | 2020-02-18 17:47 | 2020-02-18 18:04 | 17.1 | 1 | 1 | 17.1 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1428 SW.25 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 159311 | 102264 | 6073 | 2074 | 1.9833e-05 | 1.1598e-06 | 17.1 | 1 | 310 | Customer | 1418 | Load | TranOpenDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | OK - 2022
J2002.006257 | PD-02182020-00758 | SOUTHERN | MADILL | 5408:CANEY CREEK | CANEY_CREEK_831 | 540831 | 2020-02-18 17:58 | 2020-02-18 18:38 | 39.7 | 1 | 1 | 39.7 | 29 | TREES : GROW IN | 34 | CONDUCTOR SECONDARY - OH | KINGSTON | KINGSTON OK 73439 | CMI_NORMAL | NO | NO | NO | 862209 | 77728 | 7204 | 1054 | 630 | 4.6045e-05 | 1.1598e-06 | 39.7 | 1 | 320 | Customer | 3344 | Load | Tran1phOH | DAVID TAYLOR | 580-574-4517 | [5 empty] | Vegetation | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006258 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4022 | 834022 | 2020-02-18 17:59 | 2020-02-18 18:05 | 5.98 | 1 | 1 | 5.9833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 9224 LANSBROOK LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 129031 | 116230 | 10846 | 1369 | 6.9395e-06 | 1.1598e-06 | 5.9833 | 1 | 310 | Customer | 38531 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006260 | PD-02182020-00759 | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4022 | 834022 | 2020-02-18 18:17 | 2020-02-18 22:27 | 249.82 | 1 | 1 | 249.8167 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 9224 LANSBROOK LN | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862209 | 129033 | 116230 | 10846 | 1369 | 0.00028974 | 1.1598e-06 | 249.8167 | 1 | 315 | Customer | 38531 | Load | Tran1phPad | TONY J ILG | 405-714-7441 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006264 | PD-02182020-00762 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2022 | 862022 | 2020-02-18 18:49 | 2020-02-18 20:13 | 84.17 | 1 | 2 | 29.4 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 1033 SE.39 | CMI_NORMAL | NO | NO | NO | 862209 | 159306 | 102262 | 4762 | 1556 | 3.4098e-05 | 1.1598e-06 | 29.4 | 1 | 320 | Customer | 12503 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006265 |  | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2029 | 862029 | 2020-02-18 18:51 | 2020-02-18 21:15 | 144.4 | 9 | 9 | 1232.85 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 726 SE 28TH ST | CMI_PLANNED | YES | NO | NO | 862209 | 159306 | 102262 | 4762 | 986 | 0.0014299 | 1.0438e-05 | 136.9833 | 1 | 310 | Load | 1832 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006271 | PD-02182020-00767 | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5824 | 845824 | 2020-02-18 19:23 | 2020-02-18 23:28 | 244.68 | 1 | 1 | 240.5333 | 11 | OVERLOAD | 2 | TRANSFORMER OH | JONES | 14701 HOGBACK RD., JONES | CMI_NORMAL | NO | NO | NO | 862209 | 114533 | 71275 | 2988 | 862 | 0.00027897 | 1.1598e-06 | 240.5333 | 1 | 310 | Load | 178806 | Load | Tran1phOH | JEREMIAH D WALKER | 405-974-0464 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-18 | 2020 |  | #N/A
J2002.006275 | PD-02182020-00768 | METRO NORTH | GUTHRIE | 8806:COTTONWOOD CR | COTTONWOOD_CK_621 | 880621 | 2020-02-18 19:45 | 2020-02-18 23:17 | 211.62 | 1 | 1 | 211.6167 | 1 | CANCELLED | 57 | CANCELLED | GUTHRIE | GUTHRIE><1E-77,1/4S PRARIE GRV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 168379 | 19843 | 5175 | 1882 | 0.00024544 | 1.1598e-06 | 211.6167 | 1 | 320 | Load | 61616 | Load | Tran1phOH | KELLEY D WATSON | 405-763-8148 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006276 |  | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2029 | 862029 | 2020-02-18 19:57 | 2020-02-18 21:14 | 77.6 | 1 | 1 | 71.1667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 705 SE 29TH ST | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 159306 | 102262 | 4762 | 986 | 8.254e-05 | 1.1598e-06 | 71.1667 | 1 | 310 | Customer | 48161 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006280 | PD-02182020-00772 | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6222 | 866222 | 2020-02-18 20:15 | 2020-02-18 21:58 | 102.57 | 1 | 1 | 90.1667 | 25 | LIGHTNING | 30 | CONDUCTOR SERVICE - UG | CHOCTAW | 13501 SE.29 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862209 | 114533 | 71275 | 7214 | 1901 | 0.00010458 | 1.1598e-06 | 90.1667 | 1 | 320 | Customer | 40457 | Load | Tran1phPad | JEREMIAH D WALKER | 405-974-0464 | [5 empty] | Weather | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006282 | PD-02182020-00775 | METRO EAST | CHANDLER | 7119:WARWICK | WARWICK_1942 | 711942 | 2020-02-18 20:33 | 2020-02-18 21:52 | 78.93 | 1 | 1 | 71.2667 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | CARNEY | SEWER LAGOON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 114533 | 7482 | 2425 | 958 | 8.2656e-05 | 1.1598e-06 | 71.2667 | 1 | 310 | Customer | 15909 | Load | TranOpenDelta | KELLEY D WATSON | 405-763-8148 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2022
J2002.006285 |  | METRO NORTH | NORTH | 8398:CHISHOLM CREEK | CHISHOLM_CREEK_9869 | 839869 | 2020-02-18 21:01 | 2020-02-18 21:07 | 6.43 | 1 | 1 | 6.4333 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | Silver Hawk Sec 2 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862209 | 168379 | 148536 | 10669 | 3003 | 7.4615e-06 | 1.1598e-06 | 6.4333 | 1 | 310 | Customer | 257745 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | OK - 2022
J2002.006298 | PD-02182020-00784 | METRO SOUTH | SOUTH | 8621:DRAPER LAKE | DRAPER_LAKE_2171 | 862171 | 2020-02-18 23:13 | 2020-02-19 01:13 | 119.98 | 1 | 2 | 119.9833 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | OKLAHOMA CITY | 18536 SE.104 | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862209 | 159306 | 57044 | 4237 | 3068 | 0.00013916 | 1.1598e-06 | 119.9833 | 1 | 320 | Load | 78851 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-18 | 2020 |  | #N/A
J2002.006314 | PD-02192020-00024 | METRO EAST | SHAWNEE | 7410:MAUD TAP | MAUD_TAP_1022 | 741022 | 2020-02-19 04:25 | 2020-02-19 09:33 | 307.8 | 1 | 2 | 303.1 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | MAUD | 1MNW MAUD ON 9A 1ST POLE N | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862195 | 114533 | 22147 | 1020 | 257 | 0.00035154 | 1.1598e-06 | 303.1 | 1 | 310 | Load | 10919 | Load | Tran1phOH | DAVID M CLEMMONS | 405-777-8355 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006327 |  | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3722 | 913722 | 2020-02-19 07:01 | 2020-02-19 07:46 | 44.65 | 1 | 1 | 44.65 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 5801 KINKEAD AV HLD1 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862195 | 82364 | 61282 | 4576 | 1441 | 5.1786e-05 | 1.1598e-06 | 44.65 | 1 | 310 | Customer | 20 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | Ark - Series 3
J2002.006337 |  | SOUTHERN | ARDMORE | 5125:LONE GROVE | LONE_GROVE_2524 | 512524 | 2020-02-19 08:08 | 2020-02-19 15:31 | 442.67 | 3 | 1 | 1317.5 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | LONE GROVE | W CASE RD .5N HWY 70 | CMI_PLANNED | YES | NO | NO | 862195 | 77726 | 23612 | 3309 | 1002 | 0.0015281 | 3.4795e-06 | 439.1667 | 1 | 308 | Load | 29792 | Load | TranOpenDelta | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006338 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7029 | 817029 | 2020-02-19 08:11 | 2020-02-19 09:53 | 102.5 | 3 | 2 | 169.35 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 9625 S.SHIELDS | CMI_PLANNED | YES | NO | NO | 862195 | 159306 | 102262 | 9937 | 1756 | 0.00019642 | 3.4795e-06 | 56.45 | 1 | 308 | Load | 5368 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | OK - 2022
J2002.006349 | PD-02192020-00103 | METRO SOUTH | SOUTH CENTRAL | 8132:KENTUCKY | KENTUCKY_3224 | 813224 | 2020-02-19 08:31 | 2020-02-19 09:28 | 57.27 | 11 | 10 | 590.7 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 1420 SW 58TH ST | CMI_NORMAL | NO | NO | NO | 862195 | 159306 | 102262 | 7610 | 1583 | 0.00068511 | 1.2758e-05 | 53.7 | 1 | 310 | Load | 52844 | Load | Tran1phOH | GERARDO D SOTO | 405-758-6334 | [5 empty] | Animals | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | #N/A
J2002.006344 | PD-02192020-00104 | METRO WEST | WEST | 8335:BETHANY | BETHANY_3526 | 833526 | 2020-02-19 08:34 | 2020-02-19 10:26 | 112.42 | 1 | 1 | 112.4167 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | WARR ACRES | 3631 N MacARTHUR | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862195 | 129033 | 116230 | 7882 | 2063 | 0.00013038 | 1.1598e-06 | 112.4167 | 1 | 310 | Customer | 15310 | Load | TranOH3phDelta | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | #N/A
J2002.006345 |  | ARKANSAS | FORT SMITH | 9117:BARLING | BARLING_1724 | 911724 | 2020-02-19 08:34 | 2020-02-19 14:06 | 331.13 | 7 | 7 | 1497.4911 | 4 | DETERIORATION | 12 | POLE | BARLING | 1211 B LITE | CMI_PLANNED | YES | NO | NO | 862195 | 82364 | 61282 | 4247 | 611 | 0.0017368 | 8.1188e-06 | 213.9273 | 1 | 310 | Load | 11603 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-19 | 2020 |  | #N/A
J2002.006351 | PD-02192020-00126 | METRO WEST | WEST | 8381:DIVISION AVE | DIVISION_8124 | 838124 | 2020-02-19 08:42 | 2020-02-19 11:21 | 158.95 | 1 | 1 | 158.95 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | PRARIE SPRINGS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862195 | 129033 | 116230 | 8966 | 1638 | 0.00018436 | 1.1598e-06 | 158.95 | 1 | 310 | Customer | 88045 | Load | Tran1phPad | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006357 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7422 | 847422 | 2020-02-19 08:53 | 2020-02-19 11:10 | 137.03 | 3 | 1 | 384.8 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 709 NE.20 | CMI_PLANNED | YES | NO | NO | 862195 | 168379 | 148536 | 6173 | 1215 | 0.0004463 | 3.4795e-06 | 128.2667 | 1 | 310 | Load | 9059 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | OK - 2022
J2002.006358 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7422 | 847422 | 2020-02-19 08:53 | 2020-02-19 11:10 | 137.03 | 6 | 5 | 188.8 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 715 NE.20 | CMI_PLANNED | YES | NO | NO | 862195 | 168379 | 148536 | 6173 | 1215 | 0.00021898 | 6.959e-06 | 31.4667 | 1 | 308 | Load | 14591 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | OK - 2022
J2002.006359 |  | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_622 | 770622 | 2020-02-19 08:56 | 2020-02-19 09:56 | 60.23 | 5 | 2 | 181.7917 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | BRISTOW | 5MN-66 ON 48 ES | CMI_PLANNED | YES | NO | NO | 862377 | 74159 | 40832 | 3786 | 2012 | 0.0002108 | 5.7979e-06 | 36.3583 | 1 | 308 | Tap | 6911 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | #N/A
J2002.006360 |  | METRO NORTH | NORTH | 8221:MERIDIAN | MERIDIAN_2122 | 822122 | 2020-02-19 09:04 | 2020-02-19 09:14 | 9.87 | 1 | 1 | 9.8667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 2212 N.TULSA | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 168379 | 148536 | 9254 | 1838 | 1.1441e-05 | 1.1596e-06 | 9.8667 | 1 | 310 | Customer | 10265 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | OK - 2020
J2002.006361 |  | ARKANSAS | FORT SMITH | 9512:ADABELL ROAD | ADABELL_ROAD_1222 | 951222 | 2020-02-19 09:06 | 2020-02-19 13:09 | 242.98 | 65 | 31 | 7427.3333 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | VAN BUREN | HADDEN AND N 8TH ST | CMI_PLANNED | YES | NO | NO | 862377 | 82364 | 61282 | 3126 | 1089 | 0.0086126 | 7.5373e-05 | 114.2667 | 1 | 310 | Tap | 523 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-19 | 2020 |  | Ark - Series 1, Ark - Series 2
J2002.006365 |  | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1421 | 911421 | 2020-02-19 09:12 | 2020-02-19 13:48 | 275.47 | 11 | 10 | 3002.8198 | 4 | DETERIORATION | 37 | CONDUCTOR PRIMARY - OH | FORT SMITH | 2217 N.31, S-WARNER | CMI_PLANNED | YES | NO | NO | 862377 | 82364 | 61282 | 4743 | 1752 | 0.003482 | 1.2755e-05 | 272.9836 | 1 | 310 | Load | 5449 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-19 | 2020 |  | Ark - Series 1
J2002.006372 |  | ARKANSAS | FORT SMITH | 9109:SOUTHSIDE | SOUTHSIDE_921 | 910921 | 2020-02-19 09:29 | 2020-02-19 10:31 | 62.22 | 1 | 1 | 62.2167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 3725 S.32 CIRCLE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 82364 | 61282 | 5016 | 1429 | 7.2146e-05 | 1.1596e-06 | 62.2167 | 1 | 310 | Load | 2702 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | Ark - Series 3
J2002.006371 | PD-02192020-00173 | NORTHWEST | WOODWARD | 4608:WOODWARD DISTR | WOODWARD_DIST_847 | 460847 | 2020-02-19 09:30 | 2020-02-19 10:50 | 80.37 | 1 | 1 | 80.3667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | WOODWARD | 603 17TH WOODWARD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 53601 | 10440 | 1219 | 565 | 9.3192e-05 | 1.1596e-06 | 80.3667 | 1 | 310 | Customer | 10031 | Load | Tran1phOH | ROY L THRASH | 580-334-5371 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006375 |  | ARKANSAS | POTEAU | 3608:MULDROW | MULDROW 21 | 360821 | 2020-02-19 09:31 | 2020-02-19 10:54 | 83.62 | 1 | 1 | 83.6167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MULDROW | 2ND POLE E OF MAIN ON PAYNE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 82364 | 13528 | 2280 | 1229 | 9.6961e-05 | 1.1596e-06 | 83.6167 | 1 | 310 | Customer | 16350 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | #N/A
J2002.006378 |  | METRO EAST | SHAWNEE | 7410:MAUD TAP | MAUD_TAP_1022 | 741022 | 2020-02-19 09:41 | 2020-02-19 09:57 | 15.83 | 1 | 1 | 15.8333 | 1 | CANCELLED | 57 | CANCELLED | MAUD | 1MNW MAUD ON 9A 1ST POLE N | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 114533 | 22147 | 1020 | 257 | 1.836e-05 | 1.1596e-06 | 15.8333 | 1 | 310 | Load | 10919 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006395 |  | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4024 | 914024 | 2020-02-19 09:50 | 2020-02-19 13:49 | 238.52 | 16 | 8 | 3373.0667 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | S. TULSA + S. 28TH | CMI_NORMAL | NO | NO | NO | 862377 | 82364 | 61282 | 4723 | 1167 | 0.0039114 | 1.8553e-05 | 210.8167 | 1 | 310 | Tap | 4900 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-19 | 2020 |  | Ark - Series 2
J2002.006385 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9921 | 829921 | 2020-02-19 09:52 | 2020-02-19 10:10 | 18.27 | 1 | 1 | 18.2667 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 6100 N MACARTHUR PK LN-BLDG 16 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 129033 | 116230 | 9242 | 1637 | 2.1182e-05 | 1.1596e-06 | 18.2667 | 1 | 310 | Customer | 76321 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006386 | PD-02192020-00177 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3729 | 833729 | 2020-02-19 09:54 | 2020-02-19 11:00 | 65.8 | 1 | 2 | 65.8 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1005 NW.87 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 168379 | 148536 | 5769 | 1400 | 7.6301e-05 | 1.1596e-06 | 65.8 | 1 | 310 | Customer | 35597 | Load | Tran1phPad | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | OK - 2021
J2002.006403 |  | ARKANSAS | FORT SMITH | 9140:COLONY | COLONY_4024 | 914024 | 2020-02-19 10:05 | 2020-02-19 13:48 | 222.77 | 8 | 8 | 1754.4 | 4 | DETERIORATION | 2 | TRANSFORMER OH | FORT SMITH | 1723 S.UTICA PL | CMI_PLANNED | YES | NO | NO | 862377 | 82364 | 61282 | 4723 | 1167 | 0.0020344 | 9.2767e-06 | 219.3 | 1 | 308 | Load | 6567 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-19 | 2020 |  | Ark - Series 2
J2002.006394 | PD-02192020-00180 | NORTHWEST | ENID | 4119:GLENWOOD | GLENWOOD_1931 | 411931 | 2020-02-19 10:06 | 2020-02-19 11:06 | 60.45 | 1 | 1 | 26.85 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | ENID | 2910 CONSTITUTION | CMI_NORMAL | NO | NO | NO | 862377 | 53601 | 37640 | 5419 | 986 | 3.1135e-05 | 1.1596e-06 | 26.85 | 1 | 320 | Customer | 13256 | Load | Tran1phPad | C-TSENID1 TOM SEEDORF | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006398 | PD-02192020-00183 | METRO SOUTH | SOUTH CENTRAL | 8620:LIGHTNING CR | LIGHTNING_CRE_2022 | 862022 | 2020-02-19 10:07 | 2020-02-19 16:48 | 400.83 | 95 | 85 | 37765.6667 | 3 | DAMAGED BY PUBLIC | 37 | CONDUCTOR PRIMARY - OH | OKLAHOMA CITY | SSSW39 ES SHIELDS BLVD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 159306 | 102262 | 4762 | 1556 | 0.043793 | 0.00011016 | 397.5333 | 1 | 310 | Mainline | 17819 | Fuse | FuseOH | JESSE PHILLER | 405-512-8086 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006401 | PD-02192020-00204 | METRO NORTH | NORTH | 8352:QUAIL CREEK | QUAIL_CREEK_5221 | 835221 | 2020-02-19 10:12 | 2020-02-19 11:34 | 81.65 | 1 | 1 | 81.65 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 4400 FOXGLOVE LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 168379 | 148536 | 6522 | 1500 | 9.468e-05 | 1.1596e-06 | 81.65 | 1 | 310 | Customer | 53102 | Load | Tran1phPad | ZACHARY J BUCKLEY | 405-818-5023 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006404 | PD-02192020-00186 | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2721 | 872721 | 2020-02-19 10:24 | 2020-02-19 11:21 | 57.08 | 1 | 2 | 57.0833 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | NORMAN | 800 LEXINGTON | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 159306 | 57044 | 6502 | 960 | 6.6193e-05 | 1.1596e-06 | 57.0833 | 1 | 320 | Customer | 52630 | Load | Tran1phPad | MIKE MITCHELL | 405-996-8178 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006407 |  | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-02-19 10:30 | 2020-02-19 10:31 | 1.93 | 4823 | 0 | 9565.6167 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 1401 N SARA RD | CMI_MOMENTARY | YES | NO | NO | 862377 | 129033 | 116230 | 18298 | 4433 | 0.011092 | 0.0055927 | 1.9833 | 1 | 0 | Mainline | SARA_5869T | Switch | SWITCH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | OK - 2022
J2002.006410 |  | METRO WEST | WEST | 8340:SILVER LAKE | SILVER_LAKE_4031 | 834031 | 2020-02-19 10:31 | 2020-02-19 12:24 | 112.48 | 7 | 3 | 754.8333 | 4 | DETERIORATION | 14 | PEDESTAL/J-BOX | OKLAHOMA CITY | 10516 BAYBERRY DR | CMI_PLANNED | YES | NO | NO | 862377 | 129033 | 116230 | 10846 | 1642 | 0.00087529 | 8.1171e-06 | 107.8333 | 1 | 308 | Load | 53062 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006413 |  | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4122 | 814122 | 2020-02-19 10:35 | 2020-02-19 10:41 | 5.63 | 1 | 1 | 5.6333 | 1 | CANCELLED | 57 | CANCELLED | OKLAHOMA CITY | 501 SE.44 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 159306 | 102262 | 5814 | 1274 | 6.5323e-06 | 1.1596e-06 | 5.6333 | 1 | 310 | Load | 39096 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | #N/A
J2002.006414 |  | NORTHEAST | SAPULPA | 3213:BOWDEN | BOWDEN_1323 | 321323 | 2020-02-19 10:38 | 2020-02-19 10:57 | 19.38 | 1 | 1 | 19.3833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | SAPULPA | 614 N.ELIZABETH | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 74159 | 40832 | 3379 | 918 | 2.2477e-05 | 1.1596e-06 | 19.3833 | 1 | 310 | Customer | 45657 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | OK - 2020
J2002.006415 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3829 | 913829 | 2020-02-19 10:40 | 2020-02-19 13:51 | 190.97 | 9 | 10 | 1674.2831 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 1812 S.R | CMI_PLANNED | YES | NO | NO | 862377 | 82364 | 61282 | 2945 | 1191 | 0.0019415 | 1.0436e-05 | 186.0315 | 1 | 310 | Load | 132 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-19 | 2020 |  | Ark - Series 2
J2002.006432 |  | METRO NORTH | NORTH | 8308:LONE OAK | LONE_OAK_861 | 830861 | 2020-02-19 10:40 | 2020-02-19 12:58 | 138.02 | 1 | 6 | 124.9833 | 13 | PREMATURE FAILURE | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | Meadow Lark Dr | CMI_NORMAL | NO | NO | NO | 862377 | 168379 | 148536 | 19434 | 3958 | 0.00014493 | 1.1596e-06 | 124.9833 | 1 | 310 | Customer | 357252 | Load | Tran1phPad | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006418 |  | NORTHEAST | MUSKOGEE | 3312:CHECOTAH | CHECOTAH 22 | 331222 | 2020-02-19 10:45 | 2020-02-19 11:27 | 41.67 | 1 | 1 | 41.6667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | CHECOTAH | CHECOTAH RURAL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 74159 | 33327 | 2897 | 1537 | 4.8316e-05 | 1.1596e-06 | 41.6667 | 1 | 310 | Customer | 11629 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | OK - 2020
J2002.006425 | PD-02192020-00214 | SOUTHERN | DURANT | 5511:BOKCHITO | BOKCHITO 21 | 551121 | 2020-02-19 11:09 | 2020-02-19 13:52 | 162.98 | 1 | 1 | 162.9833 | 24 | WILDLIFE OTHER THAN SQUIRREL (DESCRIBE) | 21 | FUSE - TRANSFORMER | BENNINGTON | PERRY ST JUST EAST OF TAYLOR | CMI_NORMAL | NO | NO | NO | 862377 | 77726 | 15522 | 674 | 674 | 0.00018899 | 1.1596e-06 | 162.9833 | 1 | 320 | Load | 150312 | Load | TranOpenDelta | JUSTIN DUVAL | 580-380-5747 | [5 empty] | Animals | N | DISTRIBUTION | 34.5/19.9kv | 2020-02-19 | 2020 |  | #N/A
J2002.006429 | PD-02192020-00232 | ARKANSAS | POTEAU | 3608:MULDROW | MULDROW 21 | 360821 | 2020-02-19 11:15 | 2020-02-19 12:15 | 60.43 | 1 | 1 | 60.4333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MULDROW | 2ND POLE E OF MAIN ON PAYNE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 82364 | 13528 | 2280 | 1229 | 7.0078e-05 | 1.1596e-06 | 60.4333 | 1 | 310 | Customer | 16350 | Load | Tran1phOH | RICKEY S. WOLFE | 479-461-9162 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | #N/A
J2002.006428 | PD-02192020-00231 | ARKANSAS | OZARK | 9230:SHORT MTN | SHORT_MOUNTAIN_3061 | 923061 | 2020-02-19 11:15 | 2020-02-19 12:58 | 103.03 | 1 | 1 | 103.0333 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SUBIACO | E E ST AND SUBIACO AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 82364 | 7554 | 367 | 367 | 0.00011948 | 1.1596e-06 | 103.0333 | 1 | 310 | Load | 90071 | Load | 0 | RONALD F JOHNSON | 479-849-6565 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | #N/A
J2002.006434 | PD-02192020-00236 | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-02-19 11:25 | 2020-02-19 12:23 | 58.35 | 1 | 1 | 58.35 | 4 | DETERIORATION | 2 | TRANSFORMER OH | LAVACA | R.LAVACA ON RD. TO FAA RADAR | CMI_NORMAL | NO | NO | NO | 862377 | 82364 | 61282 | 2331 | 2129 | 6.7662e-05 | 1.1596e-06 | 58.35 | 1 | 310 | Load | 14385 | Load | Tran1phOH | DWAIN C CAUGHERN | 479-459-0231 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | Ark - Series 2
J2002.006440 | PD-02192020-00239 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7429 | 847429 | 2020-02-19 11:27 | 2020-02-19 12:09 | 41.72 | 12 | 11 | 500.6 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 2408 NE.27 | CMI_PLANNED | YES | NO | NO | 862377 | 168379 | 148536 | 6173 | 682 | 0.00058049 | 1.3915e-05 | 41.7167 | 1 | 310 | Load | 4623 | Load | Tran1phOH | RICARDO A MENCHACA | 405-301-6167 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | OK - 2022
J2002.006438 |  | ARKANSAS | FORT SMITH | 9137:PARK VIEW | PARK_VIEW_3721 | 913721 | 2020-02-19 11:34 | 2020-02-19 12:04 | 29.72 | 1 | 1 | 29.7167 | 14 | SEALED OUT/OPEN | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 4120 ROGERS AV | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 82364 | 61282 | 4576 | 1500 | 3.4459e-05 | 1.1596e-06 | 29.7167 | 1 | 310 | Customer | 14188 | Load | TranPad3phDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | Ark - Series 3
J2002.006439 |  | SOUTHERN | DURANT | 5512:COLBERT | COLBERT_1221 | 551221 | 2020-02-19 11:37 | 2020-02-19 18:37 | 420.58 | 2 | 1 | 342.0333 | 4 | DETERIORATION | 12 | POLE | CALERA | VO-AG BLDG SMISER+MCCURTN ON 4 | CMI_PLANNED | YES | NO | NO | 862377 | 77726 | 15522 | 2173 | 898 | 0.00039662 | 2.3192e-06 | 171.0167 | 1 | 308 | Load | 20088 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006442 | PD-02192020-00242 | METRO SOUTH | SOUTH CENTRAL | 8115:SW 22ND ST | SW_22ND_STREET_1521 | 811521 | 2020-02-19 11:45 | 2020-02-19 13:28 | 102.63 | 3 | 2 | 307.9 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 2036 Westwood Blvd | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 159306 | 102262 | 6073 | 1247 | 0.00035704 | 3.4788e-06 | 102.6333 | 1 | 310 | Load | 411723 | Load | Tran1phOH | ETHAN MORRIS | 918-510-5170 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | OK - 2022
J2002.006453 |  | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1421 | 911421 | 2020-02-19 12:03 | 2020-02-19 13:49 | 105.63 | 9 | 7 | 420 | 1 | CANCELLED | 57 | CANCELLED | FORT SMITH | 3213 N. 31 ST FT. SMITH, AR. | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 82364 | 61282 | 4743 | 1752 | 0.00048703 | 1.0436e-05 | 46.6667 | 1 | 308 | Load | 15426 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-19 | 2020 |  | Ark - Series 1
J2002.006448 |  | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_622 | 770622 | 2020-02-19 12:07 | 2020-02-19 14:56 | 168.67 | 1 | 2 | 17.1558 | 5 | ELECTRICAL TRACKING | 23 | FUSE - PRIMARY | BRISTOW | 1/2 W.OF HWY 48 ON 151ST STR. | CMI_PLANNED | YES | NO | NO | 862377 | 74159 | 40832 | 3786 | 2012 | 1.9894e-05 | 1.1596e-06 | 17.1558 | 1 | 310 | Load | 178713 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | #N/A
J2002.006450 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7423 | 847423 | 2020-02-19 12:10 | 2020-02-19 13:27 | 76.65 | 10 | 11 | 732.6455 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 821 NE.19 | CMI_PLANNED | YES | NO | NO | 862377 | 168379 | 148536 | 6173 | 1296 | 0.00084957 | 1.1596e-05 | 73.2645 | 1 | 310 | Load | 1630 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | OK - 2022
J2002.006451 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7423 | 847423 | 2020-02-19 12:10 | 2020-02-19 13:26 | 75.85 | 9 | 9 | 594.1652 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 839 NE.19 | CMI_PLANNED | YES | NO | NO | 862377 | 168379 | 148536 | 6173 | 1296 | 0.00068899 | 1.0436e-05 | 66.0183 | 1 | 310 | Load | 14870 | Load | TranOHDeltaSplitBank | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | OK - 2022
J2002.006452 |  | SOUTHERN | HEALDTON | 5305:HEALDTON | HEALDTON_523 | 530523 | 2020-02-19 12:18 | 2020-02-19 12:18 | 0.6 | 869 | 0 | 0 | 16 | SUBSTATION OPERATION | 45 | SUBSTATION CIRCUIT | HEALDTON | 128 S 8TH ST | CMI_MOMENTARY | YES | NO | NO | 862377 | 77726 | 6811 | 2133 | 869 | 0 | 0.0010077 | 0 | 1 | 0 | Feeder | HEALDTON_523 | Recloser | SubRecloser | Circuit Operation | [6 empty] | Cause Exclusion | N | SUBSTATION | 69kV | 2020-02-19 | 2020 |  | #N/A
J2002.006458 | PD-02192020-00263 | METRO WEST | EL RENO | 8905:EL RENO | EL_RENO_523 | 890523 | 2020-02-19 12:32 | 2020-02-19 15:24 | 171.92 | 1 | 1 | 171.9167 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | EL RENO | 700 BLK S SHEP | CMI_NORMAL | NO | NO | NO | 862377 | 129033 | 12803 | 6969 | 1259 | 0.00019935 | 1.1596e-06 | 171.9167 | 1 | 310 | Customer | 50818 | Load | Tran1phPad | HEATH THOMAS | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006461 |  | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-02-19 12:40 | 2020-02-19 13:10 | 29.57 | 7 | 0 | 206.2749 | 4 | DETERIORATION | 32 | CONDUCTOR SECONDARY - UG | MUSTANG | 403 S.BROOKVIEW LN | CMI_PLANNED | YES | NO | NO | 862377 | 129033 | 116230 | 18298 | 4433 | 0.00023919 | 8.1171e-06 | 29.4678 | 1 | 0 | Load | 47119 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | OK - 2022
J2002.006462 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1522 | 921522 | 2020-02-19 12:43 | 2020-02-19 12:59 | 15.88 | 1 | 1 | 8.2333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | CHARLESTON | LOT 9 QUAIL RIDGE S-HWY 22 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 82364 | 61282 | 962 | 471 | 9.5473e-06 | 1.1596e-06 | 8.2333 | 1 | 310 | Customer | 17882 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-19 | 2020 |  | Ark - Series 2
J2002.006465 |  | NORTHEAST | SAPULPA | 7706:BRISTOW | BRISTOW_622 | 770622 | 2020-02-19 12:49 | 2020-02-19 13:17 | 27.57 | 2 | 1 | 51.9667 | 11 | OVERLOAD | 23 | FUSE - PRIMARY | BRISTOW | 7.5MN-BRISTOW | CMI_PLANNED | YES | NO | NO | 862377 | 74159 | 40832 | 3786 | 2012 | 6.026e-05 | 2.3192e-06 | 25.9833 | 1 | 308 | Tap | 7145 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | #N/A
J2002.006467 |  | SOUTHERN | ARDMORE | 5109:ARDMORE WEST | ARDMORE_WEST_929 | 510929 | 2020-02-19 13:01 | 2020-02-19 13:42 | 41.12 | 1 | 0 | 31.9833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | 0 | WS DEESE RD 1MI N FR ACORN RD | CMI_PLANNED | YES | NO | NO | 862377 | 77726 | 23612 | 1318 | 616 | 3.7087e-05 | 1.1596e-06 | 31.9833 | 1 | 0 | Load | 173721 | Load | Tran3phWye | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006470 | PD-02192020-00273 | SOUTHERN | HEALDTON | 5122:DILLARD | DILLARD_2223 | 512223 | 2020-02-19 13:05 | 2020-02-19 13:57 | 51.98 | 1 | 1 | 50.15 | 4 | DETERIORATION | 17 | JUMPER | WILSON | SWSWSW 20 4S 2W-1 N TERRYS | CMI_NORMAL | NO | NO | NO | 862377 | 77726 | 6811 | 1191 | 339 | 5.8153e-05 | 1.1596e-06 | 50.15 | 1 | 310 | Load | 24247 | Load | Tran1phOH | BLAKE TAYLOR | 580-504-2901 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006471 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-02-19 13:07 | 2020-02-19 13:36 | 29.58 | 1 | 2 | 29.1153 | 4 | DETERIORATION | 12 | POLE | MOUNTAINBURG | 11807 Hwy 282 | CMI_PLANNED | YES | NO | NO | 862377 | 82364 | 61282 | 3793 | 2586 | 3.3762e-05 | 1.1596e-06 | 29.1153 | 1 | 310 | Load | 304350 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-19 | 2020 |  | Ark - Series 2
J2002.006474 |  | METRO WEST | WEST | 8158:SARA | SARA_5869 | 815869 | 2020-02-19 13:22 | 2020-02-19 13:52 | 30.4 | 1 | 1 | 30.4 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MUSTANG | 1125 W Hwy 152 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 129033 | 116230 | 18298 | 4433 | 3.5251e-05 | 1.1596e-06 | 30.4 | 1 | 310 | Customer | 234977 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | OK - 2022
J2002.006475 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2564 | 912564 | 2020-02-19 13:28 | 2020-02-19 17:00 | 212.35 | 1 | 1 | 92.7333 | 4 | DETERIORATION | 2 | TRANSFORMER OH | LAVACA | R.LAVACA ON RD. TO FAA RADAR | CMI_NORMAL | NO | NO | NO | 862377 | 82364 | 61282 | 2331 | 2129 | 0.00010753 | 1.1596e-06 | 92.7333 | 1 | 310 | Load | 14385 | Load | Tran1phOH | [7 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | Ark - Series 2
J2002.006486 | PD-02192020-00306 | METRO SOUTH | SOUTH CENTRAL | 8656:FOSTER | FOSTER_5629 | 865629 | 2020-02-19 13:51 | 2020-02-19 15:38 | 107 | 1 | 1 | 107 | 28 | OTHER (DESCRIBE) | 23 | FUSE - PRIMARY | OKLAHOMA CITY | I-240 & EASTERN | CMI_NORMAL | NO | NO | NO | 862377 | 159306 | 102262 | 2763 | 737 | 0.00012408 | 1.1596e-06 | 107 | 1 | 310 | Load | 205226 | Load | 0 | GERARDO D SOTO | 405-758-6334 | [5 empty] | Other | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006494 | PD-02192020-00333 | ARKANSAS | FORT SMITH | 9508:WHITESIDE | WHITESIDE_821 | 950821 | 2020-02-19 14:24 | 2020-02-19 17:40 | 196.5 | 1 | 1 | 140.85 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | VAN BUREN | 103 J-TURNER TR A | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862377 | 82364 | 61282 | 1922 | 1283 | 0.00016333 | 1.1596e-06 | 140.85 | 1 | 310 | Customer | 9097 | Load | Tran1phOH | DWAIN C CAUGHERN | 479-459-0231 | [5 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-19 | 2020 |  | Ark - Series 2
J2002.006495 | PD-02192020-00337 | SOUTHERN | ARDMORE | 5104:FOUNDATION | FOUNDATION_422 | 510422 | 2020-02-19 14:25 | 2020-02-19 15:37 | 72.32 | 1 | 1 | 72.3167 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ARDMORE | 418 PINE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 77726 | 23612 | 2320 | 1058 | 8.3857e-05 | 1.1596e-06 | 72.3167 | 1 | 310 | Customer | 7349 | Load | Tran1phOH | DAVID TAYLOR | 580-574-4517 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006496 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1522 | 921522 | 2020-02-19 14:29 | 2020-02-19 15:52 | 83.3 | 1 | 0 | 70.6667 | 5 | ELECTRICAL TRACKING | 28 | CROSSARM | 0 | 28714 ST HWY 22 | CMI_PLANNED | YES | NO | NO | 862377 | 82364 | 61282 | 962 | 471 | 8.1944e-05 | 1.1596e-06 | 70.6667 | 1 | 0 | Mainline | 7627 | Fuse | FuseOH | [7 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-19 | 2020 |  | Ark - Series 2
J2002.006498 |  | ARKANSAS | FORT SMITH | 9125:CARNALL | CARNALL_2525 | 912525 | 2020-02-19 14:29 | 2020-02-19 16:41 | 132.05 | 1 | 1 | 102.5167 | 4 | DETERIORATION | 36 | CONDUCTOR PRIMARY - UG | FORT SMITH | 4923 OLD GRNWD ROAD | CMI_PLANNED | YES | NO | NO | 862377 | 82364 | 61282 | 2331 | 202 | 0.00011888 | 1.1596e-06 | 102.5167 | 1 | 308 | Mainline | 1793 | Fuse | FuseRiser | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | Ark - Series 2
J2002.006500 |  | METRO WEST | WEST | 8299:WESTOAKS | WESTOAKS_9929 | 829929 | 2020-02-19 14:31 | 2020-02-19 14:38 | 7.12 | 1 | 1 | 7.1167 | 1 | CANCELLED | 57 | CANCELLED | BETHANY | 2502 N.ROCKWELL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 129033 | 116230 | 9242 | 2209 | 8.2524e-06 | 1.1596e-06 | 7.1167 | 1 | 310 | Customer | 34367 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006510 |  | METRO SOUTH | SOUTH CENTRAL | 8170:SANTA FE AVE | SANTA_FE_AVE_7022 | 817022 | 2020-02-19 14:57 | 2020-02-19 15:26 | 28.23 | 1 | 1 | 28.2333 | 1 | CANCELLED | 57 | CANCELLED | MOORE | 2009 REGENCY BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 159306 | 102262 | 9937 | 2103 | 3.2739e-05 | 1.1596e-06 | 28.2333 | 1 | 310 | Customer | 20681 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006511 |  | ARKANSAS | FORT SMITH | 9215:CHARLESTON | CHARLESTON_1522 | 921522 | 2020-02-19 15:01 | 2020-02-19 16:14 | 72.68 | 2 | 1 | 135.3 | 4 | DETERIORATION | 12 | POLE | CHARLESTON | CHARLESTN AR 72933 | CMI_PLANNED | YES | NO | NO | 862377 | 82364 | 61282 | 962 | 471 | 0.00015689 | 2.3192e-06 | 67.65 | 1 | 308 | Load | 6273 | Load | Tran1phOH | Contractor | [6 empty] | Equipment | N | DISTRIBUTION | 34.5/19.9kV | 2020-02-19 | 2020 |  | Ark - Series 2
J2002.006512 |  | METRO EAST | EAST | 8662:SE 15TH ST | SE_15TH_STREET_6222 | 866222 | 2020-02-19 15:16 | 2020-02-19 16:34 | 78.5 | 14 | 11 | 942.6667 | 4 | DETERIORATION | 1 | TRANSFORMER UG | CHOCTAW | 13501 SE.29 | CMI_PLANNED | YES | NO | NO | 862377 | 114533 | 71275 | 7214 | 1901 | 0.0010931 | 1.6234e-05 | 67.3333 | 1 | 310 | Load | 68774 | Load | Tran1phPad | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006521 |  | ARKANSAS | FORT SMITH | 9318:ALMA | ALMA_1823 | 931823 | 2020-02-19 15:43 | 2020-02-19 15:57 | 14.53 | 1 | 0 | 9.45 | 4 | DETERIORATION | 12 | POLE | ALMA | MT. GROVE RD. | CMI_PLANNED | YES | NO | NO | 862377 | 82364 | 61282 | 2851 | 1241 | 1.0958e-05 | 1.1596e-06 | 9.45 | 1 | 0 | Tap | 7097 | Fuse | FuseOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | Ark - Series 2
J2002.006526 |  | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2731 | 872731 | 2020-02-19 15:52 | 2020-02-19 16:15 | 23.23 | 1 | 1 | 23.2333 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 708 N University Blvd | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 159306 | 57044 | 6502 | 1351 | 2.6941e-05 | 1.1596e-06 | 23.2333 | 1 | 310 | Customer | 46876 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006536 | PD-02192020-00435 | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-02-19 16:19 | 2020-02-19 17:15 | 55.95 | 1 | 1 | 55.95 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ADA | 1600 ARLINGTON BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 77726 | 11525 | 2519 | 1090 | 6.4879e-05 | 1.1596e-06 | 55.95 | 1 | 310 | Customer | 12134 | Load | TranPad3phDelta | KEVIN GRAHAM | 580-421-2546 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | #N/A
J2002.006540 | PD-02192020-00450 | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6523 | 836523 | 2020-02-19 16:33 | 2020-02-19 17:56 | 83.37 | 1 | 1 | 83.3667 | 3 | DAMAGED BY PUBLIC | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 7214 GALAHAD CI | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 129033 | 116230 | 7425 | 2256 | 9.6671e-05 | 1.1596e-06 | 83.3667 | 1 | 310 | Customer | 34947 | Load | Tran1phPad | DANIEL PARMENTER | 405-313-2257 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | OK - 2022
J2002.006541 | PD-02192020-00455 | METRO EAST | EAST | 8522:MIDWAY | MIDWAY_2222 | 852222 | 2020-02-19 16:36 | 2020-02-19 19:11 | 154.58 | 1 | 1 | 154.5833 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | HARRAH | RENO AND LEGACY CROSSING | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 114533 | 71275 | 11649 | 2220 | 0.00017925 | 1.1596e-06 | 154.5833 | 1 | 310 | Customer | 386617 | Load | Tran1phPad | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006555 |  | METRO NORTH | NORTH | 8493:KELLEY AVE | KELLEY_AVENUE_9329 | 849329 | 2020-02-19 17:15 | 2020-02-19 19:00 | 104.87 | 1 | 1 | 93.4 | 13 | PREMATURE FAILURE | 1 | TRANSFORMER UG | OKLAHOMA CITY | 9800 N Oklahoma Av | CMI_PLANNED | YES | NO | NO | 862377 | 168379 | 148536 | 1483 | 422 | 0.00010831 | 1.1596e-06 | 93.4 | 1 | 308 | Tap | 334653 | Fuse | SwitchCubicleFuse | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006567 |  | ARKANSAS | FORT SMITH | 9330:SIMMONS | SIMMONS_3061 | 933061 | 2020-02-19 17:59 | 2020-02-19 20:32 | 153.02 | 4 | 2 | 543.4667 | 4 | DETERIORATION | 34 | CONDUCTOR SECONDARY - OH | WINSLOW | HWT 71 @ HL25/2, MT GAYLOR | CMI_PLANNED | YES | NO | NO | 862377 | 82364 | 61282 | 3793 | 2586 | 0.0006302 | 4.6383e-06 | 135.8667 | 1 | 308 | Load | 5061 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-19 | 2020 |  | Ark - Series 2
J2002.006569 |  | SOUTHERN | ADA | 5806:VALLEY VIEW | VALLEY_VIEW_623 | 580623 | 2020-02-19 18:02 | 2020-02-19 18:21 | 18.77 | 1 | 1 | 18.7667 | 1 | CANCELLED | 57 | CANCELLED | ADA | 1600 ARLINGTON BL | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 77748 | 11526 | 2519 | 1090 | 2.1762e-05 | 1.1596e-06 | 18.7667 | 1 | 310 | Customer | 12134 | Load | TranPad3phDelta | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | #N/A
J2002.006570 | PD-02192020-00466 | SOUTHERN | MADILL | 5906:TISHOMINGO | TISHOMINGO_621 | 590621 | 2020-02-19 18:15 | 2020-02-19 18:44 | 28.88 | 1 | 1 | 28.8833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | TISHOMINGO | 205 N HARRIS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 77748 | 7206 | 967 | 916 | 3.3493e-05 | 1.1596e-06 | 28.8833 | 1 | 310 | Customer | 13246 | Load | Tran1phOH | DAVID TAYLOR | 580-574-4517 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | OK - 2021
J2002.006572 | PD-02192020-00467 | SOUTHERN | HEALDTON | 5322:DUNDEE | DUNDEE 22 | 532222 | 2020-02-19 18:25 | 2020-02-19 20:28 | 123.35 | 1 | 1 | 114.5167 | 4 | DETERIORATION | 30 | CONDUCTOR SERVICE - UG | RINGLING | LOT 22 FORE ADDN | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862377 | 77748 | 6812 | 1015 | 1004 | 0.00013279 | 1.1596e-06 | 114.5167 | 1 | 310 | Customer | 19882 | Load | Tran1phPad | JOE LOFTIS | 918-884-5349 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006577 | PD-02192020-00470 | METRO EAST | EAST | 8458:GREEN PASTURES | GREEN_PASTURES_5822 | 845822 | 2020-02-19 18:47 | 2020-02-19 19:52 | 64.65 | 1 | 1 | 64.65 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | SPENCER | 5009 N.ABLE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 114552 | 71284 | 2989 | 937 | 7.4967e-05 | 1.1596e-06 | 64.65 | 1 | 310 | Customer | 12656 | Load | Tran1phOH | GARRISON L COLE | 405-206-2908 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | #N/A
J2002.006579 |  | METRO NORTH | NORTH | 8469:MEMORIAL | MEMORIAL_6963 | 846963 | 2020-02-19 19:17 | 2020-02-19 19:44 | 26.13 | 1 | 1 | 26.1333 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | 1/4E-BDWY EXT.5SS-SUMMIT RIDGE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 168405 | 148561 | 7736 | 1172 | 3.0304e-05 | 1.1596e-06 | 26.1333 | 1 | 310 | Customer | 69937 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | #N/A
J2002.006582 |  | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_524 | 510524 | 2020-02-19 19:34 | 2020-02-19 19:49 | 14.6 | 1 | 1 | 14.6 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | ARDMORE | HWY70/CARTER ST 3S .1W SS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 77748 | 23620 | 4782 | 1434 | 1.693e-05 | 1.1596e-06 | 14.6 | 1 | 320 | Customer | 6111 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | OK - 2021
J2002.006585 |  | METRO WEST | WEST | 8365:LAKESIDE | LAKESIDE_6523 | 836523 | 2020-02-19 19:38 | 2020-02-19 21:41 | 122.62 | 2 | 4 | 171.9 | 3 | DAMAGED BY PUBLIC | 32 | CONDUCTOR SECONDARY - UG | OKLAHOMA CITY | 7214 GALAHAD CI | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 129058 | 116252 | 7425 | 2256 | 0.00019933 | 2.3192e-06 | 85.95 | 1 | 310 | Secondary | 34947 | Load | Tran1phPad | Ties | [6 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | OK - 2022
J2002.006587 | PD-02192020-00484 | ARKANSAS | FORT SMITH | 9114:JOHNSON | JOHNSON_1423 | 911423 | 2020-02-19 20:15 | 2020-02-19 21:52 | 96.75 | 1 | 2 | 80.05 | 23 | CUSTOMER EQUIPMENT | 49 | CUSTOMER EQUIPMENT | FORT SMITH | 2408 N.57 LN | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 82387 | 61301 | 4745 | 781 | 9.2825e-05 | 1.1596e-06 | 80.05 | 1 | 320 | Customer | 6667 | Load | Tran1phOH | MARK A. SAWYER | 479-462-4457 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-19 | 2020 |  | Ark - Series 1
J2002.006589 | PD-02192020-00487 | SOUTHERN | ARDMORE | 5105:ARDMORE | ARDMORE_524 | 510524 | 2020-02-19 20:38 | 2020-02-19 21:41 | 63.45 | 1 | 1 | 57.95 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | ARDMORE | HWY70/CARTER ST 3S .1W SS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 77748 | 23620 | 4782 | 1434 | 6.7198e-05 | 1.1596e-06 | 57.95 | 1 | 310 | Customer | 6111 | Load | Tran1phOH | DAVID TAYLOR | 580-574-4517 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | OK - 2021
J2002.006590 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1228 | 831228 | 2020-02-19 20:39 | 2020-02-19 22:04 | 84.83 | 1 | 0 | 80.3833 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 130 NE.50 | CMI_PLANNED | YES | NO | NO | 862377 | 168405 | 148561 | 7757 | 522 | 9.3211e-05 | 1.1596e-06 | 80.3833 | 1 | 0 | Load | 19305 | Load | TranOH3phDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | OK - 2021
J2002.006594 |  | METRO SOUTH | SOUTH CENTRAL | 8163:SOUTHGATE | SOUTHGATE_6335 | 816335 | 2020-02-19 21:21 | 2020-02-19 21:59 | 37.92 | 1 | 1 | 37.9167 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | MOORE | 769 SW 19TH ST, BLDG 8 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862377 | 159318 | 102269 | 11849 | 1214 | 4.3968e-05 | 1.1596e-06 | 37.9167 | 1 | 310 | Customer | 366050 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | OK - 2022
J2002.006599 |  | ARKANSAS | FORT SMITH | 9113:CAVANAUGH | CAVANAUGH_1327 | 911327 | 2020-02-19 22:15 | 2020-02-20 01:46 | 211.35 | 1 | 1 | 204.55 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 6301 S.HWY-271 | CMI_PLANNED | YES | NO | NO | 862377 | 82387 | 61301 | 1458 | 1240 | 0.00023719 | 1.1596e-06 | 204.55 | 1 | 308 | Load | 1125 | Load | TranOH3phDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-19 | 2020 |  | Ark - Series 2
J2002.006600 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1226 | 831226 | 2020-02-19 22:20 | 2020-02-19 23:29 | 69.27 | 8 | 5 | 386.2667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 1237 NW.48 | CMI_PLANNED | YES | NO | NO | 862377 | 168405 | 148561 | 7757 | 1748 | 0.00044791 | 9.2767e-06 | 48.2833 | 1 | 310 | Load | 18082 | Load | TranOpenDelta | [7 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | OK - 2021
J2002.006609 | PD-02192020-00498 | METRO EAST | EAST | 8519:NE 10TH ST | NE_10TH_ST_1926 | 851926 | 2020-02-19 23:23 | 2020-02-20 04:40 | 317.42 | 12 | 14 | 3765.4 | 4 | DETERIORATION | 27 | CUTOUT | MIDWEST CITY | 817 LOTUS AV | CMI_NORMAL | NO | NO | NO | 862377 | 114552 | 71284 | 12472 | 2128 | 0.0043663 | 1.3915e-05 | 313.7833 | 1 | 310 | Load | 32443 | Load | Tran1phOH | JEREMIAH D WALKER | 405-974-0464 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-19 | 2020 |  | OK - 2021
J2002.006619 | PD-02202020-00002 | METRO EAST | SHAWNEE | 7432:ST GREGORY | ST_GREGORY_3222 | 743222 | 2020-02-20 00:51 | 2020-02-20 06:53 | 362.02 | 8 | 7 | 2892.2667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | SHAWNEE | 1/2 MW OF KICKAPOO ON 45TH NS | CMI_NORMAL | NO | NO | NO | 862377 | 114552 | 22152 | 4104 | 722 | 0.0033538 | 9.2767e-06 | 361.5333 | 1 | 310 | Load | 11019 | Load | Tran1phOH | JEREMIAH D WALKER | 405-974-0464 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-20 | 2020 |  | #N/A
J2002.006642 |  | ARKANSAS | FORT SMITH | 9111:MASSARD | MASSARD_1124 | 911124 | 2020-02-20 05:27 | 2020-02-20 09:43 | 255.77 | 1 | 1 | 250.3 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 7719 ROGERS AV | CMI_PLANNED | YES | NO | NO | 862411 | 82387 | 61301 | 4988 | 545 | 0.00029023 | 1.1595e-06 | 250.3 | 1 | 308 | Load | 660 | Load | Tran3phPadWye | Contractor | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-20 | 2020 |  | Ark - Series 3
J2002.006646 | PD-02202020-00014 | METRO SOUTH | SOUTH CENTRAL | 8141:SAGE | SAGE_4122 | 814122 | 2020-02-20 06:43 | 2020-02-20 09:00 | 137.18 | 1 | 1 | 137.1833 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | OKLAHOMA CITY | 706 SE.47 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862411 | 159318 | 102269 | 5814 | 1274 | 0.00015907 | 1.1595e-06 | 137.1833 | 1 | 320 | Customer | 14032 | Load | Tran1phOH | GERARDO D SOTO | 405-758-6334 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 69kV | 2020-02-20 | 2020 |  | #N/A
J2002.006647 |  | METRO EAST | EAST | 8690:WILD MARY | WILD_MARY_9023 | 869023 | 2020-02-20 06:44 | 2020-02-20 07:16 | 31.97 | 1 | 1 | 31.9667 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | OKLAHOMA CITY | SE 89 AND BRYANT LOT28 BLK 9 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862411 | 114552 | 71284 | 4024 | 2250 | 3.7067e-05 | 1.1595e-06 | 31.9667 | 1 | 310 | Customer | 78437 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-20 | 2020 |  | #N/A
J2002.006651 | PD-02202020-00024 | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2724 | 872724 | 2020-02-20 07:30 | 2020-02-20 11:20 | 229.68 | 1257 | 648 | 121761.75 | 3 | DAMAGED BY PUBLIC | 12 | POLE | NORMAN | 1000 ROCKCREEK RD | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862411 | 159318 | 57049 | 6502 | 1257 | 0.14119 | 0.0014575 | 96.8669 | 1 | 310 | Feeder | STUBBEMN_2724 | Recloser | SubRecloser | [7 empty] | Cause Exclusion | N | SUBSTATION | 138kV | 2020-02-20 | 2020 |  | #N/A
J2002.006664 |  | METRO NORTH | NORTH | 8322:THIRTY EIGHTH | THIRTY_EIGHTH_ST_2225 | 832225 | 2020-02-20 08:09 | 2020-02-20 10:57 | 168.13 | 3 | 3 | 504.4 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 3020 N.PENN | CMI_PLANNED | YES | NO | NO | 862411 | 168405 | 148561 | 9181 | 2040 | 0.00058487 | 3.4786e-06 | 168.1333 | 1 | 310 | Secondary | 2983 | Load | TranOpenDelta | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-20 | 2020 |  | OK - 2021
J2002.006666 |  | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2722 | 872722 | 2020-02-20 08:11 | 2020-02-20 08:14 | 3.6 | 1 | 1 | 3.6 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 2612 QUANAH PARKER TRAIL | CMI_MOMENTARY | YES | NO | NO | 862411 | 159318 | 57049 | 6502 | 1364 | 4.1743e-06 | 1.1595e-06 | 3.6 | 1 | 310 | Customer | 46351 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-20 | 2020 |  | #N/A
J2002.006668 |  | METRO SOUTH | SOUTH | 8727:STUBBEMAN | STUBBEMAN_2721 | 872721 | 2020-02-20 08:14 | 2020-02-20 08:18 | 3.78 | 1 | 1 | 3.7833 | 1 | CANCELLED | 57 | CANCELLED | NORMAN | 800 LEXINGTON | CMI_MOMENTARY | YES | NO | NO | 862411 | 159318 | 57049 | 6502 | 960 | 4.3869e-06 | 1.1595e-06 | 3.7833 | 1 | 310 | Customer | 39414 | Load | Tran1phPad | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-20 | 2020 |  | #N/A
J2002.006669 | PD-02202020-00052 | ARKANSAS | FORT SMITH | 9340:TWIN BRIDGES | TWIN_BRIDGES_4021 | 934021 | 2020-02-20 08:16 | 2020-02-20 10:05 | 109.35 | 1 | 1 | 109.35 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | VAN BUREN | REAR 33 IRIS | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862411 | 82387 | 61301 | 1040 | 1040 | 0.0001268 | 1.1595e-06 | 109.35 | 1 | 310 | Load | 18127 | Load | Tran1phOH | SHELDON D KANNADY | 479-650-0226 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 161kV | 2020-02-20 | 2020 |  | Ark - Series 1
J2002.006674 | PD-02202020-00071 | METRO NORTH | NORTH | 8337:EIGHTY FOURTH | EIGHTY_FOURTH_ST_3729 | 833729 | 2020-02-20 08:20 | 2020-02-20 08:56 | 36.23 | 14 | 9 | 480.4333 | 15 | SQUIRREL | 21 | FUSE - TRANSFORMER | OKLAHOMA CITY | 616 NW.92 | CMI_NORMAL | NO | NO | NO | 862411 | 168405 | 148561 | 5773 | 1401 | 0.00055708 | 1.6234e-05 | 34.3167 | 1 | 310 | Load | 14015 | Load | Tran1phOH | KIRK REILLEY | 405-550-3062 | [5 empty] | Animals | N | DISTRIBUTION | 138kV | 2020-02-20 | 2020 |  | OK - 2021
J2002.006675 | PD-02202020-00070 | METRO SOUTH | SOUTH CENTRAL | 8129:SW 64TH ST | SW_64TH_ST_2924 | 812924 | 2020-02-20 08:30 | 2020-02-20 10:02 | 92.25 | 1 | 2 | 88.5333 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 2928 SW.60 | CMI_NORMAL | NO | NO | NO | 862411 | 159318 | 102269 | 6392 | 2130 | 0.00010266 | 1.1595e-06 | 88.5333 | 1 | 310 | Customer | 22812 | Load | Tran1phOH | REX R WILSON | 405-535-4507 | [5 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-20 | 2020 |  | #N/A
J2002.006679 | PD-02202020-00078 | NORTHWEST | ALVA | 4707:KNOBHILL | KNOBHILL_730 | 470730 | 2020-02-20 08:36 | 2020-02-20 08:54 | 18.38 | 1 | 1 | 18.3833 | 22 | WIND | 31 | CONDUCTOR SERVICE - OH | ALVA | 520 PARK--ALVA | CMI_EQUIP_EXCLUSION | YES | NO | NO | 862411 | 53615 | 5524 | 1741 | 524 | 2.1316e-05 | 1.1595e-06 | 18.3833 | 1 | 310 | Customer | 9090 | Load | Tran1phOH | DENNIS PEARSON | 580-541-4106 | [5 empty] | Weather | N | DISTRIBUTION | 69kV | 2020-02-20 | 2020 |  | #N/A
J2002.006682 |  | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-02-20 08:37 | 2020-02-20 08:41 | 3.8 | 1 | 1 | 3.8 | 0 | BREAKER | 49 | CUSTOMER EQUIPMENT | DEL CITY | 3909 SE.27 | CMI_MOMENTARY | YES | NO | NO | 862411 | 159318 | 102269 | 7429 | 2243 | 4.4063e-06 | 1.1595e-06 | 3.8 | 1 | 310 | Customer | 10250 | Load | Tran1phOH | [7 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-20 | 2020 |  | OK - 2022
J2002.006681 | PD-02202020-00095 | SOUTHERN | DURANT | 5504:BUTTERFIELD | BUTTERFIELD_422 | 550422 | 2020-02-20 08:38 | 2020-02-20 09:41 | 63.45 | 1 | 1 | 63.45 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | ACHILLE | 200 W.MAIN -- ACHILLE | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862411 | 77748 | 15531 | 3491 | 562 | 7.3573e-05 | 1.1595e-06 | 63.45 | 1 | 310 | Customer | 14938 | Load | TranOpenDelta | CONTRACTOR BHI3 DAVID ELLIOT INC | 918-282-1005 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-20 | 2020 |  | #N/A
J2002.006684 |  | ARKANSAS | OZARK | 9418:LITTLE SPADRA | LITTLE_SPAD_CR_1863 | 941863 | 2020-02-20 08:41 | 2020-02-20 11:37 | 175.55 | 2 | 2 | 235 | 4 | DETERIORATION | 12 | POLE | LAMAR | ON CABIN CK. RD. 1000 W OF 64 | CMI_PLANNED | YES | NO | NO | 862411 | 82387 | 7554 | 731 | 0 | 0.00027249 | 2.3191e-06 | 117.5 | 1 | 308 | Load | 18580 | Load | Tran1phOH | Contractor | [6 empty] | Equipment | N | DISTRIBUTION | 69kV | 2020-02-20 | 2020 |  | #N/A
J2002.006686 | PD-02202020-00080 | METRO SOUTH | SOUTH CENTRAL | 8626:TROSPER | TROSPER_2621 | 862621 | 2020-02-20 08:42 | 2020-02-20 09:40 | 58.05 | 1 | 1 | 20.4395 | 9 | ON UPON ARRIVAL | 53 | ON UPON ARRIVAL | DEL CITY | 3909 SE.27 | CMI_CAUSE_EXCLUSION | YES | NO | NO | 862411 | 159318 | 102269 | 7429 | 2243 | 2.37e-05 | 1.1595e-06 | 20.4395 | 1 | 320 | Customer | 10250 | Load | Tran1phOH | GERARDO D SOTO | 405-758-6334 | [5 empty] | Cause Exclusion | N | DISTRIBUTION | 138kV | 2020-02-20 | 2020 |  | OK - 2022
J2002.006690 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7429 | 847429 | 2020-02-20 08:49 | 2020-02-20 09:46 | 57.67 | 4 | 3 | 197.6667 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 2300 E.MADISON | CMI_PLANNED | YES | NO | NO | 862411 | 168405 | 148561 | 6172 | 681 | 0.0002292 | 4.6382e-06 | 49.4167 | 1 | 308 | Load | 49998 | Load | TranOpenDelta | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-20 | 2020 |  | OK - 2022
J2002.006691 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3829 | 913829 | 2020-02-20 08:56 | 2020-02-20 15:37 | 400.92 | 5 | 5 | 1834.0833 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 1610 S.T | CMI_PLANNED | YES | NO | NO | 862411 | 82387 | 61301 | 2946 | 1192 | 0.0021267 | 5.7977e-06 | 366.8167 | 1 | 308 | Load | 684 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-20 | 2020 |  | Ark - Series 2
J2002.006700 |  | METRO NORTH | NORTH | 8361:WESTERN AVE | WESTERN_AV_6121 | 836121 | 2020-02-20 08:56 | 2020-02-20 10:09 | 73.17 | 13 | 8 | 891.8 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 407 NW.33 | CMI_PLANNED | YES | NO | NO | 862411 | 168405 | 148561 | 11129 | 1639 | 0.0010341 | 1.5074e-05 | 68.6 | 1 | 310 | Load | 18172 | Load | TranOpenDelta | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-20 | 2020 |  | OK - 2021
J2002.006693 |  | ARKANSAS | FORT SMITH | 9138:ARKOMA | ARKOMA_3829 | 913829 | 2020-02-20 08:59 | 2020-02-20 15:08 | 369.23 | 6 | 3 | 2114.5 | 4 | DETERIORATION | 12 | POLE | FORT SMITH | 1622 S.T | CMI_PLANNED | YES | NO | NO | 862411 | 82387 | 61301 | 2946 | 1192 | 0.0024518 | 6.9572e-06 | 352.4167 | 1 | 308 | Load | 1540 | Load | Tran1phOH | Crew | [6 empty] | Equipment | N | DISTRIBUTION | 161kV | 2020-02-20 | 2020 |  | Ark - Series 2
J2002.006694 |  | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7423 | 847423 | 2020-02-20 09:00 | 2020-02-20 12:01 | 181.82 | 9 | 8 | 478.8 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 1301 NE.18 | CMI_PLANNED | YES | NO | NO | 862411 | 168405 | 148561 | 6172 | 1296 | 0.00055519 | 1.0436e-05 | 53.2 | 1 | 310 | Load | 41 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-20 | 2020 |  | OK - 2022
J2002.006699 | PD-02202020-00141 | METRO NORTH | NORTH | 8474:STONEWALL | STONEWALL_7431 | 847431 | 2020-02-20 09:01 | 2020-02-20 12:24 | 203.3 | 3 | 3 | 156.3 | 4 | DETERIORATION | 50 | CONNECTOR | OKLAHOMA CITY | 720 NE.36 | CMI_NORMAL | NO | NO | NO | 862411 | 168405 | 148561 | 6172 | 374 | 0.00018124 | 3.4786e-06 | 52.1 | 1 | 310 | Secondary | 841 | Load | Tran1phOH | DERRICK P NICHOLS | 405-623-1868 | [5 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-20 | 2020 |  | OK - 2022
J2002.006696 |  | METRO NORTH | NORTH | 8312:BELLE ISLE STA | BELLE_ISLE_1229 | 831229 | 2020-02-20 09:03 | 2020-02-20 09:39 | 35.98 | 13 | 10 | 429 | 4 | DETERIORATION | 2 | TRANSFORMER OH | OKLAHOMA CITY | 2029 NW.45 | CMI_PLANNED | YES | NO | NO | 862411 | 168405 | 148561 | 7757 | 787 | 0.00049744 | 1.5074e-05 | 33 | 1 | 310 | Load | 12365 | Load | Tran1phOH | OGE | [6 empty] | Equipment | N | DISTRIBUTION | 138kV | 2020-02-20 | 2020 |  | OK - 2022
Formulas:
Month/Day/Year = (MONTH([Job OFF Time])&"/"&DAY([Job OFF Time])&"/"&YEAR([Job OFF Time]))*1